## TOC
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
FILE DESCRIPTION
This file includes all tables from the Post Event Report submitted following the De-energization Event.
TABLE OF CONTENTS
SECTION 01: Executive Summary
SECTION 02: Decision Making Process
Table 02: | Factors Considered in Decision to De-Energize
Table 03: | Circuit Thresholds
Table 04: | PSPS Risk vs. Benefit Comparison Tool
SECTION 03: De-Energized Time, Place, Duration and Customers
Table 05: | Circuits De-Energized
SECTION 04: Damage and Hazards to Overhead Facilities
Table 06: | Damage and Hazards
SECTION 05: Notifications
Table 07: | Notification Timeline
Table 09: | Breakdown of Notification Failures
SECTION 06: Local and State Public Safety Partner Engagement
Table 10: | Public Safety Partners Contacted
Table 11: | Entities Invited to SCE Emergency Operations Center
SECTION 07: Complaints and Claims
Table 12: | Count and Nature of Complaints Received
Table 13: | Count and Type of Claims Received
SECTION 08: Power Restoration Timeline
Table 14: | Circuits Requiring more than 24 hours to restore
SECTION 09: Community Resource Centers
Table 15: | Community Resource Center Address

## T02
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 02: Decision Making Process
Factors Considered in Decision to De-Energize
Circuit De-energized | Sustained Wind Speed |  |  | Gust Wind Speed |  |  | Fire Potential Index (FPI) |  | Firecast Output Ratio
| Activation Threshold | De-energization Threshold | Actual | Activation Threshold | De-energization Threshold | Actual | Threshold | Actual
ACOSTA | 31 | 40 | 32 | 46 | 58 | 50.1 | 12 | 12.5 | 133.4303
ALLVIEW (DS OF ROWCO) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ALPINE (DS OF RIM) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
AMETHYST | 40 | 40 | 32.1 | 58 | 58 | 54.9 | 12 | 12.5 | 122.755
ANGUS | 31 | 31 | 23.2 | 46 | 46 | 38.9 | 12 | 12.1 | 37.4045
ANTON | 31 | 40 | 27.9 | 46 | 58 | 51.2 | 12 | 12.1 | 759.8012
ARAPAHO | 29.1 | 27.7 | 19.9 | 41.8 | 39.7 | 37.9 | 12 | 12.2 | 448.9955
ARCHIE | 29 | 26.1 | 23.1 | 43.3 | 38.9 | 31.2 | 12 | 13.2 | 75857.825
ARMADA | 27.6 | 26.2 | 18.1 | 39.4 | 37.4 | 36.3 | 12 | 12.2 | 118.5479
ATENTO | 40 | 36 | 32.5 | 58 | 52.2 | 49.2 | 12 | 14.1 | 163.6888
ATLANTA | 31 | 32 | 29.1 | 45.4 | 45.4 | 42.7 | 12 | 12.1 | 60.5374
AVIATOR | 40 | 36 | 35.9 | 58 | 52.2 | 47.5 | 12 | 12.5 | 200.2361
BALCOM | 31 | 32.2 | 30 | 46 | 54.4 | 48.8 | 12 | 12.6 | 88.7432
BEAR VALLEY | 18 | 17.1 | 21.2 | 29 | 27.6 | 40.7 | 12 | 12.1 | 1016.3495
BELPAC | 31 | 32.9 | 32.1 | 42.4 | 42.4 | 40.2 | 12 | 12.1 | 46.1392
BIG FALLS (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
BIG ROCK | 31 | 36 | 30.8 | 46 | 52.2 | 43.1 | 12 | 14.2 | 121.9302
BLACKHILLS | 31 | 40 | 34.4 | 46 | 58 | 51.2 | 12 | 12.6 | 78.0557
BLEDSOE | 31 | 29.5 | 31.4 | 46 | 43.7 | 43.8 | 12 | 12.1 | 515.5994
BLUE CUT | 31 | 31 | 22.7 | 46 | 46 | 40.4 | 12 | 11.2 | 947.0319
BONNEVILLE | 28.1 | 28.1 | 30.6 | 40.1 | 40.1 | 40.6 | 12 | 12.2 | 401.2756
BOOTLEGGER | 40 | 40 | 29.5 | 58 | 58 | 52.3 | 12 | 12.1 | 282.3573
BORCHARD | 31 | 29.5 | 18.5 | 43.4 | 41.3 | 37 | 12 | 12.2 | 138.7561
BOULDER | 31 | 31 | 17.3 | 42.6 | 42.6 | 36.4 | 12 | 12.1 | 35.1405
BOUQUET | 31 | 29.5 | 18.5 | 46 | 43.7 | 39.4 | 12 | 12.1 | 336.0849
BRAKEMAN | 27.1 | 27.1 | 21.2 | 39.5 | 39.5 | 35.4 | 12 | 12.2 | 24.4698
BRENNAN | 40 | 38 | 34.4 | 58 | 55.1 | 46.1 | 12 | 12.6 | 126.7623
BROADCAST | 30.7 | 30.7 | 26.5 | 46 | 46 | 64.6 | 12 | 11.2 | 6335.8821
BUCKHORN | 31 | 31 | 19.6 | 46 | 46 | 46.3 | 12 | 12.2 | 62.8385
BURNS | 27.6 | 26.2 | 18.6 | 39.1 | 37.2 | 33.9 | 12 | 12.1 | 42.8731
BUTTERFIELD | 27.6 | 26.2 | 31.6 | 42.2 | 40.1 | 41.3 | 12 | 12.1 | 96.8332
CABANA | 40 | 38 | 30.3 | 58 | 55.1 | 47 | 12 | 12.6 | 16.0902
CALAMAR | 28 | 28 | 27.7 | 43.8 | 43.8 | 40.5 | 12 | 11.6 | 1775.9341
CALGROVE | 31 | 40 | 45.5 | 46 | 58 | 57.1 | 12 | 11.6 | 203.8888
CALSTATE | 40 | 40 | 35.2 | 58 | 58 | 49.3 | 12 | 12.5 | 295.2836
CAMP ANGELUS (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CANAL | 27.5 | 27.5 | 18.1 | 44.1 | 44.1 | 42.1 | 12 | 12.2 | 20400.3111
CARANCHO | 28.1 | 26.7 | 19.1 | 43.3 | 41.1 | 33.4 | 12 | 12.2 | 900.2218
CASSIDY | 31 | 38 | 28.5 | 46 | 55.1 | 49 | 12 | 13.2 | 68.1485
CASTRO | 29.8 | 28.3 | 18.8 | 46 | 43.7 | 44.3 | 12 | 12.2 | 44.0938
CEDAR GLEN (DS OF RIM) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CHAMPION | 40 | 38 | 34 | 58 | 55.1 | 49.1 | 12 | 12.6 | 58.5455
CHARDONNAY | 29.6 | 26.6 | 23.1 | 42.4 | 38.2 | 37.8 | 12 | 13.1 | 540.6424
CHAWA | 40 | 36 | 32.8 | 58 | 52.2 | 44.6 | 12 | 14.2 | 528.2056
CHEVELLE | 40 | 38 | 35.5 | 58 | 55.1 | 51.2 | 12 | 13.2 | 132.6304
CLARINET | 31 | 29.5 | 24.9 | 46 | 43.7 | 40.8 | 12 | 12.2 | 84.7158
CONDOR | 40 | 38 | 33.8 | 58 | 55.1 | 52.2 | 12 | 12.8 | 260.0349
CONFERENCE (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CONINE | 28.2 | 26.8 | 18.8 | 39.9 | 37.9 | 36 | 12 | 12.2 | 86.4425
CORSAIR | 29.6 | 28.1 | 19.7 | 42.1 | 40 | 37.9 | 12 | 12.2 | 113.9781
COTTAGE GROVE (DS OF RIM) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CRAB | 31 | 27.9 | 24 | 46 | 41.4 | 37.8 | 12 | 12.9 | N/A
CRAM | 31 | 27.9 | 25.6 | 46 | 41.4 | 38.6 | 12 | 13 | 65.0766
CRESCENTA | 31 | 32.7 | 20.2 | 41.9 | 41.9 | 35.7 | 12 | 12.2 | 35.8807
CRESTLINE (DS OF SAWPIT) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CRUMNER | 31 | 27.9 | 23.1 | 46 | 41.4 | 38.9 | 12 | 13.2 | 73.7524
CRUMP (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CUSHENBURY | 31 | 29.5 | 26.5 | 46 | 43.7 | 49.5 | 12 | 12.3 | 2249.5506
CUTHBERT | 31 | 36.5 | 29.8 | 46 | 48.6 | 44.6 | 12 | 12.6 | 110.6259
DALBA (DS OF ROWCO) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
DARTMOUTH | 31 | 38 | 30.4 | 44.6 | 55.1 | 47.1 | 12 | 12.6 | 95.407
DAVENPORT | 40 | 40 | 34.1 | 58 | 58 | 50.2 | 12 | 12.1 | 512.7478
DEACON | 28 | 26.6 | 23.4 | 40.3 | 38.3 | 32.4 | 12 | 13.1 | 93.798
DEL CARBON | 27.2 | 25.8 | 18.3 | 41.5 | 39.4 | 38 | 12 | 12.2 | 53.8367
DELUZ (DS OF LUISENO) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
DOBLE | 31 | 27.9 | 24.4 | 46 | 41.4 | 39.1 | 12 | 13.1 | 4744.1809
DONLON | 31 | 30 | 27.5 | 46 | 51 | 44.6 | 12 | 13.2 | 409.2928
DUKE | 40 | 36 | 32.8 | 58 | 52.2 | 44.6 | 12 | 14.1 | 142.6265
DYSART (DS OF SADDLEBACK) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ENERGY | 40 | 38 | 31.6 | 58 | 55.1 | 49 | 12 | 13.1 | 431.1843
ESCALA (DS OF WILDOMAR) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EVITA | 31 | 32 | 29.5 | 46 | 46 | 43.2 | 12 | 12.1 | 56.5762
FERRARA | 31 | 31 | 22.8 | 46 | 46 | 41.5 | 12 | 12 | 49.5653
FINGAL | 40 | 38 | 31 | 58 | 55.1 | 47.1 | 12 | 13.1 | 740.7848
FIREBIRD | 31 | 38 | 35.2 | 46 | 55.1 | 56.7 | 12 | 12.8 | 67.4319
FLYING D | 31 | 27.9 | 24.9 | 45.8 | 41.2 | 38.9 | 12 | 12.8 | 105.5493
GALAHAD | 40 | 38 | 31.4 | 58 | 55.1 | 48.6 | 12 | 12.6 | 136.1253
GARBONI | 28 | 28 | 30.5 | 40.1 | 40.1 | 49.1 | 12 | 12.6 | 44.6174
GILMAN | 31 | 29.4 | 18.6 | 44.6 | 42.4 | 41.5 | 12 | 12.1 | 14754.7606
GINGER | 28.5 | 27.1 | 20.2 | 40.5 | 38.5 | 34.2 | 12 | 12.2 | 196.8076
GRANNY SMITH | 30 | 28.5 | 18.8 | 42.9 | 40.8 | 38.4 | 12 | 12.2 | 660.919
GREEN BEAR (DS OF HEAPS PEAK) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GUITAR | 31 | 27.9 | 24.9 | 46 | 41.4 | 34.8 | 12 | 13.2 | 1011.3175
GUNSITE (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
HEAPS PEAK | 31 | 27.9 | 25.5 | 46 | 41.4 | 43.6 | 12 | 12.9 | N/A
HELICOPTER | 28.1 | 28.1 | 25.1 | 40.1 | 40.1 | 33.5 | 12 | 13.2 | 62.2741
HI LINE | 31 | 29.5 | 28.1 | 46 | 43.7 | 41.5 | 11 | 13.2 | 125.3803
HIGH SCHOOL (DS OF RIM) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
HIGHBALL | 31 | 27.9 | 29.1 | 46 | 41.4 | 38.8 | 12 | 12.6 | 61.6621
HILLFIELD | 31 | 38 | 35.8 | 46 | 55.1 | 51.2 | 12 | 13.2 | 84.1828
HONEYCRISP | 40 | 38 | 33 | 58 | 55.1 | 46.4 | 12 | 14.2 | 67.5405
HOOLIGAN | 31 | 29.5 | 19.8 | 46 | 43.7 | 40 | 12 | 12.2 | 39.5439
HORNTOAD | 31 | 27.9 | 26 | 46 | 41.4 | 36.6 | 12 | 13.2 | 173.3448
HUCKLEBERRY | 40 | 40 | 44.4 | 58 | 58 | 65 | 12 | 11.9 | 2183.2601
HUGO | 27.3 | 27.3 | 23.9 | 38.9 | 38.9 | 35.2 | 12 | 13.2 | 1822.0945
ICE HOUSE (DS OF FERRARA) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
INDEPENDENCE | 26.2 | 24.9 | 29.7 | 33.8 | 32.1 | 48.3 | 12 | 12.6 | 32.66
INTERIOR | 31 | 29.5 | 20 | 46 | 43.7 | 39 | 11 | 12.2 | 9.3995
INTERN | 31 | 31.7 | 19.4 | 40.8 | 40.8 | 36.2 | 12 | 12.2 | 90.5498
IRAN | 31 | 31.8 | 18.1 | 41 | 41 | 37.9 | 12 | 12.1 | 21.7989
JARVIS | 31 | 29.5 | 22.7 | 46 | 43.7 | 42.8 | 12 | 12 | 64.8
JEEP | 31 | 29.5 | 30.1 | 46 | 43.7 | 43.5 | 12 | 11.9 | 48.7883
JENKS LAKE (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
JUBILEE | 31 | 31.6 | 21.2 | 45 | 45 | 40.1 | 12 | 12.1 | 175.231
KINSEY | 31 | 33.9 | 31.9 | 46 | 48.5 | 48 | 12 | 12.1 | 264.9587
KUFFEL (DS OF RIM) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
KULBERG (DS OF SKINNER) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LA GRANDE | 31 | 29.5 | 29.2 | 46 | 43.7 | 49.3 | 12 | 12.5 | 91.2001
LA SIERRA | 31 | 36.4 | 26.7 | 46 | 52.8 | 51.1 | 12 | 13.2 | 727.8071
LACRESTA (DS OF WILDOMAR) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LAKELAND | 30.2 | 28.7 | 23.7 | 43.5 | 41.3 | 36.4 | 12 | 13.2 | 210.0464
LARCH | 31 | 38 | 29.9 | 46 | 55.1 | 53.6 | 12 | 12.6 | 7135.4665
LAUDA | 30.9 | 29.4 | 25.3 | 44.2 | 42 | 57.8 | 12 | 11.6 | 181269.698
LAZARO | 28 | 26.6 | 17.6 | 39.9 | 37.9 | 34.5 | 12 | 12.2 | 102.9755
LIMITED | 31 | 29.5 | 31 | 46 | 43.7 | 44.1 | 12 | 11.6 | 123.9917
LIMONITE | 31 | 37.8 | 29.9 | 46 | 48.8 | 53.6 | 12 | 12.6 | 40456.2517
LIVERMORE | 27 | 38 | 30.3 | 38.7 | 55.1 | 52.5 | 12 | 12.5 | 13.758
LOCKNER | 40 | 40 | 27.9 | 58 | 58 | 69.8 | 12 | 11.6 | 105.9103
LOPEZ | 40 | 38 | 26.5 | 58 | 55.1 | 49 | 12 | 13.2 | 183.3814
LOUCKS (DS OF DAVENPORT) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LUISENO | 30.7 | 27.6 | 25.9 | 43.9 | 39.5 | 35.7 | 12 | 13.1 | 25245.882
LURING (DS OF ROWCO) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
MACIEL | 40 | 40 | 36.7 | 58 | 58 | 51.7 | 12 | 12.1 | 55.7336
MAGUIRE | 30.7 | 27.6 | 29.4 | 46 | 41.4 | 43.9 | 12 | 12.5 | 418.6313
MAIZE | 27.2 | 24.5 | 29.7 | 40.3 | 36.2 | 48.3 | 12 | 12.6 | 66.2778
MAMBA | 31 | 40 | 29.5 | 46 | 58 | 49.2 | 12 | 12.1 | 72.7774
MERLIN | 31 | 27.9 | 25.3 | 46 | 41.4 | 35.1 | 12 | 13.1 | 267.358
METTLER | 40 | 38 | 30.3 | 58 | 55.1 | 50.7 | 12 | 12.8 | 440.1543
MILO | 31 | 27.9 | 23.1 | 46 | 41.4 | 38.9 | 12 | 13.2 | 55.2316
MORELAND | 31 | 27.9 | 24.9 | 46 | 41.4 | 37.2 | 12 | 13.2 | 41.7187
MORELLO | 31 | 29.5 | 22.3 | 45 | 42.8 | 38.9 | 12 | 12.2 | 1708.6732
MORGANSTEIN | 40 | 36 | 30.7 | 58 | 52.2 | 42.3 | 12 | 14.2 | 216.377
MULHOLLAND | 31 | 29.5 | 25 | 46 | 43.7 | 41.7 | 12 | 11.6 | 119.611
NAPOLEON | 40 | 38 | 30 | 58 | 55.1 | 48.4 | 12 | 12.6 | 201.4456
NATIONS | 27.5 | 26.2 | 18.3 | 39.3 | 37.3 | 32.7 | 12 | 12.2 | 564.366
NAYLOR | 31 | 38.9 | 31 | 46 | 50 | 48.1 | 12 | 12.6 | 83.1241
NORTH SHORE (DS OF RIM) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
NORTHPARK | 40 | 38 | 32.5 | 58 | 55.1 | 47.7 | 12 | 12.8 | 138.0538
OAK KNOLL (DS OF HEAPS PEAK) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
OBSERVATORY (DS OF BROADCAST) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
OLIVER | 29.3 | 29.3 | 26.8 | 42.3 | 42.3 | 45.9 | 12 | 11.1 | 94366.0461
OZARK | 40 | 38 | 33 | 58 | 55.1 | 46.4 | 12 | 14.2 | 45272.2851
PASCAL | 30.8 | 29.2 | 17.1 | 44.1 | 41.9 | 36.5 | 12 | 12.2 | 340.9951
PATRIOT | 31 | 27.9 | 24.5 | 44.8 | 40.3 | 37.5 | 12 | 13.2 | 86.9542
PAWNEE | 30.2 | 28.7 | 22.6 | 43.5 | 41.3 | 37.6 | 12 | 12.2 | 235.672
PENSTOCK | 40 | 40 | 34.3 | 58 | 58 | 46.2 | 12 | 12.2 | 80.429
PERRIS | 29.1 | 27.6 | 19.9 | 41.8 | 39.7 | 37.9 | 12 | 12.2 | 627.1442
PHEASANT (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PHOTON | 27.5 | 26.1 | 30.4 | 39.2 | 37.2 | 48.7 | 12 | 12.6 | 30.8047
PICK | 40 | 40 | 34 | 58 | 58 | 52.2 | 12 | 12.1 | 427.8768
PICONI | 29.3 | 26.4 | 27.9 | 42 | 37.8 | 38.6 | 12 | 13.1 | 347.9419
PINE COVE (DS OF CANAL) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PLATEAU | 31 | 27.9 | 23.8 | 46 | 41.4 | 36.3 | 12 | 13.2 | 74.8528
PONY (DS OF SKINNER) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
POPPET FLATS (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
POTTERY | 31 | 30.1 | 23.7 | 43.5 | 41.3 | 36.4 | 12 | 13.2 | 49.6609
PRONGHORN | 31 | 29.5 | 29.5 | 46 | 43.7 | 39.5 | 12 | 12.1 | 76.1368
PURCHASE (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PYTHON | 31 | 29.5 | 17.8 | 46 | 43.7 | 42.7 | 12 | 12.1 | 209.0473
RAMAC | 31 | 31 | 20.1 | 46 | 46 | 41.3 | 12 | 12.1 | 101.3756
RED BOX (DS OF BROADCAST) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
REJADA | 31 | 29.5 | 25 | 46 | 43.7 | 40.3 | 12 | 13.2 | 500.4659
RESORT | 28.7 | 25.8 | 24.2 | 46 | 41.4 | 38.6 | 12 | 13.2 | 16473.2445
RICARDO | 31 | 38 | 32.9 | 46 | 55.1 | 41 | 12 | 12.5 | 8.5368
RIM (DS OF SHAKE) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ROCKWELL | 26.3 | 25 | 18.4 | 34 | 32.3 | 27.6 | 12 | 12.2 | 21.1537
ROS | 26.8 | 24.2 | 33.7 | 38.6 | 34.8 | 51.5 | 12 | 12.6 | 69.0554
ROTEC | 27.6 | 38 | 32.2 | 39.7 | 55.1 | 55.5 | 12 | 12.6 | 251.827
ROUNDEL | 31 | 29.4 | 22.3 | 44.3 | 42.1 | 38.9 | 12 | 12.1 | 186.1527
ROWCO | 31 | 31 | 34.5 | 46 | 46 | 54.9 | 12 | 11.9 | 42.0991
RUSTIC | 31 | 27.9 | 25.6 | 46 | 41.4 | 37.8 | 12 | 13.1 | 81.0009
SADDLEBACK | 31 | 29.5 | 29.1 | 46 | 43.7 | 40.5 | 12 | 12.1 | 62171.7092
SAND CANYON | 40 | 40 | 44.6 | 58 | 58 | 68 | 12 | 11.2 | 199.2902
SANTORINI | 31 | 29.5 | 29.2 | 41.6 | 39.5 | 49.3 | 12 | 12.5 | 87.6754
SAUGUS-MOORPARK-SANTA SUSANA-TORREY | 40 | 56 | 41.1 | 58 | 68 | 66.6 | 12 | 14.1 | 135815.2428
SAUNDERS (DS OF CANAL) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SAWPIT | 31 | 27.9 | 25.8 | 46 | 41.4 | 41.5 | 12 | 13 | N/A
SCHMIDT | 31 | 29.4 | 22.3 | 44.3 | 42.1 | 38.9 | 12 | 12.1 | 331.7565
SCOUT (DS OF DOBLE) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SEELEY (DS OF SAWPIT) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SERRA | 31 | 29.5 | 21.4 | 46 | 43.7 | 45.7 | 12 | 12.2 | 293.2213
SEYMOUR (DS OF CRAB) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SHAKE | 31 | 29.5 | 30.1 | 46 | 43.7 | 43.5 | 12 | 11.9 | N/A
SHOVEL | 40 | 40 | 34 | 58 | 58 | 52.2 | 12 | 12.1 | 761.3229
SHOWDOWN | 31 | 31 | 30.5 | 46 | 46 | 40.8 | 12 | 11.1 | 296.8388
SIENNA | 31 | 29.5 | 23.1 | 46 | 43.7 | 38.9 | 12 | 13.2 | 125.6259
SKINNER (DS OF LUISENO) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SKY HI | 40 | 38 | 33.1 | 58 | 55.1 | 50.1 | 12 | 13.3 | 114.6354
SKYLAND (DS OF SAWPIT) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SNOW VALLEY (DS OF HEAPS PEAK) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SOGGY | 28.2 | 28.2 | 30.9 | 40.3 | 40.3 | 44.1 | 12 | 12.2 | 165.8993
SONOMA | 40 | 38 | 29.4 | 58 | 55.1 | 47.4 | 12 | 12.6 | 195.8286
SQUINT | 31 | 31.6 | 31.3 | 46 | 55.4 | 47.1 | 12 | 11.9 | 30.6619
STAGHORN | 31 | 39 | 34.2 | 46 | 50.3 | 53.6 | 12 | 12.1 | 83.0876
STARGLOW | 30.1 | 27.1 | 23 | 43.5 | 39.1 | 35.3 | 12 | 13.2 | 199.4305
STEEL (DS OF LAUDA) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
STORES | 40 | 36 | 30 | 58 | 52.2 | 46 | 12 | 14.1 | 1558.0989
STRATHERN | 31 | 31 | 22.2 | 46 | 46 | 39.5 | 12 | 12.1 | 84.0899
STUBBY | 40 | 40 | 28 | 58 | 58 | 49.5 | 12 | 12.1 | 185057.8644
SUNDANCE | 27.6 | 26.2 | 29.6 | 39.5 | 37.5 | 44 | 12 | 12.6 | 30.4631
SUTT | 40 | 40 | 37.9 | 58 | 58 | 56 | 12 | 12.7 | 69.1366
TACKLE | 27.4 | 27.4 | 22.7 | 39 | 39 | 33.3 | 12 | 12.2 | 154.9854
TAGGERT | 31 | 27.9 | 30.9 | 46 | 41.4 | 47 | 12 | 12.9 | 125.3493
TAHQUITZ | 31 | 29.5 | 30.9 | 46 | 43.7 | 44.6 | 12 | 12.1 | 844.3065
TAIWAN | 31 | 29.5 | 27.1 | 46 | 43.7 | 42.8 | 12 | 11.6 | 230.6026
TEJON | 31 | 27.9 | 24.9 | 46 | 41.4 | 37.1 | 12 | 13.1 | 203.9751
TERRA COTTA | 29.6 | 28.1 | 23.7 | 42.4 | 40.3 | 36.4 | 12 | 13.2 | 29259.0249
TIMBER CANYON | 30.9 | 29.3 | 24 | 46 | 46.4 | 40 | 12 | 13.2 | 104.6407
TIVO (DS OF BROADCAST) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TRUMBLE | 28.4 | 27 | 24.7 | 40.6 | 38.6 | 30.6 | 12 | 13.2 | 133.575
TUNGSTEN | 31 | 29.5 | 31.1 | 46 | 43.7 | 40.1 | 12 | 12 | 9.9481
URBITA | 31 | 29.5 | 31.9 | 46 | 43.7 | 46.3 | 12 | 11.6 | 61.7161
VENGEANCE | 28.8 | 27.3 | 30 | 44 | 41.8 | 43.3 | 12 | 11.6 | 69.6624
VERA CRUZ | 40 | 38 | 32.6 | 58 | 55.1 | 47.1 | 12 | 12.6 | 75.9943
VERDEMONT | 40 | 38 | 27.9 | 58 | 55.1 | 49.3 | 12 | 12.8 | 18404.5886
VERDUGO | 31 | 31 | 26.5 | 46 | 46 | 64.6 | 12 | 11.2 | 122.3188
VETERANS | 31 | 33.6 | 9 | 46 | 53.7 | 20.5 | 12 | 11.2 | 51.0265
WARHAWK | 40 | 38 | 33 | 58 | 55.1 | 41.7 | 12 | 12.6 | 75.5336
WEESHA (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
WESTBROOK | 28.3 | 25.5 | 23.9 | 40.4 | 36.4 | 35.2 | 12 | 13.2 | 289.7864
WILDOMAR | 29.5 | 28.1 | 21 | 42 | 39.9 | 37.3 | 12 | 12.2 | 141878.3806
WINERY | 29.4 | 26.4 | 23.8 | 42 | 37.8 | 39.6 | 12 | 13.2 | 523.4873
WOBEGONE | 28.2 | 26.8 | 28.9 | 40.5 | 38.4 | 44.1 | 12 | 11.6 | 516.8587
YANKEE (DS OF TUNGSTEN) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ZEVO (DS OF SKINNER) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ZONE | 40 | 38 | 33.8 | 58 | 55.1 | 45.5 | 12 | 12.6 | 167.4152

## T03
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
Circuit Thresholds
Circuit | FPI Threshold Rating | Wind Speed Activation Thresholds |  | De-Energization Thresholds
|  | Sustained Wind | Gust Wind | Sustained Wind | Gust Wind
ACOSTA | 12 | 31 | 46 | 40 | 58
ALLVIEW (DS OF ROWCO) | N/A | N/A | N/A | N/A | N/A
ALPINE (DS OF RIM) | N/A | N/A | N/A | N/A | N/A
AMETHYST | 12 | 40 | 58 | 40 | 58
ANGUS | 12 | 31 | 46 | 31 | 46
ANTON | 12 | 31 | 46 | 40 | 58
ARAPAHO | 12 | 29.1 | 41.8 | 27.7 | 39.7
ARCHIE | 12 | 29 | 43.3 | 26.1 | 38.9
ARMADA | 12 | 27.6 | 39.4 | 26.2 | 37.4
ATENTO | 12 | 40 | 58 | 36 | 52.2
ATLANTA | 12 | 31 | 45.4 | 32 | 45.4
AVIATOR | 12 | 40 | 58 | 36 | 52.2
BALCOM | 12 | 31 | 46 | 32.2 | 54.4
BEAR VALLEY | 12 | 18 | 29 | 17.1 | 27.6
BELPAC | 12 | 31 | 42.4 | 32.9 | 42.4
BIG FALLS (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A
BIG ROCK | 12 | 31 | 46 | 36 | 52.2
BLACKHILLS | 12 | 31 | 46 | 40 | 58
BLEDSOE | 12 | 31 | 46 | 29.5 | 43.7
BLUE CUT | 12 | 31 | 46 | 31 | 46
BONNEVILLE | 12 | 28.1 | 40.1 | 28.1 | 40.1
BOOTLEGGER | 12 | 40 | 58 | 40 | 58
BORCHARD | 12 | 31 | 43.4 | 29.5 | 41.3
BOULDER | 12 | 31 | 42.6 | 31 | 42.6
BOUQUET | 12 | 31 | 46 | 29.5 | 43.7
BRAKEMAN | 12 | 27.1 | 39.5 | 27.1 | 39.5
BRENNAN | 12 | 40 | 58 | 38 | 55.1
BROADCAST | 12 | 30.7 | 46 | 30.7 | 46
BUCKHORN | 12 | 31 | 46 | 31 | 46
BURNS | 12 | 27.6 | 39.1 | 26.2 | 37.2
BUTTERFIELD | 12 | 27.6 | 42.2 | 26.2 | 40.1
CABANA | 12 | 40 | 58 | 38 | 55.1
CALAMAR | 12 | 28 | 43.8 | 28 | 43.8
CALGROVE | 12 | 31 | 46 | 40 | 58
CALSTATE | 12 | 40 | 58 | 40 | 58
CAMP ANGELUS (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A
CANAL | 12 | 27.5 | 44.1 | 27.5 | 44.1
CARANCHO | 12 | 28.1 | 43.3 | 26.7 | 41.1
CASSIDY | 12 | 31 | 46 | 38 | 55.1
CASTRO | 12 | 29.8 | 46 | 28.3 | 43.7
CEDAR GLEN (DS OF RIM) | N/A | N/A | N/A | N/A | N/A
CHAMPION | 12 | 40 | 58 | 38 | 55.1
CHARDONNAY | 12 | 29.6 | 42.4 | 26.6 | 38.2
CHAWA | 12 | 40 | 58 | 36 | 52.2
CHEVELLE | 12 | 40 | 58 | 38 | 55.1
CLARINET | 12 | 31 | 46 | 29.5 | 43.7
CONDOR | 12 | 40 | 58 | 38 | 55.1
CONFERENCE (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A
CONINE | 12 | 28.2 | 39.9 | 26.8 | 37.9
CORSAIR | 12 | 29.6 | 42.1 | 28.1 | 40
COTTAGE GROVE (DS OF RIM) | N/A | N/A | N/A | N/A | N/A
CRAB | 12 | 31 | 46 | 27.9 | 41.4
CRAM | 12 | 31 | 46 | 27.9 | 41.4
CRESCENTA | 12 | 31 | 41.9 | 32.7 | 41.9
CRESTLINE (DS OF SAWPIT) | N/A | N/A | N/A | N/A | N/A
CRUMNER | 12 | 31 | 46 | 27.9 | 41.4
CRUMP (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A
CUSHENBURY | 12 | 31 | 46 | 29.5 | 43.7
CUTHBERT | 12 | 31 | 46 | 36.5 | 48.6
DALBA (DS OF ROWCO) | N/A | N/A | N/A | N/A | N/A
DARTMOUTH | 12 | 31 | 44.6 | 38 | 55.1
DAVENPORT | 12 | 40 | 58 | 40 | 58
DEACON | 12 | 28 | 40.3 | 26.6 | 38.3
DEL CARBON | 12 | 27.2 | 41.5 | 25.8 | 39.4
DELUZ (DS OF LUISENO) | N/A | N/A | N/A | N/A | N/A
DOBLE | 12 | 31 | 46 | 27.9 | 41.4
DONLON | 12 | 31 | 46 | 30 | 51
DUKE | 12 | 40 | 58 | 36 | 52.2
DYSART (DS OF SADDLEBACK) | N/A | N/A | N/A | N/A | N/A
ENERGY | 12 | 40 | 58 | 38 | 55.1
ESCALA (DS OF WILDOMAR) | N/A | N/A | N/A | N/A | N/A
EVITA | 12 | 31 | 46 | 32 | 46
FERRARA | 12 | 31 | 46 | 31 | 46
FINGAL | 12 | 40 | 58 | 38 | 55.1
FIREBIRD | 12 | 31 | 46 | 38 | 55.1
FLYING D | 12 | 31 | 45.8 | 27.9 | 41.2
GALAHAD | 12 | 40 | 58 | 38 | 55.1
GARBONI | 12 | 28 | 40.1 | 28 | 40.1
GILMAN | 12 | 31 | 44.6 | 29.4 | 42.4
GINGER | 12 | 28.5 | 40.5 | 27.1 | 38.5
GRANNY SMITH | 12 | 30 | 42.9 | 28.5 | 40.8
GREEN BEAR (DS OF HEAPS PEAK) | N/A | N/A | N/A | N/A | N/A
GUITAR | 12 | 31 | 46 | 27.9 | 41.4
GUNSITE (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A
HEAPS PEAK | 12 | 31 | 46 | 27.9 | 41.4
HELICOPTER | 12 | 28.1 | 40.1 | 28.1 | 40.1
HI LINE | 11 | 31 | 46 | 29.5 | 43.7
HIGH SCHOOL (DS OF RIM) | N/A | N/A | N/A | N/A | N/A
HIGHBALL | 12 | 31 | 46 | 27.9 | 41.4
HILLFIELD | 12 | 31 | 46 | 38 | 55.1
HONEYCRISP | 12 | 40 | 58 | 38 | 55.1
HOOLIGAN | 12 | 31 | 46 | 29.5 | 43.7
HORNTOAD | 12 | 31 | 46 | 27.9 | 41.4
HUCKLEBERRY | 12 | 40 | 58 | 40 | 58
HUGO | 12 | 27.3 | 38.9 | 27.3 | 38.9
ICE HOUSE (DS OF FERRARA) | N/A | N/A | N/A | N/A | N/A
INDEPENDENCE | 12 | 26.2 | 33.8 | 24.9 | 32.1
INTERIOR | 11 | 31 | 46 | 29.5 | 43.7
INTERN | 12 | 31 | 40.8 | 31.7 | 40.8
IRAN | 12 | 31 | 41 | 31.8 | 41
JARVIS | 12 | 31 | 46 | 29.5 | 43.7
JEEP | 12 | 31 | 46 | 29.5 | 43.7
JENKS LAKE (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A
JUBILEE | 12 | 31 | 45 | 31.6 | 45
KINSEY | 12 | 31 | 46 | 33.9 | 48.5
KUFFEL (DS OF RIM) | N/A | N/A | N/A | N/A | N/A
KULBERG (DS OF SKINNER) | N/A | N/A | N/A | N/A | N/A
LA GRANDE | 12 | 31 | 46 | 29.5 | 43.7
LA SIERRA | 12 | 31 | 46 | 36.4 | 52.8
LACRESTA (DS OF WILDOMAR) | N/A | N/A | N/A | N/A | N/A
LAKELAND | 12 | 30.2 | 43.5 | 28.7 | 41.3
LARCH | 12 | 31 | 46 | 38 | 55.1
LAUDA | 12 | 30.9 | 44.2 | 29.4 | 42
LAZARO | 12 | 28 | 39.9 | 26.6 | 37.9
LIMITED | 12 | 31 | 46 | 29.5 | 43.7
LIMONITE | 12 | 31 | 46 | 37.8 | 48.8
LIVERMORE | 12 | 27 | 38.7 | 38 | 55.1
LOCKNER | 12 | 40 | 58 | 40 | 58
LOPEZ | 12 | 40 | 58 | 38 | 55.1
LOUCKS (DS OF DAVENPORT) | N/A | N/A | N/A | N/A | N/A
LUISENO | 12 | 30.7 | 43.9 | 27.6 | 39.5
LURING (DS OF ROWCO) | N/A | N/A | N/A | N/A | N/A
MACIEL | 12 | 40 | 58 | 40 | 58
MAGUIRE | 12 | 30.7 | 46 | 27.6 | 41.4
MAIZE | 12 | 27.2 | 40.3 | 24.5 | 36.2
MAMBA | 12 | 31 | 46 | 40 | 58
MERLIN | 12 | 31 | 46 | 27.9 | 41.4
METTLER | 12 | 40 | 58 | 38 | 55.1
MILO | 12 | 31 | 46 | 27.9 | 41.4
MORELAND | 12 | 31 | 46 | 27.9 | 41.4
MORELLO | 12 | 31 | 45 | 29.5 | 42.8
MORGANSTEIN | 12 | 40 | 58 | 36 | 52.2
MULHOLLAND | 12 | 31 | 46 | 29.5 | 43.7
NAPOLEON | 12 | 40 | 58 | 38 | 55.1
NATIONS | 12 | 27.5 | 39.3 | 26.2 | 37.3
NAYLOR | 12 | 31 | 46 | 38.9 | 50
NORTH SHORE (DS OF RIM) | N/A | N/A | N/A | N/A | N/A
NORTHPARK | 12 | 40 | 58 | 38 | 55.1
OAK KNOLL (DS OF HEAPS PEAK) | N/A | N/A | N/A | N/A | N/A
OBSERVATORY (DS OF BROADCAST) | N/A | N/A | N/A | N/A | N/A
OLIVER | 12 | 29.3 | 42.3 | 29.3 | 42.3
OZARK | 12 | 40 | 58 | 38 | 55.1
PASCAL | 12 | 30.8 | 44.1 | 29.2 | 41.9
PATRIOT | 12 | 31 | 44.8 | 27.9 | 40.3
PAWNEE | 12 | 30.2 | 43.5 | 28.7 | 41.3
PENSTOCK | 12 | 40 | 58 | 40 | 58
PERRIS | 12 | 29.1 | 41.8 | 27.6 | 39.7
PHEASANT (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A
PHOTON | 12 | 27.5 | 39.2 | 26.1 | 37.2
PICK | 12 | 40 | 58 | 40 | 58
PICONI | 12 | 29.3 | 42 | 26.4 | 37.8
PINE COVE (DS OF CANAL) | N/A | N/A | N/A | N/A | N/A
PLATEAU | 12 | 31 | 46 | 27.9 | 41.4
PONY (DS OF SKINNER) | N/A | N/A | N/A | N/A | N/A
POPPET FLATS (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A
POTTERY | 12 | 31 | 43.5 | 30.1 | 41.3
PRONGHORN | 12 | 31 | 46 | 29.5 | 43.7
PURCHASE (DS OF STUBBY) | N/A | N/A | N/A | N/A | N/A
PYTHON | 12 | 31 | 46 | 29.5 | 43.7
RAMAC | 12 | 31 | 46 | 31 | 46
RED BOX (DS OF BROADCAST) | N/A | N/A | N/A | N/A | N/A
REJADA | 12 | 31 | 46 | 29.5 | 43.7
RESORT | 12 | 28.7 | 46 | 25.8 | 41.4
RICARDO | 12 | 31 | 46 | 38 | 55.1
RIM (DS OF SHAKE) | N/A | N/A | N/A | N/A | N/A
ROCKWELL | 12 | 26.3 | 34 | 25 | 32.3
ROS | 12 | 26.8 | 38.6 | 24.2 | 34.8
ROTEC | 12 | 27.6 | 39.7 | 38 | 55.1
ROUNDEL | 12 | 31 | 44.3 | 29.4 | 42.1
ROWCO | 12 | 31 | 46 | 31 | 46
RUSTIC | 12 | 31 | 46 | 27.9 | 41.4
SADDLEBACK | 12 | 31 | 46 | 29.5 | 43.7
SAND CANYON | 12 | 40 | 58 | 40 | 58
SANTORINI | 12 | 31 | 41.6 | 29.5 | 39.5
SAUGUS-MOORPARK-SANTA SUSANA-TORREY | 12 | 40 | 58 | 56 | 68
SAUNDERS (DS OF CANAL) | N/A | N/A | N/A | N/A | N/A
SAWPIT | 12 | 31 | 46 | 27.9 | 41.4
SCHMIDT | 12 | 31 | 44.3 | 29.4 | 42.1
SCOUT (DS OF DOBLE) | N/A | N/A | N/A | N/A | N/A
SEELEY (DS OF SAWPIT) | N/A | N/A | N/A | N/A | N/A
SERRA | 12 | 31 | 46 | 29.5 | 43.7
SEYMOUR (DS OF CRAB) | N/A | N/A | N/A | N/A | N/A
SHAKE | 12 | 31 | 46 | 29.5 | 43.7
SHOVEL | 12 | 40 | 58 | 40 | 58
SHOWDOWN | 12 | 31 | 46 | 31 | 46
SIENNA | 12 | 31 | 46 | 29.5 | 43.7
SKINNER (DS OF LUISENO) | N/A | N/A | N/A | N/A | N/A
SKY HI | 12 | 40 | 58 | 38 | 55.1
SKYLAND (DS OF SAWPIT) | N/A | N/A | N/A | N/A | N/A
SNOW VALLEY (DS OF HEAPS PEAK) | N/A | N/A | N/A | N/A | N/A
SOGGY | 12 | 28.2 | 40.3 | 28.2 | 40.3
SONOMA | 12 | 40 | 58 | 38 | 55.1
SQUINT | 12 | 31 | 46 | 31.6 | 55.4
STAGHORN | 12 | 31 | 46 | 39 | 50.3
STARGLOW | 12 | 30.1 | 43.5 | 27.1 | 39.1
STEEL (DS OF LAUDA) | N/A | N/A | N/A | N/A | N/A
STORES | 12 | 40 | 58 | 36 | 52.2
STRATHERN | 12 | 31 | 46 | 31 | 46
STUBBY | 12 | 40 | 58 | 40 | 58
SUNDANCE | 12 | 27.6 | 39.5 | 26.2 | 37.5
SUTT | 12 | 40 | 58 | 40 | 58
TACKLE | 12 | 27.4 | 39 | 27.4 | 39
TAGGERT | 12 | 31 | 46 | 27.9 | 41.4
TAHQUITZ | 12 | 31 | 46 | 29.5 | 43.7
TAIWAN | 12 | 31 | 46 | 29.5 | 43.7
TEJON | 12 | 31 | 46 | 27.9 | 41.4
TERRA COTTA | 12 | 29.6 | 42.4 | 28.1 | 40.3
TIMBER CANYON | 12 | 30.9 | 46 | 29.3 | 46.4
TIVO (DS OF BROADCAST) | N/A | N/A | N/A | N/A | N/A
TRUMBLE | 12 | 28.4 | 40.6 | 27 | 38.6
TUNGSTEN | 12 | 31 | 46 | 29.5 | 43.7
URBITA | 12 | 31 | 46 | 29.5 | 43.7
VENGEANCE | 12 | 28.8 | 44 | 27.3 | 41.8
VERA CRUZ | 12 | 40 | 58 | 38 | 55.1
VERDEMONT | 12 | 40 | 58 | 38 | 55.1
VERDUGO | 12 | 31 | 46 | 31 | 46
VETERANS | 12 | 31 | 46 | 33.6 | 53.7
WARHAWK | 12 | 40 | 58 | 38 | 55.1
WEESHA (DS OF BEAR VALLEY) | N/A | N/A | N/A | N/A | N/A
WESTBROOK | 12 | 28.3 | 40.4 | 25.5 | 36.4
WILDOMAR | 12 | 30 | 42 | 28.1 | 37.3
WINERY | 12 | 29.4 | 42 | 26.4 | 37.8
WOBEGONE | 12 | 28.2 | 40.5 | 26.8 | 38.4
YANKEE (DS OF TUNGSTEN) | N/A | N/A | N/A | N/A | N/A
ZEVO (DS OF SKINNER) | N/A | N/A | N/A | N/A | N/A
ZONE | 12 | 40 | 58 | 38 | 55.1

## T04
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 02: Decision Making Process
PSPS Risk vs. Benefit Comparison Tool
Circuit | All Customers | Population | AFN/NRCI Multiplier | 24 Hour CMI (24 x 60) | Firecast Acres | Firecast Buildings | Firecast Population | PSPS Risk (24 hr Impact- PSPS Model) | Wildfire Risk (24hr Impact-PSPS Model) | Firecast Output Ratio
ACOSTA | 2307 | 6921 | 1.248 | 1440 | 7804.5 | 816 | 3909 | 0.00048837 | 0.065163 | 133.4303
ALLVIEW (DS OF ROWCO) | 303 | 909 | 1.012 | 1440 | N/A | N/A | N/A | 6.3042e-05 | N/A | N/A
ALPINE (DS OF RIM) | 708 | 2124 | 1.2193 | 1440 | N/A | N/A | N/A | 0.00014956 | N/A | N/A
AMETHYST | 1528 | 4584 | 1.0981 | 1440 | 3693.9 | 493 | 1304 | 0.00031994 | 0.039274 | 122.755
ANGUS | 1599 | 4797 | 1.2756 | 1440 | 7024.7 | 148 | 315 | 0.00033917 | 0.012686 | 37.4045
ANTON | 298 | 894 | 1.2113 | 1440 | 10963 | 594 | 1329 | 6.2915e-05 | 0.047803 | 759.8012
ARAPAHO | 1133 | 3399 | 1.2406 | 1440 | 10184 | 1358 | 2981 | 0.00023971 | 0.10763 | 448.9955
ARCHIE | 2 | 6 | 1.5 | 1440 | 16775 | 393 | 712 | 0.00096407 | 0.032704 | 75857.825
ARMADA | 1591 | 4773 | 1.0409 | 1440 | 4709.5 | 492 | 1911 | 0.00033173 | 0.039326 | 118.5479
ATENTO | 2292 | 6876 | 1.3401 | 1440 | 19240 | 988 | 4590 | 0.00048844 | 0.079951 | 163.6888
ATLANTA | 930 | 2790 | 1.2216 | 1440 | 1281.1 | 148 | 750 | 0.00019649 | 0.011895 | 60.5374
AVIATOR | 1819 | 5457 | 1.142 | 1440 | 8583.2 | 961 | 747 | 0.0003821 | 0.076509 | 200.2361
BALCOM | 2076 | 6228 | 1.0602 | 1440 | 12689 | 468 | 505 | 0.00043347 | 0.038468 | 88.7432
BEAR VALLEY | 40 | 120 | 1.4716 | 1440 | 5159 | 104 | 137 | 0.00024546 | 0.0087457 | 1016.3495
BELPAC | 3205 | 9615 | 1.0426 | 1440 | 9914 | 372 | 1741 | 0.00066834 | 0.030837 | 46.1392
BIG FALLS (DS OF BEAR VALLEY) | 142 | 426 | 1.0066 | 1440 | N/A | N/A | N/A | 2.9533e-05 | N/A | N/A
BIG ROCK | 2448 | 7344 | 1.1546 | 1440 | 8424.9 | 784 | 1501 | 0.0005147 | 0.062757 | 121.9302
BLACKHILLS | 1813 | 5439 | 1.1889 | 1440 | 748.46 | 376 | 1765 | 0.00038214 | 0.029828 | 78.0557
BLEDSOE | 158 | 474 | 1.4866 | 1440 | 9307.9 | 210 | 252 | 3.4026e-05 | 0.017544 | 515.5994
BLUE CUT | 298 | 894 | 1.3754 | 1440 | 16103 | 746 | 2031 | 6.3667e-05 | 0.060294 | 947.0319
BONNEVILLE | 515 | 1545 | 1.278 | 1440 | 10876 | 543 | 2678 | 0.00010926 | 0.043842 | 401.2756
BOOTLEGGER | 1611 | 4833 | 1.1536 | 1440 | 14554 | 1197 | 1766 | 0.00033869 | 0.095632 | 282.3573
BORCHARD | 1334 | 4002 | 1.0466 | 1440 | 11037 | 474 | 1620 | 0.00027826 | 0.03861 | 138.7561
BOULDER | 1436 | 4308 | 1.2572 | 1440 | 2233.7 | 130 | 355 | 0.00030419 | 0.010689 | 35.1405
BOUQUET | 740 | 2220 | 1.1113 | 1440 | 22502 | 631 | 2379 | 0.00015509 | 0.052125 | 336.0849
BRAKEMAN | 1964 | 5892 | 1.0887 | 1440 | 2023.5 | 121 | 486 | 0.00041095 | 0.010056 | 24.4698
BRENNAN | 2497 | 7491 | 1.1388 | 1440 | 5333.3 | 836 | 2075 | 0.00052439 | 0.066473 | 126.7623
BROADCAST | 17 | 51 | 1.75 | 1440 | 7398.6 | 291 | 530 | 2.1952e-05 | 0.023632 | 6335.8821
BUCKHORN | 2768 | 8304 | 1.1224 | 1440 | 18755 | 432 | 1060 | 0.00058061 | 0.036484 | 62.8385
BURNS | 1800 | 5400 | 1.1272 | 1440 | 569.06 | 202 | 590 | 0.0003777 | 0.016193 | 42.8731
BUTTERFIELD | 1445 | 4335 | 1.0591 | 1440 | 13468 | 350 | 1420 | 0.00030169 | 0.029214 | 96.8332
CABANA | 2496 | 7488 | 1.1022 | 1440 | 522.56 | 101 | 554 | 0.00052278 | 0.0084116 | 16.0902
CALAMAR | 174 | 522 | 1.1753 | 1440 | 11626 | 814 | 970 | 3.6639e-05 | 0.065069 | 1775.9341
CALGROVE | 1180 | 3540 | 1.1946 | 1440 | 5881.6 | 637 | 2581 | 0.00024882 | 0.050732 | 203.8888
CALSTATE | 607 | 1821 | 1.144 | 1440 | 3313.2 | 475 | 2382 | 0.00012752 | 0.037656 | 295.2836
CAMP ANGELUS (DS OF BEAR VALLEY) | 316 | 948 | 1.4296 | 1440 | N/A | N/A | N/A | 6.7776e-05 | N/A | N/A
CANAL | 4 | 12 | 1.7789 | 1440 | 8248.6 | 217 | 589 | 0.0008927 | 0.01794 | 20400.3111
CARANCHO | 517 | 1551 | 1.0373 | 1440 | 26074 | 1200 | 598 | 0.00010777 | 0.097015 | 900.2218
CASSIDY | 1904 | 5712 | 1.0716 | 1440 | 8862.4 | 329 | 973 | 0.00039789 | 0.027116 | 68.1485
CASTRO | 2405 | 7215 | 1.2425 | 1440 | 13601 | 261 | 472 | 0.00054332 | 0.02244 | 44.0938
CEDAR GLEN (DS OF RIM) | 1468 | 4404 | 1.0596 | 1440 | N/A | N/A | N/A | 0.00071702 | N/A | N/A
CHAMPION | 1735 | 5205 | 1.0661 | 1440 | 2839.1 | 263 | 978 | 0.00036243 | 0.021218 | 58.5455
CHARDONNAY | 1081 | 3243 | 1.1785 | 1440 | 8030.4 | 1559 | 3561 | 0.00022768 | 0.12309 | 540.6424
CHAWA | 1194 | 3582 | 1.1263 | 1440 | 27298 | 1648 | 3397 | 0.00025052 | 0.13233 | 528.2056
CHEVELLE | 2247 | 6741 | 1.2019 | 1440 | 15111 | 776 | 3068 | 0.00047407 | 0.062876 | 132.6304
CLARINET | 1787 | 5361 | 1.21 | 1440 | 5629.7 | 396 | 1048 | 0.00037724 | 0.031958 | 84.7158
CONDOR | 1499 | 4497 | 1.5934 | 1440 | 9893.6 | 1063 | 1410 | 0.00032528 | 0.084584 | 260.0349
CONFERENCE (DS OF BEAR VALLEY) | 20 | 60 | 1 | 1440 | N/A | N/A | N/A | 4.1575e-06 | N/A | N/A
CONINE | 2014 | 6042 | 1.0867 | 1440 | 14695 | 439 | 1319 | 0.00042134 | 0.036422 | 86.4425
CORSAIR | 2540 | 7620 | 1.108 | 1440 | 11772 | 752 | 701 | 0.00053222 | 0.060661 | 113.9781
COTTAGE GROVE (DS OF RIM) | 429 | 1287 | 1.0676 | 1440 | N/A | N/A | N/A | 8.9624e-05 | N/A | N/A
CRAB | 0 | 0 | 0 | 1440 | 8163.3 | 102 | 203 | 0 | 0.030321 | INF
CRAM | 1315 | 3945 | 1.1495 | 1440 | 7958.6 | 215 | 709 | 0.00027638 | 0.017986 | 65.0766
CRESCENTA | 2627 | 7881 | 1.451 | 1440 | 1858.9 | 250 | 872 | 0.0005643 | 0.020248 | 35.8807
CRESTLINE (DS OF SAWPIT) | 793 | 2379 | 1.4195 | 1440 | N/A | N/A | N/A | 0.00016996 | N/A | N/A
CRUMNER | 1818 | 5454 | 1.0418 | 1440 | 2814.5 | 349 | 841 | 0.00037908 | 0.027958 | 73.7524
CRUMP (DS OF BEAR VALLEY) | 474 | 1422 | 1.3138 | 1440 | N/A | N/A | N/A | 0.00010082 | N/A | N/A
CUSHENBURY | 3 | 9 | 1.2105 | 1440 | 2816.4 | 14 | 0 | 8.5659e-07 | 0.0014247 | 2249.5506
CUTHBERT | 2408 | 7224 | 1.0775 | 1440 | 1585.4 | 704 | 896 | 0.00050343 | 0.055693 | 110.6259
DALBA (DS OF ROWCO) | 593 | 1779 | 1.1085 | 1440 | N/A | N/A | N/A | 0.00012426 | N/A | N/A
DARTMOUTH | 1399 | 4197 | 1.1994 | 1440 | 4476 | 350 | 1191 | 0.00029511 | 0.028155 | 95.407
DAVENPORT | 1462 | 4386 | 1.1518 | 1440 | 18716 | 1983 | 2184 | 0.00031939 | 0.15758 | 512.7478
DEACON | 1984 | 5952 | 1.1058 | 1440 | 9243.3 | 480 | 644 | 0.00041565 | 0.038987 | 93.798
DEL CARBON | 1504 | 4512 | 1.2331 | 1440 | 5629.8 | 207 | 364 | 0.00031803 | 0.017122 | 53.8367
DELUZ (DS OF LUISENO) | 248 | 744 | 1.0542 | 1440 | N/A | N/A | N/A | 5.176e-05 | N/A | N/A
DOBLE | 2 | 6 | 1 | 1440 | 4827.8 | 18 | 5 | 1.2626e-06 | 0.0019724 | 4744.1809
DONLON | 533 | 1599 | 1.1541 | 1440 | 2720.2 | 581 | 783 | 0.00011206 | 0.045865 | 409.2928
DUKE | 1149 | 3447 | 1.1157 | 1440 | 11749 | 419 | 862 | 0.00024089 | 0.034358 | 142.6265
DYSART (DS OF SADDLEBACK) | 73 | 219 | 1.3646 | 1440 | N/A | N/A | N/A | 1.5584e-05 | N/A | N/A
ENERGY | 1785 | 5355 | 1.3014 | 1440 | 16514 | 2062 | 3112 | 0.00037933 | 0.16356 | 431.1843
ESCALA (DS OF WILDOMAR) | 148 | 444 | 1.2614 | 1440 | N/A | N/A | N/A | 3.136e-05 | N/A | N/A
EVITA | 2888 | 8664 | 1.0597 | 1440 | 11681 | 412 | 2097 | 0.00060299 | 0.034115 | 56.5762
FERRARA | 1804 | 5412 | 1.2258 | 1440 | 13003 | 218 | 544 | 0.00038376 | 0.018898 | 49.5653
FINGAL | 846 | 2538 | 1.3493 | 1440 | 55838 | 1623 | 5559 | 0.00018041 | 0.13364 | 740.7848
FIREBIRD | 2772 | 8316 | 1 | 1440 | 6907 | 480 | 1330 | 0.00057623 | 0.038856 | 67.4319
FLYING D | 335 | 1005 | 1.0656 | 1440 | 4448.3 | 87 | 68 | 6.9976e-05 | 0.0073859 | 105.5493
GALAHAD | 2222 | 6666 | 1.1594 | 1440 | 6758.2 | 798 | 1154 | 0.00046734 | 0.063617 | 136.1253
GARBONI | 1387 | 4161 | 1.13 | 1440 | 2565.2 | 159 | 642 | 0.0002911 | 0.012988 | 44.6174
GILMAN | 12 | 36 | 1.4287 | 1440 | 3596 | 480 | 769 | 2.5736e-06 | 0.037973 | 14754.7606
GINGER | 951 | 2853 | 1.3596 | 1440 | 8288.9 | 496 | 1678 | 0.00020295 | 0.039942 | 196.8076
GRANNY SMITH | 322 | 966 | 1.0985 | 1440 | 15323 | 546 | 988 | 6.7423e-05 | 0.044561 | 660.919
GREEN BEAR (DS OF HEAPS PEAK) | 675 | 2025 | 1.293 | 1440 | N/A | N/A | N/A | 0.00014336 | N/A | N/A
GUITAR | 246 | 738 | 1.1983 | 1440 | 24247 | 634 | 2526 | 5.1887e-05 | 0.052474 | 1011.3175
GUNSITE (DS OF STUBBY) | 4 | 12 | 1.75 | 1440 | N/A | N/A | N/A | 8.7762e-07 | N/A | N/A
HEAPS PEAK | 0 | 0 | 0 | 1440 | 9854.7 | 124 | 211 | 0 | 0.030321 | INF
HELICOPTER | 1812 | 5436 | 1.1854 | 1440 | 525.42 | 299 | 1406 | 0.00038183 | 0.023778 | 62.2741
HI LINE | 131 | 393 | 1.2976 | 1440 | 2212.7 | 41 | 157 | 2.7831e-05 | 0.0034895 | 125.3803
HIGH SCHOOL (DS OF RIM) | 326 | 978 | 1.3196 | 1440 | N/A | N/A | N/A | 6.9369e-05 | N/A | N/A
HIGHBALL | 1670 | 5010 | 1.1312 | 1440 | 2305 | 269 | 1410 | 0.00035052 | 0.021614 | 61.6621
HILLFIELD | 2075 | 6225 | 1.0956 | 1440 | 1788.5 | 460 | 2322 | 0.00043439 | 0.036568 | 84.1828
HONEYCRISP | 2161 | 6483 | 1.1645 | 1440 | 14468 | 385 | 987 | 0.00045468 | 0.03071 | 67.5405
HOOLIGAN | 3210 | 9630 | 1.1503 | 1440 | 14507 | 312 | 940 | 0.00067469 | 0.02668 | 39.5439
HORNTOAD | 1462 | 4386 | 1.4196 | 1440 | 10015 | 676 | 2024 | 0.00031334 | 0.054317 | 173.3448
HUCKLEBERRY | 174 | 522 | 1.1527 | 1440 | 26416 | 981 | 864 | 3.6579e-05 | 0.079861 | 2183.2601
HUGO | 56 | 168 | 1.4245 | 1440 | 9724.6 | 265 | 691 | 1.2006e-05 | 0.021877 | 1822.0945
ICE HOUSE (DS OF FERRARA) | 12 | 36 | 1 | 1440 | N/A | N/A | N/A | 2.4945e-06 | N/A | N/A
INDEPENDENCE | 2195 | 6585 | 1.0319 | 1440 | 597.51 | 185 | 774 | 0.00045736 | 0.014938 | 32.66
INTERIOR | 1182 | 3546 | 1.1558 | 1440 | 2105.1 | 24 | 61 | 0.00024854 | 0.0023362 | 9.3995
INTERN | 2070 | 6210 | 1.0679 | 1440 | 7236 | 485 | 1225 | 0.00043246 | 0.039159 | 90.5498
IRAN | 1616 | 4848 | 1.2064 | 1440 | 211.76 | 91 | 340 | 0.00034105 | 0.0074346 | 21.7989
JARVIS | 976 | 2928 | 1.1273 | 1440 | 12988 | 148 | 372 | 0.0002048 | 0.013271 | 64.8
JEEP | 1433 | 4299 | 1.2371 | 1440 | 7190.6 | 175 | 202 | 0.00030311 | 0.014788 | 48.7883
JENKS LAKE (DS OF BEAR VALLEY) | 112 | 336 | 1.0341 | 1440 | N/A | N/A | N/A | 2.3341e-05 | N/A | N/A
JUBILEE | 509 | 1527 | 1.1055 | 1440 | 9164 | 224 | 869 | 0.00036114 | 0.018686 | 175.231
KINSEY | 113 | 339 | 1.3436 | 1440 | 10261 | 66 | 34 | 2.4087e-05 | 0.006382 | 264.9587
KUFFEL (DS OF RIM) | 548 | 1644 | 1.2038 | 1440 | N/A | N/A | N/A | 0.00011563 | N/A | N/A
KULBERG (DS OF SKINNER) | 2442 | 7326 | 1.0646 | 1440 | N/A | N/A | N/A | 0.00051005 | N/A | N/A
LA GRANDE | 1649 | 4947 | 1.1128 | 1440 | 1444.3 | 397 | 1050 | 0.00034565 | 0.031523 | 91.2001
LA SIERRA | 346 | 1038 | 1.1592 | 1440 | 3500.2 | 671 | 1476 | 7.2772e-05 | 0.052964 | 727.8071
LACRESTA (DS OF WILDOMAR) | 487 | 1461 | 1.0572 | 1440 | N/A | N/A | N/A | 0.00010166 | N/A | N/A
LAKELAND | 929 | 2787 | 1.2023 | 1440 | 4107 | 518 | 1745 | 0.00019601 | 0.04117 | 210.0464
LARCH | 13 | 39 | 1.6316 | 1440 | 2659.4 | 254 | 1014 | 0.00071938 | 0.020183 | 7135.4665
LAUDA | 2 | 6 | 2 | 1440 | 8434.5 | 1022 | 1680 | 1.3222e-05 | 0.080937 | 181269.698
LAZARO | 2137 | 6411 | 1.0411 | 1440 | 3083.3 | 577 | 1041 | 0.00044558 | 0.045884 | 102.9755
LIMITED | 2117 | 6351 | 1.0961 | 1440 | 27849 | 656 | 2597 | 0.0004432 | 0.054953 | 123.9917
LIMONITE | 3 | 9 | 1 | 1440 | 2341.7 | 319 | 1120 | 0.0010214 | 0.02523 | 40456.2517
LIVERMORE | 2262 | 6786 | 1.0485 | 1440 | 526.47 | 77 | 228 | 0.0004719 | 0.0064924 | 13.758
LOCKNER | 2043 | 6129 | 1.0603 | 1440 | 5906.7 | 564 | 1977 | 0.00042658 | 0.04518 | 105.9103
LOPEZ | 1817 | 5451 | 1.0696 | 1440 | 7885.7 | 874 | 2890 | 0.00037965 | 0.069621 | 183.3814
LOUCKS (DS OF DAVENPORT) | 57 | 171 | 1.0124 | 1440 | N/A | N/A | N/A | 1.186e-05 | N/A | N/A
LUISENO | 21 | 63 | 1.9566 | 1440 | 16331 | 1484 | 3442 | 0.00014483 | 0.11801 | 25245.882
LURING (DS OF ROWCO) | 368 | 1104 | 1.1606 | 1440 | N/A | N/A | N/A | 7.7407e-05 | N/A | N/A
MACIEL | 2312 | 6936 | 1.1304 | 1440 | 9633 | 326 | 1374 | 0.00048524 | 0.027044 | 55.7336
MAGUIRE | 700 | 2100 | 1.2463 | 1440 | 4185 | 785 | 925 | 0.00014816 | 0.062026 | 418.6313
MAIZE | 932 | 2796 | 1.128 | 1440 | 5725.2 | 155 | 554 | 0.00019557 | 0.012962 | 66.2778
MAMBA | 2166 | 6498 | 1.0939 | 1440 | 9240.7 | 403 | 2208 | 0.00045338 | 0.032996 | 72.7774
MERLIN | 999 | 2997 | 1.1294 | 1440 | 2821.7 | 710 | 896 | 0.00020965 | 0.056053 | 267.358
METTLER | 832 | 2496 | 1.2032 | 1440 | 11254 | 969 | 3191 | 0.00017555 | 0.077269 | 440.1543
MILO | 2038 | 6114 | 1.0472 | 1440 | 4994.8 | 288 | 1048 | 0.00042513 | 0.023481 | 55.2316
MORELAND | 2076 | 6228 | 1.0711 | 1440 | 4400.8 | 220 | 600 | 0.00043382 | 0.018098 | 41.7187
MORELLO | 44 | 132 | 1.1269 | 1440 | 11083 | 185 | 613 | 9.2323e-06 | 0.015775 | 1708.6732
MORGANSTEIN | 1778 | 5334 | 1.1493 | 1440 | 10365 | 1014 | 2130 | 0.00037368 | 0.080856 | 216.377
MULHOLLAND | 655 | 1965 | 1.2913 | 1440 | 1445.5 | 209 | 479 | 0.00013909 | 0.016637 | 119.611
NAPOLEON | 3083 | 9249 | 1.1034 | 1440 | 11928 | 1638 | 3926 | 0.00064578 | 0.13009 | 201.4456
NATIONS | 531 | 1593 | 1.2983 | 1440 | 1782 | 810 | 1807 | 0.00011282 | 0.06367 | 564.366
NAYLOR | 1726 | 5178 | 1 | 1440 | 1517.2 | 375 | 1452 | 0.00035879 | 0.029824 | 83.1241
NORTH SHORE (DS OF RIM) | 1799 | 5397 | 1.0575 | 1440 | N/A | N/A | N/A | 0.00044493 | N/A | N/A
NORTHPARK | 2253 | 6759 | 1.1515 | 1440 | 6404.6 | 821 | 1532 | 0.00047359 | 0.065381 | 138.0538
OAK KNOLL (DS OF HEAPS PEAK) | 497 | 1491 | 1.338 | 1440 | N/A | N/A | N/A | 0.0001059 | N/A | N/A
OBSERVATORY (DS OF BROADCAST) | 4 | 12 | 2 | 1440 | N/A | N/A | N/A | 8.93e-07 | N/A | N/A
OLIVER | 5 | 15 | 1 | 1440 | 7196 | 1243 | 2832 | 0.0013061 | 0.098082 | 94366.0461
OZARK | 3 | 9 | 2 | 1440 | N/A | N/A | N/A | 6.6975e-07 | N/A | 45272.2851
PASCAL | 1758 | 5274 | 1.1397 | 1440 | 13622 | 1585 | 1794 | 0.00036922 | 0.1259 | 340.9951
PATRIOT | 2654 | 7962 | 1.0399 | 1440 | 14015 | 588 | 964 | 0.00055333 | 0.048114 | 86.9542
PAWNEE | 2391 | 7173 | 1.2025 | 1440 | 11552 | 1497 | 3220 | 0.00050447 | 0.11889 | 235.672
PENSTOCK | 2136 | 6408 | 1.3216 | 1440 | 4986 | 455 | 816 | 0.00045458 | 0.036562 | 80.429
PERRIS | 711 | 2133 | 1.1469 | 1440 | 5417.3 | 1188 | 2975 | 0.0001494 | 0.093698 | 627.1442
PHEASANT (DS OF STUBBY) | 185 | 555 | 1.3297 | 1440 | N/A | N/A | N/A | 3.9395e-05 | N/A | N/A
PHOTON | 1892 | 5676 | 1.0122 | 1440 | 1108.9 | 149 | 428 | 0.00039365 | 0.012126 | 30.8047
PICK | 1003 | 3009 | 1.0882 | 1440 | 11053 | 1129 | 1155 | 0.00020986 | 0.089794 | 427.8768
PICONI | 1241 | 3723 | 1.1736 | 1440 | 6194.5 | 1150 | 2860 | 0.00026128 | 0.090912 | 347.9419
PINE COVE (DS OF CANAL) | 1464 | 4392 | 1.2111 | 1440 | N/A | N/A | N/A | 0.00030908 | N/A | N/A
PLATEAU | 2114 | 6342 | 1.2216 | 1440 | 5024.5 | 415 | 648 | 0.00044665 | 0.033433 | 74.8528
PONY (DS OF SKINNER) | 3 | 9 | 2 | 1440 | N/A | N/A | N/A | 6.6975e-07 | N/A | N/A
POPPET FLATS (DS OF STUBBY) | 683 | 2049 | 1.2774 | 1440 | N/A | N/A | N/A | 0.00014489 | N/A | N/A
POTTERY | 793 | 2379 | 1.1043 | 1440 | 419.76 | 103 | 453 | 0.00016612 | 0.0082495 | 49.6609
PRONGHORN | 974 | 2922 | 1.2417 | 1440 | 4242 | 192 | 430 | 0.00020609 | 0.015691 | 76.1368
PURCHASE (DS OF STUBBY) | 97 | 291 | 1.0992 | 1440 | N/A | N/A | N/A | 2.0312e-05 | N/A | N/A
PYTHON | 1469 | 4407 | 1.1379 | 1440 | 10684 | 805 | 2671 | 0.00030848 | 0.064488 | 209.0473
RAMAC | 1420 | 4260 | 1.1189 | 1440 | 12466 | 364 | 567 | 0.000298 | 0.030187 | 101.3756
RED BOX (DS OF BROADCAST) | 27 | 81 | 1.2589 | 1440 | N/A | N/A | N/A | 5.7201e-06 | N/A | N/A
REJADA | 465 | 1395 | 1.0604 | 1440 | 6075.6 | 611 | 992 | 9.7094e-05 | 0.048592 | 500.4659
RESORT | 6 | 18 | 1.9474 | 1440 | 12744 | 262 | 565 | 3.0532e-05 | 0.021986 | 16473.2445
RICARDO | 3451 | 10353 | 1.0553 | 1440 | 1113.6 | 69 | 474 | 0.00072031 | 0.0061491 | 8.5368
RIM (DS OF SHAKE) | 1890 | 5670 | 1.2077 | 1440 | N/A | N/A | N/A | 0.00099717 | N/A | N/A
ROCKWELL | 1581 | 4743 | 2 | 1440 | 538.06 | 91 | 290 | 0.00035296 | 0.0074664 | 21.1537
ROS | 2735 | 8205 | 1.1038 | 1440 | 2959.7 | 495 | 991 | 0.0005729 | 0.039562 | 69.0554
ROTEC | 1961 | 5883 | 1.0377 | 1440 | 7611.5 | 1300 | 2184 | 0.00040878 | 0.10294 | 251.827
ROUNDEL | 1520 | 4560 | 1.1134 | 1440 | 12509 | 736 | 1866 | 0.00031862 | 0.059312 | 186.1527
ROWCO | 1275 | 3825 | 1.4316 | 1440 | 4185.7 | 138 | 339 | 0.00067866 | 0.011514 | 42.0991
RUSTIC | 3099 | 9297 | 1.202 | 1440 | 6601.3 | 660 | 2368 | 0.00065383 | 0.052961 | 81.0009
SADDLEBACK | 8 | 24 | 1.0066 | 1440 | 18925 | 1294 | 3331 | 1.7248e-05 | 0.10344 | 62171.7092
SAND CANYON | 2206 | 6618 | 1.1832 | 1440 | 15376 | 1156 | 3333 | 0.00046479 | 0.092627 | 199.2902
SANTORINI | 1385 | 4155 | 1.318 | 1440 | 2725.5 | 323 | 881 | 0.00029468 | 0.025836 | 87.6754
SAUGUS-MOORPARK-SANTA SUSANA-TORREY | 1 | 3 | 2 | 1440 | 9043 | 137 | 381 | 2.2325e-07 | 0.030321 | 135815.2428
SAUNDERS (DS OF CANAL) | 2775 | 8325 | 1.1381 | 1440 | N/A | N/A | N/A | 0.00058274 | N/A | N/A
SAWPIT | 0 | 0 | 0 | 1440 | 7616.5 | 98 | 196 | 0 | 0.030321 | INF
SCHMIDT | 1369 | 4107 | 1.1082 | 1440 | 12288 | 1195 | 2522 | 0.00028686 | 0.095167 | 331.7565
SCOUT (DS OF DOBLE) | 3 | 9 | 1 | 1440 | N/A | N/A | N/A | 6.2363e-07 | N/A | N/A
SEELEY (DS OF SAWPIT) | 743 | 2229 | 1.2766 | 1440 | N/A | N/A | N/A | 0.00015761 | N/A | N/A
SERRA | 288 | 864 | 1.2325 | 1440 | 2406.4 | 224 | 556 | 6.0898e-05 | 0.017857 | 293.2213
SEYMOUR (DS OF CRAB) | 4 | 12 | 1 | 1440 | N/A | N/A | N/A | 8.315e-07 | N/A | N/A
SHAKE | 0 | 0 | 0 | 1440 | 7154.4 | 98 | 37 | 0 | 0.030321 | INF
SHOVEL | 725 | 2175 | 1.1683 | 1440 | 9555.5 | 1469 | 1534 | 0.00015259 | 0.11617 | 761.3229
SHOWDOWN | 1362 | 4086 | 1.3369 | 1440 | 18039 | 1071 | 1087 | 0.00029018 | 0.086137 | 296.8388
SIENNA | 932 | 2796 | 1.152 | 1440 | 5002.8 | 305 | 1094 | 0.00019592 | 0.024612 | 125.6259
SKINNER (DS OF LUISENO) | 1 | 3 | 2 | 1440 | N/A | N/A | N/A | 0.0008561 | N/A | N/A
SKY HI | 1689 | 5067 | 1.1694 | 1440 | 4720.6 | 510 | 212 | 0.0003555 | 0.040753 | 114.6354
SKYLAND (DS OF SAWPIT) | 847 | 2541 | 1.1527 | 1440 | N/A | N/A | N/A | 0.00017806 | N/A | N/A
SNOW VALLEY (DS OF HEAPS PEAK) | 954 | 2862 | 1.1911 | 1440 | N/A | N/A | N/A | 0.00048783 | N/A | N/A
SOGGY | 1063 | 3189 | 1.182 | 1440 | 981 | 471 | 1143 | 0.00022395 | 0.037152 | 165.8993
SONOMA | 2207 | 6621 | 1.1913 | 1440 | 5090.9 | 1152 | 2182 | 0.00046527 | 0.091113 | 195.8286
SQUINT | 1214 | 3642 | 1.418 | 1440 | 6145.7 | 90 | 74 | 0.00026016 | 0.0079771 | 30.6619
STAGHORN | 1465 | 4395 | 1.1224 | 1440 | 671.26 | 322 | 976 | 0.00030729 | 0.025532 | 83.0876
STARGLOW | 2442 | 7326 | 1.2223 | 1440 | 9208.7 | 1296 | 3593 | 0.00051598 | 0.1029 | 199.4305
STEEL (DS OF LAUDA) | 36 | 108 | 1.2612 | 1440 | N/A | N/A | N/A | 7.6281e-06 | N/A | N/A
STORES | 716 | 2148 | 1.1026 | 1440 | 18919 | 2957 | 8325 | 0.00014997 | 0.23367 | 1558.0989
STRATHERN | 2669 | 8007 | 1.1176 | 1440 | 3629.7 | 590 | 1896 | 0.00055964 | 0.04706 | 84.0899
STUBBY | 7 | 21 | 1.6666 | 1440 | 17322 | 3586 | 9566 | 0.00053738 | 0.28256 | 185057.8644
SUNDANCE | 1689 | 5067 | 1.0866 | 1440 | 475.15 | 133 | 426 | 0.00035335 | 0.010764 | 30.4631
SUTT | 1843 | 5529 | 1.1304 | 1440 | 5093.9 | 330 | 1361 | 0.00038681 | 0.026743 | 69.1366
TACKLE | 689 | 2067 | 1.065 | 1440 | 6382.9 | 274 | 788 | 0.00014391 | 0.022305 | 154.9854
TAGGERT | 632 | 1896 | 1.2805 | 1440 | 3630.3 | 208 | 285 | 0.0003459 | 0.01681 | 125.3493
TAHQUITZ | 140 | 420 | 1.0441 | 1440 | 23304 | 280 | 316 | 2.9197e-05 | 0.024652 | 844.3065
TAIWAN | 690 | 2070 | 1.3691 | 1440 | 8546 | 420 | 1406 | 0.00014735 | 0.033979 | 230.6026
TEJON | 494 | 1482 | 1.2441 | 1440 | 14366 | 250 | 174 | 0.00010454 | 0.021324 | 203.9751
TERRA COTTA | 4 | 12 | 1.1666 | 1440 | 5232.8 | 307 | 1109 | 8.4174e-07 | 0.024629 | 29259.0249
TIMBER CANYON | 700 | 2100 | 1.1228 | 1440 | 7899.3 | 183 | 493 | 0.0001512 | 0.015365 | 104.6407
TIVO (DS OF BROADCAST) | 52 | 156 | 2 | 1440 | N/A | N/A | N/A | 1.2502e-05 | N/A | N/A
TRUMBLE | 857 | 2571 | 1.0897 | 1440 | 3502.1 | 299 | 912 | 0.00017933 | 0.023954 | 133.575
TUNGSTEN | 1645 | 4935 | 2 | 1440 | 3292.3 | 38 | 22 | 0.00036791 | 0.0036534 | 9.9481
URBITA | 2042 | 6126 | 1.2384 | 1440 | 4073 | 330 | 963 | 0.00043197 | 0.026659 | 61.7161
VENGEANCE | 1285 | 3855 | 1.0901 | 1440 | 7697 | 225 | 845 | 0.0002689 | 0.018732 | 69.6624
VERA CRUZ | 1739 | 5217 | 1.1381 | 1440 | 5189.1 | 343 | 929 | 0.00036519 | 0.027752 | 75.9943
VERDEMONT | 15 | 45 | 1.6157 | 1440 | 14029 | 746 | 1965 | 6.6927e-05 | 0.060001 | 18404.5886
VERDUGO | 3032 | 9096 | 1.0958 | 1440 | 13055 | 966 | 2439 | 0.00063474 | 0.077641 | 122.3188
VETERANS | 2299 | 6897 | 1.0959 | 1440 | 1767.8 | 306 | 1342 | 0.0004813 | 0.024559 | 51.0265
WARHAWK | 1906 | 5718 | 1.1181 | 1440 | 13066 | 362 | 1875 | 0.00039967 | 0.030189 | 75.5336
WEESHA (DS OF BEAR VALLEY) | 54 | 162 | 1.0019 | 1440 | N/A | N/A | N/A | 1.1227e-05 | N/A | N/A
WESTBROOK | 662 | 1986 | 2 | 1440 | 10674 | 530 | 890 | 0.00014779 | 0.042828 | 289.7864
WILDOMAR | 2 | 6 | 2 | 1440 | 16327 | 402 | 312 | 4.465e-07 | 0.030321 | 141878.3806
WINERY | 877 | 2631 | 1.0695 | 1440 | 8824.7 | 1211 | 1737 | 0.00018324 | 0.095926 | 523.4873
WOBEGONE | 1198 | 3594 | 1.2878 | 1440 | 9781.1 | 1663 | 3375 | 0.00025433 | 0.13146 | 516.8587
YANKEE (DS OF TUNGSTEN) | 3 | 9 | 1.8 | 1440 | N/A | N/A | N/A | 6.6053e-07 | N/A | N/A
ZEVO (DS OF SKINNER) | 894 | 2682 | 1.0132 | 1440 | N/A | N/A | N/A | 0.00018602 | N/A | N/A
ZONE | 952 | 2856 | 1.1704 | 1440 | 5125.8 | 419 | 929 | 0.00020039 | 0.033549 | 167.4152

## T05
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 03: De-Energized Time, Place, Duration and Customers
Circuits De-Energized
County | Circuit Name | De-energization Date | De-energization Time (2400) | All Clear Declaration Date | All Clear Declaration Time (2400) | Restoration Date | Restoration Time (2400) | GO 95, Tier HFTD Tier(s) 1,2,3 | Distribution / Transmission Classification
SAN BERNARDINO | ACOSTA | 2025-01-21 08:02 | 45678.3347 | 2025-01-24 01:45 | 45681.0729 | 2025-01-24 15:49 | 45681.659 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | ALLVIEW | 2025-01-22 16:25 | 45679.684 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 00:27 | 45681.0188 | T3 | Distribution
SAN BERNARDINO | ALPINE | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:45 | 45680.7812 | 2025-01-24 04:54 | 45681.2042 | T3 | Distribution
SAN BERNARDINO | AMETHYST | 2025-01-20 20:54 | 45677.8708 | 2025-01-21 08:52 | 45678.3694 | 2025-01-21 11:04 | 45678.4611 | Non HFRA, T3, T2 | Distribution
VENTURA | ANGUS | 2025-01-20 11:14 | 45677.4681 | 2025-01-21 14:40 | 45678.6111 | 2025-01-24 14:19 | 45681.5965 | Non HFRA, T3, T2 | Distribution
VENTURA | ANTON | 2025-01-21 07:07 | 45678.2965 | 2025-01-21 16:42 | 45678.6958 | 2025-01-24 15:16 | 45681.6361 | T3 | Distribution
RIVERSIDE | ARAPAHO | 2025-01-23 12:53 | 45680.5368 | 2025-01-24 00:17 | 45681.0118 | 2025-01-24 03:11 | 45681.1326 | Non HFRA, T2 | Distribution
RIVERSIDE | ARCHIE | 2025-01-23 13:05 | 45680.5451 | 2025-01-23 20:29 | 45680.8535 | 2025-01-23 22:58 | 45680.9569 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | ARMADA | 2025-01-23 10:48 | 45680.45 | 2025-01-24 00:42 | 45681.0292 | 2025-01-24 03:11 | 45681.1326 | Non HFRA, T3 | Distribution
ORANGE | ATENTO | 2025-01-21 06:36 | 45678.275 | 2025-01-23 20:46 | 45680.8653 | 2025-01-24 16:24 | 45681.6833 | T3 | Distribution
ORANGE | ATLANTA | 2025-01-23 06:24 | 45680.2667 | 2025-01-23 14:19 | 45680.5965 | 2025-01-23 16:20 | 45680.6806 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | AVIATOR | 2025-01-20 20:08 | 45677.8389 | 2025-01-21 12:30 | 45678.5208 | 2025-01-21 16:45 | 45678.6979 | Non HFRA, T2 | Distribution
VENTURA | BALCOM | 2025-01-21 04:05 | 45678.1701 | 2025-01-21 16:05 | 45678.6701 | 2025-01-21 19:34 | 45678.8153 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | BEAR VALLEY | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 10:30 | 45678.4375 | T3, T2 | Distribution
VENTURA | BELPAC | 2025-01-21 06:06 | 45678.2542 | 2025-01-23 23:28 | 45680.9778 | 2025-01-24 03:37 | 45681.1507 | T3 | Distribution
SAN BERNARDINO | BIG FALLS | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 09:53 | 45678.4118 | T3 | Distribution
LOS ANGELES;VENTURA | BIG ROCK | 2025-01-23 08:55 | 45680.3715 | 2025-01-23 19:15 | 45680.8021 | 2025-01-24 13:19 | 45681.5549 | T3 | Distribution
RIVERSIDE | BLACKHILLS | 2025-01-20 18:48 | 45677.7833 | 2025-01-21 08:58 | 45678.3736 | 2025-01-21 12:42 | 45678.5292 | Non HFRA, T2 | Distribution
KERN;LOS ANGELES | BLEDSOE | 2025-01-20 15:39 | 45677.6521 | 2025-01-20 17:52 | 45677.7444 | 2025-01-20 21:53 | 45677.9118 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | BLUE CUT | 2025-01-20 11:27 | 45677.4771 | 2025-01-24 09:07 | 45681.3799 | 2025-01-24 11:11 | 45681.466 | T3, T2 | Distribution
RIVERSIDE | BONNEVILLE | 2025-01-23 13:05 | 45680.5451 | 2025-01-24 01:08 | 45681.0472 | 2025-01-24 10:03 | 45681.4187 | Non HFRA, T2 | Distribution
LOS ANGELES | BOOTLEGGER | 2025-01-20 05:39 | 45677.2354 | 2025-01-26 06:57 | 45683.2896 | 2025-01-27 14:34 | 45684.6069 | T3 | Distribution
VENTURA | BORCHARD | 2025-01-23 12:10 | 45680.5069 | 2025-01-23 18:39 | 45680.7771 | 2025-01-23 21:05 | 45680.8785 | T3 | Distribution
SAN BERNARDINO | BOULDER | 2025-01-20 14:49 | 45677.6174 | 2025-01-21 08:49 | 45678.3674 | 2025-01-21 10:41 | 45678.4451 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | BOUQUET | 2025-01-20 15:48 | 45677.6583 | 2025-01-21 11:25 | 45678.4757 | 2025-01-21 13:13 | 45678.5507 | T3 | Distribution
LOS ANGELES;ORANGE | BRAKEMAN | 2025-01-23 09:08 | 45680.3806 | 2025-01-24 01:31 | 45681.0632 | 2025-01-24 05:45 | 45681.2396 | Non HFRA, T3, T2 | Distribution
VENTURA | BRENNAN | 2025-01-21 06:25 | 45678.2674 | 2025-01-23 17:26 | 45680.7264 | 2025-01-23 17:54 | 45680.7458 | T3 | Distribution
LOS ANGELES | BROADCAST | 2025-01-20 10:22 | 45677.4319 | 2025-01-21 14:22 | 45678.5986 | 2025-01-24 11:34 | 45681.4819 | T3 | Distribution
VENTURA | BUCKHORN | 2025-01-23 11:01 | 45680.459 | 2025-01-23 18:55 | 45680.7882 | 2025-01-24 15:08 | 45681.6306 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | BURNS | 2025-01-23 13:30 | 45680.5625 | 2025-01-23 16:58 | 45680.7069 | 2025-01-23 18:04 | 45680.7528 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | BUTTERFIELD | 2025-01-22 23:01 | 45679.959 | 2025-01-23 21:57 | 45680.9146 | 2025-01-23 23:48 | 45680.9917 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | CABANA | 2025-01-20 21:48 | 45677.9083 | 2025-01-23 17:21 | 45680.7229 | 2025-01-23 17:40 | 45680.7361 | Non HFRA, T2 | Distribution
RIVERSIDE | CALAMAR | 2025-01-21 08:08 | 45678.3389 | 2025-01-24 01:05 | 45681.0451 | 2025-01-24 08:07 | 45681.3382 | T3 | Distribution
LOS ANGELES | CALGROVE | 2025-01-20 23:01 | 45677.959 | 2025-01-24 10:00 | 45681.4167 | 2025-01-24 10:50 | 45681.4514 | T3 | Distribution
SAN BERNARDINO | CALSTATE | 2025-01-21 01:04 | 45678.0444 | 2025-01-21 20:22 | 45678.8486 | 2025-01-24 13:34 | 45681.5653 | T3, T2 | Distribution
SAN BERNARDINO | CAMP ANGELUS | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 10:30 | 45678.4375 | T3 | Distribution
RIVERSIDE | CANAL | 2025-01-20 17:56 | 45677.7472 | 2025-01-21 07:58 | 45678.3319 | 2025-01-21 12:39 | 45678.5271 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | CARANCHO | 2025-01-23 10:54 | 45680.4542 | 2025-01-24 00:58 | 45681.0403 | 2025-01-24 09:41 | 45681.4035 | T3 | Distribution
VENTURA | CASSIDY | 2025-01-23 11:32 | 45680.4806 | 2025-01-23 17:23 | 45680.7243 | 2025-01-23 19:54 | 45680.8292 | T3 | Distribution
VENTURA | CASTRO | 2025-01-23 10:20 | 45680.4306 | 2025-01-23 17:16 | 45680.7194 | 2025-01-24 14:28 | 45681.6028 | Non HFRA, T3 | Distribution
SAN BERNARDINO | CEDAR GLEN | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:45 | 45680.7812 | 2025-01-24 02:55 | 45681.1215 | T3 | Distribution
SAN BERNARDINO | CHAMPION | 2025-01-20 18:56 | 45677.7889 | 2025-01-20 20:10 | 45677.8403 | 2025-01-21 09:04 | 45678.3778 | T2 | Distribution
RIVERSIDE | CHARDONNAY | 2025-01-21 09:37 | 45678.4007 | 2025-01-24 00:57 | 45681.0396 | 2025-01-24 09:47 | 45681.4076 | T3 | Distribution
RIVERSIDE | CHAWA | 2025-01-21 09:44 | 45678.4056 | 2025-01-24 00:53 | 45681.0368 | 2025-01-24 14:49 | 45681.6174 | T3, T2 | Distribution
SAN BERNARDINO | CHEVELLE | 2025-01-20 10:45 | 45677.4479 | 2025-01-24 07:25 | 45681.309 | 2025-01-24 12:43 | 45681.5299 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | CLARINET | 2025-01-20 13:37 | 45677.5674 | 2025-01-21 14:36 | 45678.6083 | 2025-01-24 14:11 | 45681.591 | T3, T2 | Distribution
KERN | CONDOR | 2025-01-20 13:57 | 45677.5813 | 2025-01-20 17:21 | 45677.7229 | 2025-01-20 21:13 | 45677.884 | T3, T2 | Distribution
SAN BERNARDINO | CONFERENCE | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 09:53 | 45678.4118 | T3 | Distribution
RIVERSIDE;SAN BERNARDINO | CONINE | 2025-01-23 10:08 | 45680.4222 | 2025-01-24 01:35 | 45681.066 | 2025-01-24 06:03 | 45681.2521 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | CORSAIR | 2025-01-20 17:54 | 45677.7458 | 2025-01-21 13:05 | 45678.5451 | 2025-01-21 20:46 | 45678.8653 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | COTTAGE GROVE | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:45 | 45680.7812 | 2025-01-24 02:55 | 45681.1215 | T3 | Distribution
SAN BERNARDINO | CRAB | 2025-01-22 | 16:05 | 2025-01-23 | 18:45 | 2025-01-23 | 23:26 | T3 | Distribution
SAN BERNARDINO | CRAM | 2025-01-22 22:59 | 45679.9576 | 2025-01-23 14:11 | 45680.591 | 2025-01-23 15:42 | 45680.6542 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | CRESCENTA | 2025-01-23 06:33 | 45680.2729 | 2025-01-23 14:54 | 45680.6208 | 2025-01-23 16:11 | 45680.6743 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | CRESTLINE | 2025-01-25 04:50 | 45682.2014 | 2025-01-25 07:15 | 45682.3021 | 2025-01-25 09:14 | 45682.3847 | T3 | Distribution
LOS ANGELES | CRUMNER | 2025-01-23 11:02 | 45680.4597 | 2025-01-23 18:00 | 45680.75 | 2025-01-23 20:39 | 45680.8604 | T3 | Distribution
SAN BERNARDINO | CRUMP | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 09:55 | 45678.4132 | T3 | Distribution
SAN BERNARDINO | CUSHENBURY | 2025-01-25 12:58 | 45682.5403 | 2025-01-25 15:47 | 45682.6576 | 2025-01-25 16:28 | 45682.6861 | Non HFRA, T2 | Distribution
LOS ANGELES | CUTHBERT | 2025-01-21 00:19 | 45678.0132 | 2025-01-24 00:21 | 45681.0146 | 2025-01-24 09:38 | 45681.4014 | T3 | Distribution
SAN BERNARDINO | DALBA | 2025-01-20 10:21 | 45677.4313 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 02:06 | 45681.0875 | T3 | Distribution
RIVERSIDE | DARTMOUTH | 2025-01-20 20:03 | 45677.8354 | 2025-01-21 13:03 | 45678.5437 | 2025-01-23 18:40 | 45680.7778 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | DAVENPORT | 2025-01-20 09:19 | 45677.3882 | 2025-01-23 17:39 | 45680.7354 | 2025-01-24 00:59 | 45681.041 | T3 | Distribution
RIVERSIDE | DEACON | 2025-01-21 12:42 | 45678.5292 | 2025-01-23 23:33 | 45680.9812 | 2025-01-24 00:19 | 45681.0132 | Non HFRA, T2 | Distribution
ORANGE/SAN BERNARDINO | DEL CARBON | 2025-01-23 08:43 | 45680.3632 | 2025-01-23 14:40 | 45680.6111 | 2025-01-23 18:13 | 45680.759 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | DELUZ | 2025-01-21 09:07 | 45678.3799 | 2025-01-24 00:23 | 45681.016 | 2025-01-24 05:33 | 45681.2312 | T3 | Distribution
SAN BERNARDINO | DOBLE | 2025-01-25 13:14 | 45682.5514 | 2025-01-25 15:36 | 45682.65 | 2025-01-26 13:49 | 45683.5757 | Non HFRA, T2 | Distribution
VENTURA | DONLON | 2025-01-23 10:08 | 45680.4222 | 2025-01-24 00:19 | 45681.0132 | 2025-01-24 12:35 | 45681.5243 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | DUKE | 2025-01-21 10:05 | 45678.4201 | 2025-01-24 05:06 | 45681.2125 | 2025-01-24 08:59 | 45681.3743 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | DYSART | 2025-01-20 16:30 | 45677.6875 | 2025-01-24 10:04 | 45681.4194 | 2025-01-24 13:16 | 45681.5528 | Non HFRA, T3, T2 | Distribution
LOS ANGELES;VENTURA | ENERGY | 2025-01-21 04:00 | 45678.1667 | 2025-01-24 10:00 | 45681.4167 | 2025-01-24 13:24 | 45681.5583 | T3 | Distribution
RIVERSIDE | ESCALA | 2025-01-21 10:31 | 45678.4382 | 2025-01-21 15:20 | 45678.6389 | 2025-01-21 17:25 | 45678.7257 | T3 | Distribution
VENTURA | EVITA | 2025-01-23 11:34 | 45680.4819 | 2025-01-23 20:30 | 45680.8542 | 2025-01-24 12:58 | 45681.5403 | T3, T2 | Distribution
LOS ANGELES;SAN BERNARDINO | FERRARA | 2025-01-23 03:47 | 45680.1576 | 2025-01-23 14:33 | 45680.6062 | 2025-01-23 19:26 | 45680.8097 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | FINGAL | 2025-01-20 09:30 | 45677.3958 | 2025-01-23 21:49 | 45680.909 | 2025-01-24 09:12 | 45681.3833 | T3 | Distribution
SAN BERNARDINO | FIREBIRD | 2025-01-21 00:19 | 45678.0132 | 2025-01-24 07:25 | 45681.309 | 2025-01-24 10:22 | 45681.4319 | Non HFRA, T3, T2 | Distribution
KERN | FLYING D | 2025-01-20 13:57 | 45677.5813 | 2025-01-20 17:16 | 45677.7194 | 2025-01-20 19:04 | 45677.7944 | T3, T2 | Distribution
LOS ANGELES;VENTURA | GALAHAD | 2025-01-21 00:43 | 45678.0299 | 2025-01-23 20:27 | 45680.8521 | 2025-01-24 11:54 | 45681.4958 | T3, T2 | Distribution
RIVERSIDE | GARBONI | 2025-01-20 19:20 | 45677.8056 | 2025-01-21 03:16 | 45678.1361 | 2025-01-21 04:42 | 45678.1958 | T2 | Distribution
RIVERSIDE | GILMAN | 2025-01-20 18:05 | 45677.7535 | 2025-01-24 00:18 | 45681.0125 | 2025-01-24 08:11 | 45681.341 | T3, T2 | Distribution
RIVERSIDE | GINGER | 2025-01-21 10:19 | 45678.4299 | 2025-01-24 11:47 | 45681.491 | 2025-01-24 12:43 | 45681.5299 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | GRANNY SMITH | 2025-01-23 11:33 | 45680.4812 | 2025-01-23 21:45 | 45680.9062 | 2025-01-24 01:34 | 45681.0653 | T3 | Distribution
SAN BERNARDINO | GREEN BEAR | 2025-01-22 17:11 | 45679.716 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 06:25 | 45681.2674 | T3 | Distribution
LOS ANGELES;VENTURA | GUITAR | 2025-01-23 09:42 | 45680.4042 | 2025-01-23 18:49 | 45680.784 | 2025-01-24 12:36 | 45681.525 | T3 | Distribution
RIVERSIDE;SAN BERNARDINO | GUNSITE | 2025-01-20 19:28 | 45677.8111 | 2025-01-23 21:45 | 45680.9062 | 2025-01-24 17:31 | 45681.7299 | T3 | Distribution
RIVERSIDE | HELICOPTER | 2025-01-21 12:21 | 45678.5146 | 2025-01-24 00:17 | 45681.0118 | 2025-01-24 03:00 | 45681.125 | Non HFRA, T2 | Distribution
SAN BERNARDINO | HEAPS PEAK | 2025-01-22 | 17:04 | 2025-01-23 | 18:45 | 2025-01-24 | 13:10 | T3 | Distribution
LOS ANGELES | HI LINE | 2025-01-23 08:21 | 45680.3479 | 2025-01-23 12:09 | 45680.5062 | 2025-01-23 16:15 | 45680.6771 | Non HFRA, T3 | Distribution
SAN BERNARDINO | HIGH SCHOOL | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 02:30 | 45681.1042 | T3 | Distribution
RIVERSIDE;SAN BERNARDINO | HIGHBALL | 2025-01-20 19:41 | 45677.8201 | 2025-01-23 17:12 | 45680.7167 | 2025-01-23 18:28 | 45680.7694 | Non HFRA, T2 | Distribution
LOS ANGELES | HILLFIELD | 2025-01-20 09:29 | 45677.3951 | 2025-01-23 18:40 | 45680.7778 | 2025-01-23 20:06 | 45680.8375 | T3 | Distribution
RIVERSIDE | HONEYCRISP | 2025-01-23 11:35 | 45680.4826 | 2025-01-23 17:21 | 45680.7229 | 2025-01-23 18:23 | 45680.766 | T2 | Distribution
VENTURA | HOOLIGAN | 2025-01-23 09:34 | 45680.3986 | 2025-01-23 19:15 | 45680.8021 | 2025-01-23 20:19 | 45680.8465 | T3 | Distribution
LOS ANGELES | HORNTOAD | 2025-01-21 16:45 | 45678.6979 | 2025-01-23 | 19:29 | 2025-01-24 12:49 | 45681.534 | T3, T2 | Distribution
LOS ANGELES | HUCKLEBERRY | 2025-01-20 14:05 | 45677.5868 | 2025-01-25 14:16 | 45682.5944 | 2025-01-25 15:23 | 45682.641 | T3 | Distribution
RIVERSIDE | HUGO | 2025-01-23 08:44 | 45680.3639 | 2025-01-23 21:57 | 45680.9146 | 2025-01-23 22:46 | 45680.9486 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | ICE HOUSE | 2025-01-23 03:47 | 45680.1576 | 2025-01-23 14:33 | 45680.6062 | 2025-01-24 09:40 | 45681.4028 | T3 | Distribution
SAN BERNARDINO | INDEPENDENCE | 2025-01-20 20:01 | 45677.834 | 2025-01-23 14:40 | 45680.6111 | 2025-01-23 16:21 | 45680.6813 | Non HFRA, T2 | Distribution
LOS ANGELES | INTERIOR | 2025-01-23 07:49 | 45680.3257 | 2025-01-23 11:56 | 45680.4972 | 2025-01-23 16:25 | 45680.684 | Non HFRA, T3 | Distribution
SAN BERNARDINO | INTERN | 2025-01-21 10:45 | 45678.4479 | 2025-01-21 15:35 | 45678.6493 | 2025-01-21 16:46 | 45678.6986 | Non HFRA, T3, T2 | Distribution
ORANGE | IRAN | 2025-01-22 15:26 | 45679.6431 | 2025-01-22 22:36 | 45679.9417 | 2025-01-24 01:11 | 45681.0493 | Non HFRA, T2 | Distribution
LOS ANGELES | JARVIS | 2025-01-21 00:26 | 45678.0181 | 2025-01-21 14:22 | 45678.5986 | 2025-01-24 11:29 | 45681.4785 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | JEEP | 2025-01-20 14:58 | 45677.6236 | 2025-01-23 18:38 | 45680.7764 | 2025-01-24 08:20 | 45681.3472 | T3 | Distribution
SAN BERNARDINO | JENKS LAKE | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 10:30 | 45678.4375 | T3 | Distribution
RIVERSIDE | JUBILEE | 2025-01-21 11:08 | 45678.4639 | 2025-01-24 01:44 | 45681.0722 | 2025-01-24 02:22 | 45681.0986 | Non HFRA, T2 | Distribution
LOS ANGELES | KINSEY | 2025-01-20 13:20 | 45677.5556 | 2025-01-23 17:56 | 45680.7472 | 2025-01-24 17:57 | 45681.7479 | Non HFRA, T2 | Distribution
SAN BERNARDINO | KUFFEL | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:45 | 45680.7812 | 2025-01-24 02:55 | 45681.1215 | T3 | Distribution
RIVERSIDE | KULBERG | 2025-01-23 08:44 | 45680.3639 | 2025-01-23 10:07 | 45680.4208 | 2025-01-23 09:39 | 45680.4021 | Non HFRA, T2 | Distribution
SAN BERNARDINO | LA GRANDE | 2025-01-20 21:34 | 45677.8986 | 2025-01-21 08:58 | 45678.3736 | 2025-01-21 13:33 | 45678.5646 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | LA SIERRA | 2025-01-23 13:38 | 45680.5681 | 2025-01-23 21:57 | 45680.9146 | 2025-01-24 08:57 | 45681.3729 | Non HFRA, T2 | Distribution
RIVERSIDE | LACRESTA | 2025-01-21 10:31 | 45678.4382 | 2025-01-21 03:21 | 45678.1394 | 2025-01-21 17:26 | 45678.7264 | T3 | Distribution
RIVERSIDE | LAKELAND | 2025-01-23 11:23 | 45680.4743 | 2025-01-23 15:31 | 45680.6465 | 2025-01-23 19:28 | 45680.8111 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | LARCH | 2025-01-20 14:31 | 45677.6049 | 2025-01-23 17:29 | 45680.7285 | 2025-01-23 18:34 | 45680.7736 | Non HFRA, T2 | Distribution
RIVERSIDE | LAUDA | 2025-01-20 18:05 | 45677.7535 | 2025-01-24 00:18 | 45681.0125 | 2025-01-24 08:09 | 45681.3396 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | LAZARO | 2025-01-23 09:32 | 45680.3972 | 2025-01-23 17:24 | 45680.725 | 2025-01-23 18:23 | 45680.766 | T3 | Distribution
ORANGE/RIVERSIDE | LIMITED | 2025-01-20 13:50 | 45677.5764 | 2025-01-21 18:05 | 45678.7535 | 2025-01-24 10:09 | 45681.4229 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | LIMONITE | 2025-01-20 14:30 | 45677.6042 | 2025-01-23 18:38 | 45680.7764 | 2025-01-23 19:44 | 45680.8222 | Non HFRA, T2 | Distribution
RIVERSIDE | LIVERMORE | 2025-01-20 21:35 | 45677.8993 | 2025-01-23 15:34 | 45680.6486 | 2025-01-23 16:40 | 45680.6944 | Non HFRA, T2 | Distribution
RIVERSIDE | LOCKNER | 2025-01-20 18:42 | 45677.7792 | 2025-01-23 20:28 | 45680.8528 | 2025-01-23 22:18 | 45680.9292 | Non HFRA, T2 | Distribution
LOS ANGELES | LOPEZ | 2025-01-23 07:59 | 45680.3326 | 2025-01-23 17:31 | 45680.7299 | 2025-01-24 14:08 | 45681.5889 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | LOUCKS | 2025-01-20 09:19 | 45677.3882 | 2025-01-23 17:21 | 45680.7229 | 2025-01-24 02:24 | 45681.1 | T3 | Distribution
RIVERSIDE/SAN DIEGO | LUISENO | 2025-01-21 07:58 | 45678.3319 | 2025-01-24 00:23 | 45681.016 | 2025-01-24 12:26 | 45681.5181 | Non HFRA, T3 | Distribution
SAN BERNARDINO | LURING | 2025-01-22 16:25 | 45679.684 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 00:23 | 45681.016 | T3 | Distribution
RIVERSIDE;SAN BERNARDINO | MACIEL | 2025-01-23 01:23 | 45680.0576 | 2025-01-23 20:46 | 45680.8653 | 2025-01-23 22:25 | 45680.934 | T3, T2 | Distribution
LOS ANGELES;VENTURA | MAGUIRE | 2025-01-21 00:19 | 45678.0132 | 2025-01-24 01:30 | 45681.0625 | 2025-01-24 11:20 | 45681.4722 | T3 | Distribution
SAN BERNARDINO | MAIZE | 2025-01-20 20:03 | 45677.8354 | 2025-01-23 14:40 | 45680.6111 | 2025-01-23 17:59 | 45680.7493 | Non HFRA, T3 | Distribution
LOS ANGELES | MAMBA | 2025-01-20 09:21 | 45677.3896 | 2025-01-22 07:42 | 45679.3208 | 2025-01-24 10:35 | 45681.441 | T3 | Distribution
LOS ANGELES | MERLIN | 2025-01-22 19:14 | 45679.8014 | 2025-01-24 01:41 | 45681.0701 | 2025-01-24 10:57 | 45681.4563 | T3 | Distribution
KERN | METTLER | 2025-01-20 13:30 | 45677.5625 | 2025-01-23 18:53 | 45680.7868 | 2025-01-23 22:17 | 45680.9285 | T3, T2 | Distribution
LOS ANGELES | MILO | 2025-01-23 10:51 | 45680.4521 | 2025-01-23 18:00 | 45680.75 | 2025-01-23 21:37 | 45680.9007 | T3, T2 | Distribution
VENTURA | MORELAND | 2025-01-23 15:43 | 45680.6549 | 2025-01-23 18:55 | 45680.7882 | 2025-01-23 20:44 | 45680.8639 | T3 | Distribution
RIVERSIDE | MORELLO | 2025-01-21 10:20 | 45678.4306 | 2025-01-23 20:28 | 45680.8528 | 2025-01-23 22:31 | 45680.9382 | Non HFRA, T3, T2 | Distribution
VENTURA | MORGANSTEIN | 2025-01-21 06:20 | 45678.2639 | 2025-01-23 17:15 | 45680.7188 | 2025-01-23 21:23 | 45680.891 | T3 | Distribution
LOS ANGELES | MULHOLLAND | 2025-01-21 00:46 | 45678.0319 | 2025-01-23 17:27 | 45680.7271 | 2025-01-24 10:33 | 45681.4396 | T3 | Distribution
RIVERSIDE | NAPOLEON | 2025-01-20 22:37 | 45677.9424 | 2025-01-23 18:02 | 45680.7514 | 2025-01-23 21:12 | 45680.8833 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | NATIONS | 2025-01-23 11:23 | 45680.4743 | 2025-01-23 20:30 | 45680.8542 | 2025-01-24 00:39 | 45681.0271 | Non HFRA, T2 | Distribution
RIVERSIDE | NAYLOR | 2025-01-20 14:42 | 45677.6125 | 2025-01-23 23:28 | 45680.9778 | 2025-01-24 01:04 | 45681.0444 | Non HFRA, T2 | Distribution
SAN BERNARDINO | NORTH SHORE | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 02:30 | 45681.1042 | T3 | Distribution
SAN BERNARDINO | NORTHPARK | 2025-01-21 01:59 | 45678.0826 | 2025-01-24 03:53 | 45681.1618 | 2025-01-24 12:24 | 45681.5167 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | OAK KNOLL | 2025-01-22 17:11 | 45679.716 | 2025-01-23 21:58 | 45680.9153 | 2025-01-24 12:22 | 45681.5153 | T3 | Distribution
LOS ANGELES | OBSERVATORY | 2025-01-20 10:22 | 45677.4319 | 2025-01-21 15:53 | 45678.6618 | 2025-01-24 11:34 | 45681.4819 | T3 | Distribution
RIVERSIDE | OLIVER | 2025-01-21 10:56 | 45678.4556 | 2025-01-24 00:16 | 45681.0111 | 2025-01-24 06:36 | 45681.275 | Non HFRA, T2 | Distribution
RIVERSIDE | OZARK | 2025-01-23 11:38 | 45680.4847 | 2025-01-23 17:21 | 45680.7229 | 2025-01-23 18:20 | 45680.7639 | T2 | Distribution
RIVERSIDE | PASCAL | 2025-01-23 08:39 | 45680.3604 | 2025-01-23 17:36 | 45680.7333 | 2025-01-24 09:24 | 45681.3917 | T3 | Distribution
VENTURA | PATRIOT | 2025-01-23 07:57 | 45680.3313 | 2025-01-23 19:21 | 45680.8063 | 2025-01-24 08:48 | 45681.3667 | T3 | Distribution
RIVERSIDE | PAWNEE | 2025-01-23 13:29 | 45680.5618 | 2025-01-24 00:17 | 45681.0118 | 2025-01-24 04:30 | 45681.1875 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | PENSTOCK | 2025-01-20 15:05 | 45677.6285 | 2025-01-25 15:47 | 45682.6576 | 2025-01-26 14:27 | 45683.6021 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | PERRIS | 2025-01-23 12:53 | 45680.5368 | 2025-01-24 00:16 | 45681.0111 | 2025-01-24 03:24 | 45681.1417 | Non HFRA, T2 | Distribution
RIVERSIDE | PHEASANT | 2025-01-20 19:28 | 45677.8111 | 2025-01-23 21:45 | 45680.9062 | 2025-01-24 04:35 | 45681.191 | T3, T2 | Distribution
RIVERSIDE | PHOTON | 2025-01-20 20:38 | 45677.8597 | 2025-01-21 08:12 | 45678.3417 | 2025-01-21 14:44 | 45678.6139 | Non HFRA, T2 | Distribution
LOS ANGELES | PICK | 2025-01-20 09:21 | 45677.3896 | 2025-01-23 17:23 | 45680.7243 | 2025-01-24 01:39 | 45681.0687 | T3 | Distribution
RIVERSIDE | PICONI | 2025-01-21 09:10 | 45678.3819 | 2025-01-24 00:54 | 45681.0375 | 2025-01-24 03:24 | 45681.1417 | Non HFRA, T3 | Distribution
RIVERSIDE | PINE COVE | 2025-01-20 17:56 | 45677.7472 | 2025-01-21 08:14 | 45678.3431 | 2025-01-21 15:15 | 45678.6354 | T3 | Distribution
LOS ANGELES | PLATEAU | 2025-01-23 08:54 | 45680.3708 | 2025-01-23 19:14 | 45680.8014 | 2025-01-24 17:00 | 45681.7083 | T3 | Distribution
RIVERSIDE | PONY | 2025-01-23 08:44 | 45680.3639 | 2025-01-23 13:15 | 45680.4208 | 2025-01-23 13:03 | 45680.5437 | Non HFRA | Distribution
RIVERSIDE | POPPET FLATS | 2025-01-20 19:17 | 45677.8035 | 2025-01-21 15:06 | 45678.6292 | 2025-01-21 23:33 | 45678.9812 | T3, T2 | Distribution
RIVERSIDE | POTTERY | 2025-01-23 11:24 | 45680.475 | 2025-01-23 15:40 | 45680.6528 | 2025-01-23 18:09 | 45680.7562 | Non HFRA, T2 | Distribution
LOS ANGELES | PRONGHORN | 2025-01-25 04:48 | 45682.2 | 2025-01-25 14:16 | 45682.5944 | 2025-01-25 15:20 | 45682.6389 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | PURCHASE | 2025-01-20 20:27 | 45677.8521 | 2025-01-23 21:45 | 45680.9062 | 2025-01-23 23:07 | 45680.9632 | T3 | Distribution
LOS ANGELES | PYTHON | 2025-01-23 09:48 | 45680.4083 | 2025-01-23 17:31 | 45680.7299 | 2025-01-24 11:16 | 45681.4694 | T3 | Distribution
VENTURA | RAMAC | 2025-01-23 08:09 | 45680.3396 | 2025-01-23 18:54 | 45680.7875 | 2025-01-24 12:44 | 45681.5306 | Non HFRA, T2 | Distribution
LOS ANGELES | RED BOX | 2025-01-20 10:17 | 45677.4285 | 2025-01-21 14:22 | 45678.5986 | 2025-01-24 12:00 | 45681.5 | T3 | Distribution
VENTURA | REJADA | 2025-01-21 09:39 | 45678.4021 | 2025-01-24 05:06 | 45681.2125 | 2025-01-24 10:08 | 45681.4222 | T3 | Distribution
RIVERSIDE | RESORT | 2025-01-20 18:37 | 45677.7757 | 2025-01-23 20:46 | 45680.8653 | 2025-01-23 22:49 | 45680.9507 | Non HFRA, T3, T2 | Distribution
VENTURA | RICARDO | 2025-01-21 04:05 | 45678.1701 | 2025-01-21 13:17 | 45678.5535 | 2025-01-21 14:00 | 45678.5833 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | RIM | 2025-01-23 07:09 | 45680.2979 | 2025-01-23 18:45 | 45680.7812 | 2025-01-25 00:19 | 45682.0132 | T3 | Distribution
SAN BERNARDINO | ROCKWELL | 2025-01-23 13:30 | 45680.5625 | 2025-01-23 21:18 | 45680.8875 | 2025-01-24 02:34 | 45681.1069 | Non HFRA, T2 | Distribution
RIVERSIDE | ROS | 2025-01-20 20:41 | 45677.8618 | 2025-01-23 21:16 | 45680.8861 | 2025-01-24 00:53 | 45681.0368 | T2 | Distribution
RIVERSIDE | ROTEC | 2025-01-20 19:25 | 45677.809 | 2025-01-23 20:29 | 45680.8535 | 2025-01-23 22:24 | 45680.9333 | Non HFRA, T2 | Distribution
RIVERSIDE | ROUNDEL | 2025-01-21 10:20 | 45678.4306 | 2025-01-24 01:43 | 45681.0715 | 2025-01-24 03:02 | 45681.1264 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | ROWCO | 2025-01-20 10:21 | 45677.4313 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 01:51 | 45681.0771 | T3 | Distribution
ORANGE;RIVERSIDE | RUSTIC | 2025-01-21 07:51 | 45678.3271 | 2025-01-23 14:19 | 45680.5965 | 2025-01-23 17:07 | 45680.7132 | T3 | Distribution
RIVERSIDE | SADDLEBACK | 2025-01-20 16:30 | 45677.6875 | 2025-01-24 12:21 | 45681.5146 | 2025-01-24 13:14 | 45681.5514 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | SAND CANYON | 2025-01-20 06:56 | 45677.2889 | 2025-01-24 01:31 | 45681.0632 | 2025-01-26 14:44 | 45683.6139 | T3 | Distribution
SAN BERNARDINO | SANTORINI | 2025-01-20 21:10 | 45677.8819 | 2025-01-21 03:20 | 45678.1389 | 2025-01-21 04:37 | 45678.1924 | Non HFRA, T2 | Distribution
LOS ANGELES;VENTURA | SAUGUS-MOORPARK-SANTA SUSANA-TORREY | 2025-01-23 | 45680.3681 | 2025-01-24 03:54 | 3:54 | 2025-01-24 10:28 | 10:28 | T3 | Subtranmission
RIVERSIDE | SAUNDERS | 2025-01-20 17:56 | 45677.7472 | 2025-01-21 08:14 | 45678.3431 | 2025-01-21 17:17 | 45678.7201 | T3 | Distribution
SAN BERNARDINO | SAWPIT | 2025-01-25 | 45682.1958 | 2025-01-25 14:20 | 14:20 | 2025-01-25 16:38 | 16:38 | T3 | Distribution
RIVERSIDE | SCHMIDT | 2025-01-21 10:20 | 45678.4306 | 2025-01-24 01:44 | 45681.0722 | 2025-01-24 03:40 | 45681.1528 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | SCOUT | 2025-01-25 13:14 | 45682.5514 | 2025-01-25 15:36 | 45682.65 | 2025-01-26 13:49 | 45683.5757 | T2 | Distribution
SAN BERNARDINO | SEELEY | 2025-01-25 04:50 | 45682.2014 | 2025-01-25 07:15 | 45682.3021 | 2025-01-25 09:37 | 45682.4007 | T3 | Distribution
LOS ANGELES | SERRA | 2025-01-23 08:10 | 45680.3403 | 2025-01-23 19:21 | 45680.8063 | 2025-01-24 09:53 | 45681.4118 | T3 | Distribution
SAN BERNARDINO | SEYMOUR | 2025-01-22 16:12 | 45679.675 | 2025-01-23 19:27 | 45680.8104 | 2025-01-24 13:17 | 45681.5535 | T3 | Distribution
SAN BERNARDINO | SHAKE | 2025-01-20 | 14:53 | 2025-01-23 | 18:46 | 2025-01-24 | 0:11 | T3 | Distribution
LOS ANGELES | SHOVEL | 2025-01-20 09:19 | 45677.3882 | 2025-01-25 14:17 | 45682.5951 | 2025-01-25 15:26 | 45682.6431 | T3 | Distribution
LOS ANGELES | SHOWDOWN | 2025-01-20 15:59 | 45677.666 | 2025-01-20 17:51 | 45677.7438 | 2025-01-20 20:46 | 45677.8653 | Non HFRA, T3, T2 | Distribution
LOS ANGELES;VENTURA | SIENNA | 2025-01-23 10:53 | 45680.4535 | 2025-01-23 18:00 | 45680.75 | 2025-01-23 21:32 | 45680.8972 | T3, T2 | Distribution
RIVERSIDE | SKINNER | 2025-01-23 08:44 | 45680.3639 | 2025-01-23 13:14 | 45680.4208 | 2025-01-23 13:03 | 45680.5437 | Non HFRA, T2 | Distribution
SAN BERNARDINO | SKY HI | 2025-01-25 13:26 | 45682.5597 | 2025-01-25 15:47 | 45682.6576 | 2025-01-26 13:57 | 45683.5813 | Non HFRA, T2 | Distribution
SAN BERNARDINO | SKYLAND | 2025-01-25 04:50 | 45682.2014 | 2025-01-25 07:15 | 45682.3021 | 2025-01-25 09:38 | 45682.4014 | T3 | Distribution
SAN BERNARDINO | SNOW VALLEY | 2025-01-22 17:11 | 45679.716 | 2025-01-23 18:46 | 45680.7819 | 2025-01-24 12:31 | 45681.5215 | T3 | Distribution
RIVERSIDE | SOGGY | 2025-01-23 13:29 | 45680.5618 | 2025-01-23 23:05 | 45680.9618 | 2025-01-24 01:09 | 45681.0479 | Non HFRA, T2 | Distribution
RIVERSIDE | SONOMA | 2025-01-20 21:11 | 45677.8826 | 2025-01-21 08:36 | 45678.3583 | 2025-01-21 14:26 | 45678.6014 | Non HFRA, T2 | Distribution
SAN BERNARDINO | SQUINT | 2025-01-20 15:48 | 45677.6583 | 2025-01-21 11:11 | 45678.466 | 2025-01-21 13:38 | 45678.5681 | T3 | Distribution
RIVERSIDE | STAGHORN | 2025-01-22 09:31 | 45679.3965 | 2025-01-23 21:57 | 45680.9146 | 2025-01-24 00:03 | 45681.0021 | Non HFRA, T2 | Distribution
RIVERSIDE | STARGLOW | 2025-01-21 10:30 | 45678.4375 | 2025-01-21 13:57 | 45678.5813 | 2025-01-21 20:09 | 45678.8396 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | STEEL | 2025-01-20 18:05 | 45677.7535 | 2025-01-24 01:08 | 45681.0472 | 2025-01-24 13:35 | 45681.566 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | STORES | 2025-01-20 20:27 | 45677.8521 | 2025-01-23 21:45 | 45680.9062 | 2025-01-24 01:13 | 45681.0507 | Non HFRA, T3, T2 | Distribution
VENTURA | STRATHERN | 2025-01-21 06:25 | 45678.2674 | 2025-01-23 19:14 | 45680.8014 | 2025-01-24 09:15 | 45681.3854 | T3 | Distribution
RIVERSIDE | STUBBY | 2025-01-20 19:28 | 45677.8111 | 2025-01-23 21:45 | 45680.9062 | 2025-01-24 15:45 | 45681.6562 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | SUNDANCE | 2025-01-20 20:51 | 45677.8688 | 2025-01-21 08:32 | 45678.3556 | 2025-01-21 11:28 | 45678.4778 | Non HFRA, T2 | Distribution
SAN BERNARDINO | SUTT | 2025-01-21 01:02 | 45678.0431 | 2025-01-24 05:07 | 45681.2132 | 2025-01-24 14:04 | 45681.5861 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | TACKLE | 2025-01-23 13:30 | 45680.5625 | 2025-01-23 21:46 | 45680.9069 | 2025-01-23 22:53 | 45680.9535 | Non HFRA, T3 | Distribution
SAN BERNARDINO | TAGGERT | 2025-01-21 00:25 | 45678.0174 | 2025-01-23 21:58 | 45680.9153 | 2025-01-24 12:25 | 45681.5174 | T3 | Distribution
RIVERSIDE | TAHQUITZ | 2025-01-20 06:39 | 45677.2771 | 2025-01-24 01:12 | 45681.05 | 2025-01-24 11:08 | 45681.4639 | T3 | Distribution
ORANGE | TAIWAN | 2025-01-21 02:37 | 45678.109 | 2025-01-23 14:19 | 45680.5965 | 2025-01-23 17:16 | 45680.7194 | Non HFRA, T3, T2 | Distribution
KERN;LOS ANGELES | TEJON | 2025-01-20 13:51 | 45677.5771 | 2025-01-21 14:13 | 45678.5924 | 2025-01-21 15:52 | 45678.6611 | Non HFRA, T2 | Distribution
RIVERSIDE | TERRA COTTA | 2025-01-23 11:23 | 45680.4743 | 2025-01-23 15:31 | 45680.6465 | 2025-01-23 18:55 | 45680.7882 | Non HFRA, T3, T2 | Distribution
VENTURA | TIMBER CANYON | 2025-01-23 10:24 | 45680.4333 | 2025-01-23 17:04 | 45680.7111 | 2025-01-24 14:22 | 45681.5986 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | TIVO | 2025-01-20 10:22 | 45677.4319 | 2025-01-21 14:22 | 45678.5986 | 2025-01-24 11:34 | 45681.4819 | Unknown | Distribution
RIVERSIDE | TRUMBLE | 2025-01-23 10:42 | 45680.4458 | 2025-01-23 15:59 | 45680.666 | 2025-01-23 17:03 | 45680.7104 | Non HFRA, T2 | Distribution
KERN | TUNGSTEN | 2025-01-20 13:37 | 45677.5674 | 2025-01-20 16:56 | 45677.7056 | 2025-01-20 18:44 | 45677.7806 | T3 | Distribution
SAN BERNARDINO | URBITA | 2025-01-20 14:06 | 45677.5875 | 2025-01-23 14:09 | 45680.5896 | 2025-01-23 15:19 | 45680.6382 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | VENGEANCE | 2025-01-20 11:09 | 45677.4646 | 2025-01-23 21:57 | 45680.9146 | 2025-01-24 01:42 | 45681.0708 | Non HFRA, T2 | Distribution
ORANGE | VERA CRUZ | 2025-01-20 15:10 | 45677.6319 | 2025-01-23 14:18 | 45680.5958 | 2025-01-23 17:59 | 45680.7493 | Non HFRA, T3, T2 | Distribution
SAN BERNARDINO | VERDEMONT | 2025-01-23 10:51 | 45680.4521 | 2025-01-24 00:25 | 45681.0174 | 2025-01-24 05:09 | 45681.2146 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | VERDUGO | 2025-01-20 10:10 | 45677.4236 | 2025-01-23 18:09 | 45680.7562 | 2025-01-24 11:43 | 45681.4882 | Non HFRA, T3, T2 | Distribution
LOS ANGELES | VETERANS | 2025-01-22 | 12:10 | 2025-01-23 21:00 | 45680.875 | 2025-01-24 10:17 | 45681.4285 | Non HFRA, T3, T2 | Distribution
RIVERSIDE;SAN BERNARDINO | WARHAWK | 2025-01-20 16:32 | 45677.6889 | 2025-01-23 21:57 | 45680.9146 | 2025-01-24 11:00 | 45681.4583 | Non HFRA, T2 | Distribution
SAN BERNARDINO | WEESHA | 2025-01-20 14:46 | 45677.6153 | 2025-01-21 08:41 | 45678.3618 | 2025-01-21 10:30 | 45678.4375 | T3 | Distribution
RIVERSIDE | WESTBROOK | 2025-01-23 08:44 | 45680.3639 | 2025-01-23 10:06 | 45680.4208 | 2025-01-24 02:45 | 45681.1146 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | WILDOMAR | 2025-01-21 | 10:30 | 2025-01-21 | 15:16 | 2025-01-21 | 17:26 | Non HFRA, T3, T2 | Distribution
RIVERSIDE | WINERY | 2025-01-20 18:32 | 45677.7722 | 2025-01-21 15:43 | 45678.6549 | 2025-01-22 02:14 | 45679.0931 | T3 | Distribution
RIVERSIDE | WOBEGONE | 2025-01-20 22:10 | 45677.9236 | 2025-01-24 00:19 | 45681.0132 | 2025-01-24 05:10 | 45681.2153 | Non HFRA, T2 | Distribution
KERN | YANKEE | 2025-01-20 13:37 | 45677.5674 | 2025-01-20 16:56 | 45677.7056 | 2025-01-20 18:44 | 45677.7806 | T3 | Distribution
RIVERSIDE | ZEVO | 2025-01-23 08:44 | 45680.3639 | 2025-01-23 10:05 | 45680.4208 | 2025-01-23 09:39 | 45680.4021 | Non HFRA, T3 | Distribution
VENTURA | ZONE | 2025-01-21 07:28 | 45678.3111 | 2025-01-23 18:39 | 45680.7771 | 2025-01-24 13:35 | 45681.566 | Non HFRA, T3 | Distribution
Circuits De-Energized (cont.)
County | Circuit Name | Residential Customers De-energized | Commercial / Industrial customers De-energized | Medical Baseline customers De-energized | AFN other than MBL customers De-energized | Total customers De-energized | GO 95, Tier HFTD Tier(s) 1,2,3 | Other Customers
SAN BERNARDINO | ACOSTA | 0 | 7 | 0 | 0 | 7 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | ALLVIEW | 302 | 1 | 6 | 64 | 303 | T3 | 0
SAN BERNARDINO | ALPINE | 691 | 15 | 10 | 144 | 706 | T3 | 0
SAN BERNARDINO | AMETHYST | 237 | 4 | 10 | 39 | 241 | Non HFRA, T3, T2 | 0
VENTURA | ANGUS | 57 | 0 | 1 | 0 | 57 | Non HFRA, T3, T2 | 0
VENTURA | ANTON | 59 | 16 | 2 | 9 | 75 | T3 | 0
RIVERSIDE | ARAPAHO | 1116 | 19 | 38 | 813 | 1135 | Non HFRA, T2 | 0
RIVERSIDE | ARCHIE | 1 | 1 | 0 | 0 | 2 | Non HFRA, T3, T2 | 0
RIVERSIDE | ARMADA | 1592 | 18 | 72 | 165 | 1610 | Non HFRA, T3 | 0
ORANGE | ATENTO | 29 | 7 | 0 | 2 | 36 | T3 | 0
ORANGE | ATLANTA | 8 | 22 | 0 | 0 | 30 | Non HFRA, T3, T2 | 0
RIVERSIDE | AVIATOR | 1778 | 48 | 123 | 824 | 1826 | Non HFRA, T2 | 0
VENTURA | BALCOM | 120 | 0 | 2 | 20 | 120 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | BEAR VALLEY | 37 | 2 | 3 | 6 | 39 | T3, T2 | 0
VENTURA | BELPAC | 3131 | 74 | 145 | 386 | 3205 | T3 | 0
SAN BERNARDINO | BIG FALLS | 142 | 0 | 3 | 25 | 142 | T3 | 0
LOS ANGELES/VENTURA | BIG ROCK | 454 | 12 | 21 | 104 | 466 | T3 | 0
RIVERSIDE | BLACKHILLS | 107 | 1 | 5 | 55 | 108 | Non HFRA, T2 | 0
KERN/LOS ANGELES | BLEDSOE | 118 | 39 | 7 | 31 | 157 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | BLUE CUT | 234 | 65 | 10 | 90 | 299 | T3, T2 | 0
RIVERSIDE | BONNEVILLE | 483 | 33 | 8 | 270 | 516 | Non HFRA, T2 | 0
LOS ANGELES | BOOTLEGGER | 537 | 42 | 24 | 137 | 579 | T3 | 0
VENTURA | BORCHARD | 1287 | 46 | 50 | 169 | 1333 | T3 | 0
SAN BERNARDINO | BOULDER | 1265 | 24 | 62 | 202 | 1289 | Non HFRA, T3, T2 | 0
LOS ANGELES | BOUQUET | 319 | 22 | 20 | 56 | 341 | T3 | 0
LOS ANGELES/ORANGE | BRAKEMAN | 650 | 24 | 10 | 192 | 674 | Non HFRA, T3, T2 | 0
VENTURA | BRENNAN | 437 | 22 | 25 | 49 | 459 | T3 | 0
LOS ANGELES | BROADCAST | 5 | 12 | 1 | 0 | 17 | T3 | 0
VENTURA | BUCKHORN | 1101 | 54 | 19 | 431 | 1155 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | BURNS | 1305 | 15 | 63 | 276 | 1320 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | BUTTERFIELD | 542 | 31 | 13 | 104 | 573 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | CABANA | 0 | 3 | 0 | 0 | 3 | Non HFRA, T2 | 0
RIVERSIDE | CALAMAR | 168 | 6 | 6 | 13 | 174 | T3 | 0
LOS ANGELES | CALGROVE | 1 | 1 | 0 | 0 | 2 | T3 | 0
SAN BERNARDINO | CALSTATE | 5 | 4 | 0 | 2 | 9 | T3, T2 | 0
SAN BERNARDINO | CAMP ANGELUS | 308 | 10 | 9 | 58 | 318 | T3 | 0
RIVERSIDE | CANAL | 3 | 1 | 0 | 0 | 4 | Non HFRA, T3, T2 | 0
RIVERSIDE | CARANCHO | 510 | 9 | 23 | 54 | 519 | T3 | 0
VENTURA | CASSIDY | 92 | 8 | 1 | 1 | 100 | T3 | 0
VENTURA | CASTRO | 16 | 3 | 0 | 0 | 19 | Non HFRA, T3 | 0
SAN BERNARDINO | CEDAR GLEN | 1466 | 30 | 11 | 161 | 1496 | T3 | 0
SAN BERNARDINO | CHAMPION | 1673 | 62 | 46 | 409 | 1735 | T2 | 0
RIVERSIDE | CHARDONNAY | 1065 | 18 | 83 | 122 | 1083 | T3 | 0
RIVERSIDE | CHAWA | 1145 | 47 | 48 | 248 | 1192 | T3, T2 | 0
SAN BERNARDINO | CHEVELLE | 2025 | 36 | 91 | 472 | 2061 | Non HFRA, T3, T2 | 0
LOS ANGELES | CLARINET | 4 | 11 | 0 | 0 | 15 | T3, T2 | 0
KERN | CONDOR | 1452 | 45 | 59 | 197 | 1497 | T3, T2 | 0
SAN BERNARDINO | CONFERENCE | 19 | 1 | 1 | 3 | 20 | T3 | 0
RIVERSIDE/SAN BERNARDINO | CONINE | 409 | 14 | 25 | 162 | 423 | Non HFRA, T3, T2 | 0
RIVERSIDE | CORSAIR | 2470 | 74 | 95 | 872 | 2544 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | COTTAGE GROVE | 227 | 0 | 0 | 29 | 227 | T3 | 0
SAN BERNARDINO | CRAB | 0 | 0 | 0 | 0 | 0 | T3 | 0
SAN BERNARDINO | CRAM | 4 | 4 | 0 | 0 | 8 | Non HFRA, T3, T2 | 0
LOS ANGELES | CRESCENTA | 1109 | 25 | 26 | 170 | 1134 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | CRESTLINE | 780 | 14 | 13 | 175 | 794 | T3 | 0
LOS ANGELES | CRUMNER | 617 | 15 | 14 | 65 | 632 | T3 | 0
SAN BERNARDINO | CRUMP | 467 | 7 | 17 | 97 | 474 | T3 | 0
SAN BERNARDINO | CUSHENBURY | 0 | 3 | 0 | 0 | 3 | Non HFRA, T2 | 0
LOS ANGELES | CUTHBERT | 2356 | 51 | 44 | 154 | 2407 | T3 | 0
SAN BERNARDINO | DALBA | 587 | 6 | 16 | 118 | 593 | T3 | 0
RIVERSIDE | DARTMOUTH | 443 | 43 | 6 | 105 | 486 | Non HFRA, T3, T2 | 0
LOS ANGELES | DAVENPORT | 859 | 25 | 44 | 160 | 884 | T3 | 0
RIVERSIDE | DEACON | 1785 | 79 | 34 | 1014 | 1864 | Non HFRA, T2 | 0
ORANGE/SAN BERNARDINO | DEL CARBON | 1455 | 49 | 46 | 278 | 1504 | Non HFRA, T3, T2 | 0
RIVERSIDE | DELUZ | 231 | 17 | 11 | 33 | 248 | T3 | 0
SAN BERNARDINO | DOBLE | 1 | 1 | 0 | 0 | 2 | Non HFRA, T2 | 0
VENTURA | DONLON | 497 | 36 | 12 | 75 | 533 | Non HFRA, T3, T2 | 0
RIVERSIDE | DUKE | 14 | 5 | 0 | 4 | 19 | Non HFRA, T3, T2 | 0
RIVERSIDE | DYSART | 69 | 4 | 7 | 23 | 73 | Non HFRA, T3, T2 | 0
LOS ANGELES/VENTURA | ENERGY | 1720 | 69 | 76 | 311 | 1789 | T3 | 0
RIVERSIDE | ESCALA | 145 | 5 | 6 | 19 | 150 | T3 | 0
VENTURA | EVITA | 11 | 7 | 0 | 1 | 18 | T3, T2 | 0
LOS ANGELES/SAN BERNARDINO | FERRARA | 334 | 21 | 6 | 42 | 355 | Non HFRA, T3, T2 | 0
RIVERSIDE | FINGAL | 821 | 23 | 29 | 395 | 844 | T3 | 0
SAN BERNARDINO | FIREBIRD | 1237 | 74 | 32 | 309 | 1311 | Non HFRA, T3, T2 | 0
KERN | FLYING D | 29 | 1 | 3 | 6 | 30 | T3, T2 | 0
LOS ANGELES/VENTURA | GALAHAD | 2092 | 131 | 31 | 135 | 2223 | T3, T2 | 0
RIVERSIDE | GARBONI | 824 | 44 | 34 | 117 | 868 | T2 | 0
RIVERSIDE | GILMAN | 2 | 10 | 0 | 0 | 12 | T3, T2 | 0
RIVERSIDE | GINGER | 343 | 32 | 16 | 141 | 375 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | GRANNY SMITH | 299 | 23 | 9 | 45 | 322 | T3 | 0
SAN BERNARDINO | GREEN BEAR | 666 | 11 | 10 | 141 | 677 | T3 | 0
LOS ANGELES/VENTURA | GUITAR | 119 | 96 | 0 | 6 | 215 | T3 | 0
RIVERSIDE/SAN BERNARDINO | GUNSITE | 3 | 1 | 0 | 0 | 4 | T3 | 0
SAN BERNARDINO | HEAPS PEAK | 0 | 0 | 0 | 0 | 0 | T3 | 0
RIVERSIDE | HELICOPTER | 1785 | 27 | 49 | 989 | 1812 | Non HFRA, T2 | 0
LOS ANGELES | HI LINE | 27 | 4 | 0 | 1 | 31 | Non HFRA, T3 | 0
SAN BERNARDINO | HIGH SCHOOL | 316 | 10 | 5 | 43 | 326 | T3 | 0
RIVERSIDE/SAN BERNARDINO | HIGHBALL | 1624 | 47 | 36 | 1095 | 1671 | Non HFRA, T2 | 0
LOS ANGELES | HILLFIELD | 1128 | 20 | 33 | 452 | 1148 | T3 | 0
RIVERSIDE | HONEYCRISP | 2161 | 20 | 53 | 580 | 2181 | T2 | 0
VENTURA | HOOLIGAN | 3144 | 65 | 138 | 308 | 3209 | T3 | 0
LOS ANGELES | HORNTOAD | 21 | 6 | 1 | 3 | 27 | T3, T2 | 0
LOS ANGELES | HUCKLEBERRY | 0 | 5 | 0 | 0 | 5 | T3 | 0
RIVERSIDE | HUGO | 48 | 8 | 2 | 4 | 56 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | ICE HOUSE | 11 | 0 | 0 | 1 | 11 | T3 | 0
SAN BERNARDINO | INDEPENDENCE | 2143 | 54 | 57 | 544 | 2197 | Non HFRA, T2 | 0
LOS ANGELES | INTERIOR | 109 | 31 | 0 | 6 | 140 | Non HFRA, T3 | 0
SAN BERNARDINO | INTERN | 171 | 2 | 6 | 30 | 173 | Non HFRA, T3, T2 | 0
ORANGE | IRAN | 508 | 12 | 20 | 42 | 520 | Non HFRA, T2 | 0
LOS ANGELES | JARVIS | 5 | 10 | 1 | 2 | 15 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | JEEP | 1413 | 17 | 27 | 148 | 1430 | T3 | 0
SAN BERNARDINO | JENKS LAKE | 106 | 7 | 1 | 5 | 113 | T3 | 0
RIVERSIDE | JUBILEE | 496 | 15 | 15 | 191 | 511 | Non HFRA, T2 | 0
LOS ANGELES | KINSEY | 28 | 10 | 0 | 2 | 38 | Non HFRA, T2 | 0
SAN BERNARDINO | KUFFEL | 543 | 5 | 4 | 47 | 548 | T3 | 0
RIVERSIDE | KULBERG | 2414 | 32 | 110 | 626 | 2446 | Non HFRA, T2 | 0
SAN BERNARDINO | LA GRANDE | 1594 | 54 | 98 | 273 | 1648 | Non HFRA, T3, T2 | 0
RIVERSIDE | LA SIERRA | 2 | 5 | 0 | 0 | 7 | Non HFRA, T2 | 0
RIVERSIDE | LACRESTA | 480 | 8 | 17 | 47 | 488 | T3 | 0
RIVERSIDE | LAKELAND | 900 | 29 | 27 | 442 | 929 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | LARCH | 4 | 6 | 0 | 0 | 10 | Non HFRA, T2 | 0
RIVERSIDE | LAUDA | 1 | 1 | 0 | 0 | 2 | Non HFRA, T3, T2 | 0
RIVERSIDE | LAZARO | 2072 | 66 | 133 | 288 | 2138 | T3 | 0
ORANGE/RIVERSIDE | LIMITED | 2056 | 62 | 98 | 1038 | 2118 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | LIMONITE | 2 | 0 | 0 | 0 | 2 | Non HFRA, T2 | 0
RIVERSIDE | LIVERMORE | 194 | 4 | 4 | 34 | 198 | Non HFRA, T2 | 0
RIVERSIDE | LOCKNER | 554 | 6 | 38 | 328 | 560 | Non HFRA, T2 | 0
LOS ANGELES | LOPEZ | 40 | 7 | 0 | 6 | 47 | Non HFRA, T3, T2 | 0
LOS ANGELES | LOUCKS | 56 | 0 | 3 | 13 | 56 | T3 | 0
RIVERSIDE/SAN DIEGO | LUISENO | 2 | 19 | 0 | 0 | 21 | Non HFRA, T3 | 0
SAN BERNARDINO | LURING | 369 | 2 | 8 | 87 | 371 | T3 | 0
RIVERSIDE/SAN BERNARDINO | MACIEL | 38 | 0 | 1 | 4 | 38 | T3, T2 | 0
LOS ANGELES/VENTURA | MAGUIRE | 626 | 61 | 20 | 95 | 687 | T3 | 0
SAN BERNARDINO | MAIZE | 913 | 19 | 36 | 211 | 932 | Non HFRA, T3 | 0
LOS ANGELES | MAMBA | 53 | 13 | 2 | 10 | 66 | T3 | 0
LOS ANGELES | MERLIN | 965 | 33 | 13 | 44 | 998 | T3 | 0
KERN | METTLER | 7 | 1 | 0 | 0 | 8 | T3, T2 | 0
LOS ANGELES | MILO | 1997 | 43 | 24 | 280 | 2040 | T3, T2 | 0
VENTURA | MORELAND | 1912 | 26 | 79 | 315 | 1938 | T3 | 0
RIVERSIDE | MORELLO | 31 | 16 | 0 | 3 | 47 | Non HFRA, T3, T2 | 0
VENTURA | MORGANSTEIN | 1709 | 72 | 93 | 169 | 1781 | T3 | 0
LOS ANGELES | MULHOLLAND | 542 | 34 | 20 | 50 | 576 | T3 | 0
RIVERSIDE | NAPOLEON | 37 | 11 | 2 | 13 | 48 | Non HFRA, T3, T2 | 0
RIVERSIDE | NATIONS | 516 | 11 | 19 | 238 | 527 | Non HFRA, T2 | 0
RIVERSIDE | NAYLOR | 69 | 0 | 3 | 23 | 69 | Non HFRA, T2 | 0
SAN BERNARDINO | NORTH SHORE | 1943 | 36 | 29 | 165 | 1979 | T3 | 0
SAN BERNARDINO | NORTHPARK | 556 | 29 | 35 | 140 | 585 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | OAK KNOLL | 492 | 4 | 7 | 55 | 496 | T3 | 0
LOS ANGELES | OBSERVATORY | 2 | 2 | 0 | 0 | 4 | T2 | 0
RIVERSIDE | OLIVER | 3 | 0 | 0 | 0 | 3 | Non HFRA, T2 | 0
RIVERSIDE | OZARK | 3 | 0 | 0 | 0 | 3 | T2 | 0
RIVERSIDE | PASCAL | 1721 | 40 | 75 | 320 | 1761 | T3 | 0
VENTURA | PATRIOT | 573 | 13 | 25 | 77 | 586 | T3 | 0
RIVERSIDE | PAWNEE | 2356 | 37 | 82 | 1425 | 2393 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | PENSTOCK | 94 | 19 | 3 | 25 | 113 | Non HFRA, T3, T2 | 0
RIVERSIDE | PERRIS | 685 | 27 | 19 | 415 | 712 | Non HFRA, T2 | 0
RIVERSIDE | PHEASANT | 177 | 8 | 13 | 34 | 185 | T3, T2 | 0
RIVERSIDE | PHOTON | 1012 | 24 | 35 | 220 | 1036 | Non HFRA, T2 | 0
LOS ANGELES | PICK | 970 | 32 | 53 | 224 | 1002 | T3 | 0
RIVERSIDE | PICONI | 1197 | 45 | 71 | 201 | 1242 | Non HFRA, T3 | 0
RIVERSIDE | PINE COVE | 1408 | 56 | 19 | 202 | 1464 | T3 | 0
LOS ANGELES | PLATEAU | 219 | 4 | 8 | 24 | 223 | T3 | 0
RIVERSIDE | PONY | 0 | 3 | 0 | 0 | 3 | Non HFRA | 0
RIVERSIDE | POPPET FLATS | 637 | 47 | 30 | 337 | 684 | T3, T2 | 0
RIVERSIDE | POTTERY | 747 | 48 | 19 | 315 | 795 | Non HFRA, T2 | 0
LOS ANGELES | PRONGHORN | 724 | 23 | 25 | 180 | 747 | Non HFRA, T3, T2 | 0
RIVERSIDE | PURCHASE | 64 | 33 | 1 | 30 | 97 | T3 | 0
LOS ANGELES | PYTHON | 1210 | 39 | 67 | 139 | 1249 | T3 | 0
VENTURA | RAMAC | 1223 | 66 | 13 | 234 | 1289 | Non HFRA, T2 | 0
LOS ANGELES | RED BOX | 16 | 11 | 0 | 2 | 27 | T3 | 0
VENTURA | REJADA | 2 | 3 | 0 | 0 | 5 | T3 | 0
RIVERSIDE | RESORT | 0 | 1 | 0 | 0 | 1 | Non HFRA, T3, T2 | 0
VENTURA | RICARDO | 0 | 5 | 0 | 0 | 5 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | RIM | 1846 | 51 | 30 | 406 | 1897 | T3 | 0
SAN BERNARDINO | ROCKWELL | 1540 | 44 | 80 | 555 | 1584 | Non HFRA, T2 | 0
RIVERSIDE | ROS | 2698 | 32 | 107 | 1348 | 2730 | T2 | 0
RIVERSIDE | ROTEC | 1252 | 16 | 81 | 391 | 1268 | Non HFRA, T2 | 0
RIVERSIDE | ROUNDEL | 1510 | 24 | 97 | 342 | 1534 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | ROWCO | 1241 | 26 | 23 | 255 | 1267 | T3 | 0
ORANGE/RIVERSIDE | RUSTIC | 319 | 53 | 11 | 39 | 372 | T3 | 0
RIVERSIDE | SADDLEBACK | 7 | 1 | 0 | 2 | 8 | Non HFRA, T3, T2 | 0
LOS ANGELES | SAND CANYON | 111 | 26 | 5 | 25 | 137 | T3 | 0
SAN BERNARDINO | SANTORINI | 11 | 2 | 1 | 2 | 13 | Non HFRA, T2 | 0
LOS ANGELES/VENTURA | SAUGUS-MOORPARK-SANTA SUSANA-TORREY | 0 | 1 | 0 | 0 | 1 | T3 | 0
RIVERSIDE | SAUNDERS | 2728 | 44 | 45 | 389 | 2772 | T3 | 0
SAN BERNARDINO | SAWPIT | 0 | 0 | 0 | 0 | 0 | T3 | 0
RIVERSIDE | SCHMIDT | 1334 | 44 | 73 | 371 | 1378 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | SCOUT | 3 | 0 | 0 | 0 | 3 | T2 | 0
SAN BERNARDINO | SEELEY | 731 | 11 | 24 | 223 | 742 | T3 | 0
LOS ANGELES | SERRA | 206 | 35 | 3 | 12 | 241 | T3 | 0
SAN BERNARDINO | SEYMOUR | 4 | 0 | 0 | 0 | 4 | T3 | 0
SAN BERNARDINO | SHAKE | 0 | 0 | 0 | 0 | 0 | T3 | 0
LOS ANGELES | SHOVEL | 699 | 25 | 42 | 175 | 724 | T3 | 0
LOS ANGELES | SHOWDOWN | 1335 | 28 | 42 | 552 | 1363 | Non HFRA, T3, T2 | 0
LOS ANGELES/VENTURA | SIENNA | 873 | 11 | 35 | 109 | 884 | T3, T2 | 0
RIVERSIDE | SKINNER | 0 | 1 | 0 | 0 | 1 | Non HFRA, T2 | 0
SAN BERNARDINO | SKY HI | 14 | 1 | 0 | 1 | 15 | Non HFRA, T2 | 0
SAN BERNARDINO | SKYLAND | 844 | 5 | 15 | 217 | 849 | T3 | 0
SAN BERNARDINO | SNOW VALLEY | 921 | 35 | 11 | 152 | 956 | T3 | 0
RIVERSIDE | SOGGY | 1043 | 20 | 45 | 477 | 1063 | Non HFRA, T2 | 0
RIVERSIDE | SONOMA | 2175 | 32 | 83 | 1014 | 2207 | Non HFRA, T2 | 0
SAN BERNARDINO | SQUINT | 1195 | 19 | 23 | 151 | 1214 | T3 | 0
RIVERSIDE | STAGHORN | 1440 | 36 | 21 | 907 | 1476 | Non HFRA, T2 | 0
RIVERSIDE | STARGLOW | 1261 | 40 | 34 | 831 | 1301 | Non HFRA, T3, T2 | 0
RIVERSIDE | STEEL | 22 | 14 | 0 | 3 | 36 | Non HFRA, T3, T2 | 0
RIVERSIDE | STORES | 608 | 107 | 3 | 77 | 715 | Non HFRA, T3, T2 | 0
VENTURA | STRATHERN | 2592 | 78 | 78 | 629 | 2670 | T3 | 0
RIVERSIDE | STUBBY | 2 | 5 | 0 | 0 | 7 | Non HFRA, T3, T2 | 0
RIVERSIDE | SUNDANCE | 1670 | 19 | 89 | 450 | 1689 | Non HFRA, T2 | 0
SAN BERNARDINO | SUTT | 67 | 21 | 4 | 9 | 88 | Non HFRA, T3, T2 | 0
RIVERSIDE | TACKLE | 168 | 15 | 0 | 1 | 183 | Non HFRA, T3 | 0
SAN BERNARDINO | TAGGERT | 612 | 20 | 4 | 47 | 632 | T3 | 0
RIVERSIDE | TAHQUITZ | 129 | 12 | 4 | 23 | 141 | T3 | 0
ORANGE | TAIWAN | 584 | 103 | 24 | 43 | 687 | Non HFRA, T3, T2 | 0
KERN/LOS ANGELES | TEJON | 103 | 1 | 1 | 15 | 104 | Non HFRA, T2 | 0
RIVERSIDE | TERRA COTTA | 0 | 2 | 0 | 0 | 2 | Non HFRA, T3, T2 | 0
VENTURA | TIMBER CANYON | 136 | 10 | 1 | 14 | 146 | Non HFRA, T3, T2 | 0
LOS ANGELES | TIVO | 16 | 35 | 0 | 0 | 51 | Unknown | 0
RIVERSIDE | TRUMBLE | 856 | 16 | 23 | 339 | 872 | Non HFRA, T2 | 0
KERN | TUNGSTEN | 1591 | 57 | 107 | 553 | 1648 | T3 | 0
SAN BERNARDINO | URBITA | 1417 | 30 | 76 | 324 | 1447 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | VENGEANCE | 5 | 11 | 0 | 0 | 16 | Non HFRA, T2 | 0
ORANGE | VERA CRUZ | 184 | 25 | 10 | 16 | 209 | Non HFRA, T3, T2 | 0
SAN BERNARDINO | VERDEMONT | 0 | 2 | 0 | 0 | 2 | Non HFRA, T3, T2 | 0
LOS ANGELES | VERDUGO | 55 | 23 | 5 | 8 | 78 | Non HFRA, T3, T2 | 0
LOS ANGELES | VETERANS | 8 | 12 | 0 | 0 | 20 | Non HFRA, T3, T2 | 0
RIVERSIDE/SAN BERNARDINO | WARHAWK | 14 | 2 | 0 | 1 | 16 | Non HFRA, T2 | 0
SAN BERNARDINO | WEESHA | 54 | 0 | 0 | 4 | 54 | T3 | 0
RIVERSIDE | WESTBROOK | 636 | 25 | 21 | 99 | 661 | Non HFRA, T3, T2 | 0
RIVERSIDE | WILDOMAR | 0 | 0 | 0 | 0 | 0 | Non HFRA, T3, T2 | 0
RIVERSIDE | WINERY | 853 | 26 | 27 | 171 | 879 | T3 | 0
RIVERSIDE | WOBEGONE | 1044 | 13 | 53 | 451 | 1057 | Non HFRA, T2 | 0
KERN | YANKEE | 1 | 2 | 0 | 0 | 3 | T3 | 0
RIVERSIDE | ZEVO | 871 | 25 | 0 | 11 | 896 | Non HFRA, T3 | 0
VENTURA | ZONE | 586 | 35 | 22 | 104 | 621 | Non HFRA, T3 | 0

## T06
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 04: Damage and Hazards to Overhead Facilities
Damage and Hazards
Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Type and Description of Damage
ANGUS | VENTURA | 1746409E | Tier 3 | Damaged/Broken OH Primary Wire
AVIATOR | RIVERSIDE | 2327122E | Tier 2 | Damaged/Broken OH Primary Wire
CHEVELLE | SAN BERNARDINO | 4931926E | Tier 3 | Damaged/Broken OH Primary Wire
DEL CARBON | SAN BERNARDINO | 1452116E | Tier 3 | Blown Fuses/Poor wire sag
JUBILEE | RIVERSIDE | 4656769E | Tier 2 | Damaged/Broken Pole
JUBILEE | RIVERSIDE | 1079822E | Tier 2 | Damaged/Broken OH Service
LA SIERRA | RIVERSIDE | 4239311E | Tier 2 | Wires Slapping in wind
ROS | RIVERSIDE | 1954637E | Tier 2 | Damaged/Broken OH Secondary
ROS | RIVERSIDE | 316988S | Tier 2 | Damaged/Broken Insulator(s)
ROTEC | RIVERSIDE | 1996945E | Tier 2 | Damaged/Broken OH Primary Wire
SAUNDERS | RIVERSIDE | 1588243E | Tier 3 | Wire down
SAUNDERS | RIVERSIDE | 1776015E | Tier 3 | Damaged/Broken OH Secondary
SAUNDERS | RIVERSIDE | 1776018E | Tier 3 | Damaged/Broken OH Service
SAUNDERS | RIVERSIDE | 19214S | Tier 3 | Damaged/Broken Secondary Pole
SAUNDERS | RIVERSIDE | 4212975E | Tier 3 | Damaged/Broken OH Secondary
SAUNDERS | RIVERSIDE | 4517723E | Tier 3 | Damaged/Broken OH service
SAUNDERS | RIVERSIDE | 4855309E | Tier 3 | Damaged/Broken OH service
SKY HI | SAN BERNARDINO | 4716280E | Tier 2 | Damaged/Broken OH Transformer
STAGHORN | RIVERSIDE | 1706976E | Tier 2 | Damaged/Broken OH Secondary
STARGLOW | RIVERSIDE | 46227CWT | Tier 2 | Damaged/Broken Insulator(s)
STARGLOW | RIVERSIDE | 46230CWT | Tier 2 | Damaged/Broken Insulator(s)
STORES | RIVERSIDE | 4429295E | Tier 3 | Damaged/Broken OH Transformer
STRATHERN | VENTURA | 1246605E | Tier 3 | Damaged/Broken Insulator(s)
VERA CRUZ | ORANGE | 4602836E | Tier 3 | Damaged/Broken Insulator(s)
WARHAWK | SAN BERNARDINO | 863654E | Tier 2 | Damaged/Broken OH Service

## T07
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 05: Notifications
Notification Timeline
Event Order | Notification Type | Requirement Timeline | Notification Sent To | Approximate Time Sent | Notes
Pre-De-Energization (prior) | Initial Notice for PSPS Event (Advanced Initial or Initial) | 72-48 hours | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-17 19:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-18 14:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-19 14:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 00:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 01:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 20:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 01:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:11
|  |  | Critical Facilities & Infrastructure | 2025-01-17 19:30
|  |  | Critical Facilities & Infrastructure | 2025-01-17 20:29
|  |  | Critical Facilities & Infrastructure | 2025-01-19 23:59
| Initial Notice for PSPS Event (Initial or Update) | 48-24 hours | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 18:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 20:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 13:05
|  |  | Critical Facilities & Infrastructure | 2025-01-19 14:20
|  |  | Critical Facilities & Infrastructure | 2025-01-18 10:15
|  |  | Critical Facilities & Infrastructure | 2025-01-18 10:17
|  |  | Critical Facilities & Infrastructure | 2025-01-18 10:20
|  |  | Critical Facilities & Infrastructure | 2025-01-18 10:25
|  |  | Critical Facilities & Infrastructure | 2025-01-18 10:42
|  |  | Critical Facilities & Infrastructure | 2025-01-18 14:35
|  |  | Critical Facilities & Infrastructure | 2025-01-19 14:39
|  |  | Critical Facilities & Infrastructure | 2025-01-19 16:21
|  |  | Critical Facilities & Infrastructure | 2025-01-20
|  |  | Critical Facilities & Infrastructure | 2025-01-20 00:03
|  |  | Critical Facilities & Infrastructure | 2025-01-20 00:12
|  |  | Critical Facilities & Infrastructure | 2025-01-20 00:19
|  |  | Critical Facilities & Infrastructure | 2025-01-20 00:42
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:23
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:26
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:34
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:44
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:44
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:47
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:26
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:12
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:18
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:21
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:24
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:34
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:23
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:30
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:36
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:40
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:52
|  |  | Critical Facilities & Infrastructure | 2025-01-22 06:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 17:48
|  |  | Critical Facilities & Infrastructure | 2025-01-22 17:57
|  |  | Critical Facilities & Infrastructure | 2025-01-22 18:00
|  |  | Critical Facilities & Infrastructure | 2025-01-22 18:35
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:18
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:38
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:53
|  |  | Critical Facilities & Infrastructure | 2025-01-23 01:56
|  |  | Critical Facilities & Infrastructure | 2025-01-23 03:36
|  |  | Critical Facilities & Infrastructure | 2025-01-23 03:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:48
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:54
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:14
|  |  | Critical Facilities & Infrastructure | 2025-01-24 16:35
|  |  | Critical Facilities & Infrastructure | 2025-01-24 16:39
|  |  | Critical Facilities & Infrastructure | 2025-01-25 13:42
|  |  | Critical Facilities & Infrastructure | 2025-01-25 13:44
|  |  | All other affected customers | 2025-01-18 10:15
|  |  | All other affected customers | 2025-01-18 10:17
|  |  | All other affected customers | 2025-01-18 10:20
|  |  | All other affected customers | 2025-01-18 10:25
|  |  | All other affected customers | 2025-01-18 10:42
|  |  | All other affected customers | 2025-01-18 14:35
|  |  | All other affected customers | 2025-01-19 14:20
|  |  | All other affected customers | 2025-01-19 14:39
|  |  | All other affected customers | 2025-01-19 16:21
|  |  | All other affected customers | 2025-01-19 23:59
|  |  | All other affected customers | 2025-01-20
|  |  | All other affected customers | 2025-01-20 00:03
|  |  | All other affected customers | 2025-01-20 00:12
|  |  | All other affected customers | 2025-01-20 00:19
|  |  | All other affected customers | 2025-01-20 00:42
|  |  | All other affected customers | 2025-01-20 14:23
|  |  | All other affected customers | 2025-01-20 14:26
|  |  | All other affected customers | 2025-01-20 14:34
|  |  | All other affected customers | 2025-01-20 14:38
|  |  | All other affected customers | 2025-01-20 14:44
|  |  | All other affected customers | 2025-01-20 23:39
|  |  | All other affected customers | 2025-01-20 23:44
|  |  | All other affected customers | 2025-01-20 23:47
|  |  | All other affected customers | 2025-01-21 00:26
|  |  | All other affected customers | 2025-01-21 14:42
|  |  | All other affected customers | 2025-01-21 15:12
|  |  | All other affected customers | 2025-01-21 15:18
|  |  | All other affected customers | 2025-01-21 15:21
|  |  | All other affected customers | 2025-01-21 15:24
|  |  | All other affected customers | 2025-01-21 15:27
|  |  | All other affected customers | 2025-01-21 15:34
|  |  | All other affected customers | 2025-01-21 15:37
|  |  | All other affected customers | 2025-01-22 01:30
|  |  | All other affected customers | 2025-01-22 04:59
|  |  | All other affected customers | 2025-01-22 05:36
|  |  | All other affected customers | 2025-01-22 05:37
|  |  | All other affected customers | 2025-01-22 05:40
|  |  | All other affected customers | 2025-01-22 05:52
|  |  | All other affected customers | 2025-01-22 06:37
|  |  | All other affected customers | 2025-01-22 17:48
|  |  | All other affected customers | 2025-01-22 17:57
|  |  | All other affected customers | 2025-01-22 18:00
|  |  | All other affected customers | 2025-01-22 18:35
|  |  | All other affected customers | 2025-01-22 20:18
|  |  | All other affected customers | 2025-01-22 20:37
|  |  | All other affected customers | 2025-01-22 20:38
|  |  | All other affected customers | 2025-01-22 20:53
|  |  | All other affected customers | 2025-01-23 01:56
|  |  | All other affected customers | 2025-01-23 02:39
|  |  | All other affected customers | 2025-01-23 03:10
|  |  | All other affected customers | 2025-01-23 03:28
|  |  | All other affected customers | 2025-01-23 03:36
|  |  | All other affected customers | 2025-01-23 03:52
|  |  | All other affected customers | 2025-01-23 16:37
|  |  | All other affected customers | 2025-01-23 16:48
|  |  | All other affected customers | 2025-01-23 16:54
|  |  | All other affected customers | 2025-01-24 06:14
|  |  | All other affected customers | 2025-01-24 07:16
|  |  | All other affected customers | 2025-01-24 16:35
|  |  | All other affected customers | 2025-01-24 16:39
|  |  | All other affected customers | 2025-01-25 13:42
|  |  | All other affected customers | 2025-01-25 13:44
|  |  | All other affected customers | 2025-01-25 13:46
| Imminent De-Energize (Expected) | 4-1 hour | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 04:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 07:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 07:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 07:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 07:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 07:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 07:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 08:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 08:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 12:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 12:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 12:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 12:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 03:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 05:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 08:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 16:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 16:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 17:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 19:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 19:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 19:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 20:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 21:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 21:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 21:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 22:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 23:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 00:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 02:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 02:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 04:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 05:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 20:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 22:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 13:26
|  |  | Critical Facilities & Infrastructure | 2025-01-20 05:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 05:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 05:45
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:06
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:09
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:10
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:11
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:21
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:22
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:34
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:37
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:41
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:46
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:03
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:08
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:10
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:12
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:22
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:33
|  |  | Critical Facilities & Infrastructure | 2025-01-20 08:52
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:08
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:22
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:23
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:24
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:25
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:26
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:33
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:34
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:35
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:36
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:37
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:44
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:00
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:03
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:04
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:10
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:15
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:16
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:17
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:27
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:28
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:32
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:33
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:09
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:15
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:16
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:17
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:19
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:30
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:33
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:43
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:47
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:58
|  |  | Critical Facilities & Infrastructure | 2025-01-20 12:09
|  |  | Critical Facilities & Infrastructure | 2025-01-20 12:50
|  |  | Critical Facilities & Infrastructure | 2025-01-20 12:52
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:49
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:54
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:55
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:18
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:36
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:45
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:50
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:00
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:01
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:22
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:41
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:48
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:27
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:02
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:04
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:35
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:12
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:13
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:25
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:44
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:49
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:01
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:09
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:28
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:41
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:56
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:04
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:19
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:49
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:59
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:01
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:05
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:36
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:37
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:37
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:46
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:28
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:31
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:36
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:55
|  |  | Critical Facilities & Infrastructure | 2025-01-21 03:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 03:19
|  |  | Critical Facilities & Infrastructure | 2025-01-21 03:40
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:21
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:24
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:30
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:39
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:47
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:52
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:45
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:49
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:53
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:37
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:49
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:48
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:01
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:08
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:18
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:51
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:57
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:46
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:02
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:36
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:43
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:45
|  |  | Critical Facilities & Infrastructure | 2025-01-22 16:52
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:18
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:27
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:38
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:53
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:00
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:19
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:21
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:26
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:40
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:48
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:57
|  |  | Critical Facilities & Infrastructure | 2025-01-22 22:19
|  |  | Critical Facilities & Infrastructure | 2025-01-23 00:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:34
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 05:34
|  |  | Critical Facilities & Infrastructure | 2025-01-23 05:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 05:48
|  |  | Critical Facilities & Infrastructure | 2025-01-23 05:57
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:46
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:50
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:58
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:13
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:48
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:59
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:19
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:35
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:50
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:54
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:24
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:35
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:40
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:24
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:46
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:48
|  |  | Critical Facilities & Infrastructure | 2025-01-25 04:16
|  |  | Critical Facilities & Infrastructure | 2025-01-25 10:36
|  |  | Critical Facilities & Infrastructure | 2025-01-25 13:28
|  |  | Critical Facilities & Infrastructure | 2025-01-25 13:33
|  |  | All other affected customers | 2025-01-20 05:29
|  |  | All other affected customers | 2025-01-20 05:39
|  |  | All other affected customers | 2025-01-20 05:45
|  |  | All other affected customers | 2025-01-20 05:49
|  |  | All other affected customers | 2025-01-20 06:07
|  |  | All other affected customers | 2025-01-20 06:09
|  |  | All other affected customers | 2025-01-20 06:10
|  |  | All other affected customers | 2025-01-20 06:11
|  |  | All other affected customers | 2025-01-20 06:21
|  |  | All other affected customers | 2025-01-20 06:22
|  |  | All other affected customers | 2025-01-20 06:31
|  |  | All other affected customers | 2025-01-20 06:34
|  |  | All other affected customers | 2025-01-20 06:41
|  |  | All other affected customers | 2025-01-20 06:46
|  |  | All other affected customers | 2025-01-20 07:03
|  |  | All other affected customers | 2025-01-20 07:08
|  |  | All other affected customers | 2025-01-20 07:10
|  |  | All other affected customers | 2025-01-20 07:11
|  |  | All other affected customers | 2025-01-20 07:12
|  |  | All other affected customers | 2025-01-20 07:22
|  |  | All other affected customers | 2025-01-20 08:52
|  |  | All other affected customers | 2025-01-20 09:08
|  |  | All other affected customers | 2025-01-20 09:18
|  |  | All other affected customers | 2025-01-20 09:22
|  |  | All other affected customers | 2025-01-20 09:23
|  |  | All other affected customers | 2025-01-20 09:24
|  |  | All other affected customers | 2025-01-20 09:25
|  |  | All other affected customers | 2025-01-20 09:26
|  |  | All other affected customers | 2025-01-20 09:29
|  |  | All other affected customers | 2025-01-20 09:31
|  |  | All other affected customers | 2025-01-20 09:33
|  |  | All other affected customers | 2025-01-20 09:34
|  |  | All other affected customers | 2025-01-20 09:35
|  |  | All other affected customers | 2025-01-20 09:36
|  |  | All other affected customers | 2025-01-20 09:37
|  |  | All other affected customers | 2025-01-20 09:38
|  |  | All other affected customers | 2025-01-20 09:39
|  |  | All other affected customers | 2025-01-20 09:44
|  |  | All other affected customers | 2025-01-20 10:00
|  |  | All other affected customers | 2025-01-20 10:02
|  |  | All other affected customers | 2025-01-20 10:03
|  |  | All other affected customers | 2025-01-20 10:04
|  |  | All other affected customers | 2025-01-20 10:07
|  |  | All other affected customers | 2025-01-20 10:10
|  |  | All other affected customers | 2025-01-20 10:15
|  |  | All other affected customers | 2025-01-20 10:16
|  |  | All other affected customers | 2025-01-20 10:17
|  |  | All other affected customers | 2025-01-20 10:27
|  |  | All other affected customers | 2025-01-20 10:28
|  |  | All other affected customers | 2025-01-20 10:32
|  |  | All other affected customers | 2025-01-20 10:33
|  |  | All other affected customers | 2025-01-20 10:54
|  |  | All other affected customers | 2025-01-20 11:09
|  |  | All other affected customers | 2025-01-20 11:16
|  |  | All other affected customers | 2025-01-20 11:17
|  |  | All other affected customers | 2025-01-20 11:29
|  |  | All other affected customers | 2025-01-20 11:30
|  |  | All other affected customers | 2025-01-20 11:33
|  |  | All other affected customers | 2025-01-20 11:43
|  |  | All other affected customers | 2025-01-20 11:47
|  |  | All other affected customers | 2025-01-20 11:58
|  |  | All other affected customers | 2025-01-20 12:09
|  |  | All other affected customers | 2025-01-20 12:50
|  |  | All other affected customers | 2025-01-20 12:52
|  |  | All other affected customers | 2025-01-20 13:49
|  |  | All other affected customers | 2025-01-20 13:52
|  |  | All other affected customers | 2025-01-20 13:54
|  |  | All other affected customers | 2025-01-20 13:55
|  |  | All other affected customers | 2025-01-20 14:18
|  |  | All other affected customers | 2025-01-20 14:36
|  |  | All other affected customers | 2025-01-20 14:45
|  |  | All other affected customers | 2025-01-20 14:50
|  |  | All other affected customers | 2025-01-20 14:56
|  |  | All other affected customers | 2025-01-20 15:00
|  |  | All other affected customers | 2025-01-20 15:01
|  |  | All other affected customers | 2025-01-20 15:22
|  |  | All other affected customers | 2025-01-20 15:29
|  |  | All other affected customers | 2025-01-20 15:41
|  |  | All other affected customers | 2025-01-20 15:48
|  |  | All other affected customers | 2025-01-20 16:26
|  |  | All other affected customers | 2025-01-20 16:27
|  |  | All other affected customers | 2025-01-20 16:28
|  |  | All other affected customers | 2025-01-20 16:39
|  |  | All other affected customers | 2025-01-20 16:50
|  |  | All other affected customers | 2025-01-20 17:02
|  |  | All other affected customers | 2025-01-20 17:04
|  |  | All other affected customers | 2025-01-20 17:28
|  |  | All other affected customers | 2025-01-20 17:31
|  |  | All other affected customers | 2025-01-20 17:35
|  |  | All other affected customers | 2025-01-20 17:38
|  |  | All other affected customers | 2025-01-20 18:13
|  |  | All other affected customers | 2025-01-20 18:25
|  |  | All other affected customers | 2025-01-20 18:39
|  |  | All other affected customers | 2025-01-20 18:44
|  |  | All other affected customers | 2025-01-20 18:49
|  |  | All other affected customers | 2025-01-20 18:59
|  |  | All other affected customers | 2025-01-20 19:01
|  |  | All other affected customers | 2025-01-20 19:09
|  |  | All other affected customers | 2025-01-20 19:20
|  |  | All other affected customers | 2025-01-20 19:28
|  |  | All other affected customers | 2025-01-20 19:31
|  |  | All other affected customers | 2025-01-20 19:41
|  |  | All other affected customers | 2025-01-20 19:56
|  |  | All other affected customers | 2025-01-20 19:59
|  |  | All other affected customers | 2025-01-20 20:04
|  |  | All other affected customers | 2025-01-20 20:05
|  |  | All other affected customers | 2025-01-20 20:06
|  |  | All other affected customers | 2025-01-20 20:07
|  |  | All other affected customers | 2025-01-20 20:10
|  |  | All other affected customers | 2025-01-20 20:19
|  |  | All other affected customers | 2025-01-20 20:39
|  |  | All other affected customers | 2025-01-20 20:49
|  |  | All other affected customers | 2025-01-20 20:59
|  |  | All other affected customers | 2025-01-20 21:01
|  |  | All other affected customers | 2025-01-20 21:05
|  |  | All other affected customers | 2025-01-20 21:36
|  |  | All other affected customers | 2025-01-20 21:37
|  |  | All other affected customers | 2025-01-20 23:31
|  |  | All other affected customers | 2025-01-20 23:37
|  |  | All other affected customers | 2025-01-20 23:46
|  |  | All other affected customers | 2025-01-21 00:28
|  |  | All other affected customers | 2025-01-21 00:31
|  |  | All other affected customers | 2025-01-21 00:34
|  |  | All other affected customers | 2025-01-21 00:36
|  |  | All other affected customers | 2025-01-21 00:55
|  |  | All other affected customers | 2025-01-21 03:10
|  |  | All other affected customers | 2025-01-21 03:19
|  |  | All other affected customers | 2025-01-21 03:40
|  |  | All other affected customers | 2025-01-21 06:21
|  |  | All other affected customers | 2025-01-21 06:24
|  |  | All other affected customers | 2025-01-21 06:30
|  |  | All other affected customers | 2025-01-21 06:39
|  |  | All other affected customers | 2025-01-21 06:44
|  |  | All other affected customers | 2025-01-21 06:47
|  |  | All other affected customers | 2025-01-21 06:52
|  |  | All other affected customers | 2025-01-21 07:45
|  |  | All other affected customers | 2025-01-21 07:49
|  |  | All other affected customers | 2025-01-21 07:53
|  |  | All other affected customers | 2025-01-21 09:05
|  |  | All other affected customers | 2025-01-21 09:06
|  |  | All other affected customers | 2025-01-21 09:08
|  |  | All other affected customers | 2025-01-21 09:37
|  |  | All other affected customers | 2025-01-21 09:49
|  |  | All other affected customers | 2025-01-21 10:31
|  |  | All other affected customers | 2025-01-21 11:10
|  |  | All other affected customers | 2025-01-21 15:25
|  |  | All other affected customers | 2025-01-21 15:27
|  |  | All other affected customers | 2025-01-21 15:34
|  |  | All other affected customers | 2025-01-21 15:37
|  |  | All other affected customers | 2025-01-22 03:48
|  |  | All other affected customers | 2025-01-22 04:01
|  |  | All other affected customers | 2025-01-22 04:47
|  |  | All other affected customers | 2025-01-22 05:08
|  |  | All other affected customers | 2025-01-22 08:53
|  |  | All other affected customers | 2025-01-22 09:18
|  |  | All other affected customers | 2025-01-22 09:51
|  |  | All other affected customers | 2025-01-22 11:11
|  |  | All other affected customers | 2025-01-22 11:37
|  |  | All other affected customers | 2025-01-22 12:37
|  |  | All other affected customers | 2025-01-22 12:46
|  |  | All other affected customers | 2025-01-22 13:02
|  |  | All other affected customers | 2025-01-22 13:36
|  |  | All other affected customers | 2025-01-22 13:43
|  |  | All other affected customers | 2025-01-22 13:45
|  |  | All other affected customers | 2025-01-22 13:46
|  |  | All other affected customers | 2025-01-22 15:22
|  |  | All other affected customers | 2025-01-22 15:52
|  |  | All other affected customers | 2025-01-22 16:02
|  |  | All other affected customers | 2025-01-22 16:52
|  |  | All other affected customers | 2025-01-22 17:13
|  |  | All other affected customers | 2025-01-22 19:20
|  |  | All other affected customers | 2025-01-22 19:21
|  |  | All other affected customers | 2025-01-22 20:06
|  |  | All other affected customers | 2025-01-22 20:18
|  |  | All other affected customers | 2025-01-22 20:27
|  |  | All other affected customers | 2025-01-22 20:37
|  |  | All other affected customers | 2025-01-22 20:38
|  |  | All other affected customers | 2025-01-22 20:53
|  |  | All other affected customers | 2025-01-22 21:00
|  |  | All other affected customers | 2025-01-22 21:14
|  |  | All other affected customers | 2025-01-22 21:19
|  |  | All other affected customers | 2025-01-22 21:21
|  |  | All other affected customers | 2025-01-22 21:26
|  |  | All other affected customers | 2025-01-22 21:40
|  |  | All other affected customers | 2025-01-22 21:48
|  |  | All other affected customers | 2025-01-22 21:57
|  |  | All other affected customers | 2025-01-22 22:01
|  |  | All other affected customers | 2025-01-22 22:19
|  |  | All other affected customers | 2025-01-23 00:37
|  |  | All other affected customers | 2025-01-23 02:11
|  |  | All other affected customers | 2025-01-23 04:33
|  |  | All other affected customers | 2025-01-23 04:34
|  |  | All other affected customers | 2025-01-23 04:43
|  |  | All other affected customers | 2025-01-23 04:45
|  |  | All other affected customers | 2025-01-23 05:48
|  |  | All other affected customers | 2025-01-23 05:50
|  |  | All other affected customers | 2025-01-23 05:57
|  |  | All other affected customers | 2025-01-23 06:28
|  |  | All other affected customers | 2025-01-23 06:45
|  |  | All other affected customers | 2025-01-23 06:46
|  |  | All other affected customers | 2025-01-23 06:50
|  |  | All other affected customers | 2025-01-23 06:58
|  |  | All other affected customers | 2025-01-23 07:16
|  |  | All other affected customers | 2025-01-23 07:22
|  |  | All other affected customers | 2025-01-23 07:48
|  |  | All other affected customers | 2025-01-23 07:59
|  |  | All other affected customers | 2025-01-23 08:16
|  |  | All other affected customers | 2025-01-23 08:19
|  |  | All other affected customers | 2025-01-23 08:39
|  |  | All other affected customers | 2025-01-23 09:28
|  |  | All other affected customers | 2025-01-23 09:35
|  |  | All other affected customers | 2025-01-23 09:37
|  |  | All other affected customers | 2025-01-23 09:40
|  |  | All other affected customers | 2025-01-23 09:42
|  |  | All other affected customers | 2025-01-23 09:44
|  |  | All other affected customers | 2025-01-23 09:47
|  |  | All other affected customers | 2025-01-23 09:48
|  |  | All other affected customers | 2025-01-23 09:50
|  |  | All other affected customers | 2025-01-23 09:54
|  |  | All other affected customers | 2025-01-23 10:02
|  |  | All other affected customers | 2025-01-23 10:24
|  |  | All other affected customers | 2025-01-23 10:34
|  |  | All other affected customers | 2025-01-23 10:35
|  |  | All other affected customers | 2025-01-23 10:40
|  |  | All other affected customers | 2025-01-23 10:45
|  |  | All other affected customers | 2025-01-23 10:49
|  |  | All other affected customers | 2025-01-23 11:02
|  |  | All other affected customers | 2025-01-23 11:27
|  |  | All other affected customers | 2025-01-23 11:36
|  |  | All other affected customers | 2025-01-23 11:56
|  |  | All other affected customers | 2025-01-23 12:01
|  |  | All other affected customers | 2025-01-23 12:11
|  |  | All other affected customers | 2025-01-23 12:24
|  |  | All other affected customers | 2025-01-23 13:11
|  |  | All other affected customers | 2025-01-23 14:46
|  |  | All other affected customers | 2025-01-24 20:23
|  |  | All other affected customers | 2025-01-24 23:26
|  |  | All other affected customers | 2025-01-24 23:40
|  |  | All other affected customers | 2025-01-25 04:16
|  |  | All other affected customers | 2025-01-25 09:15
|  |  | All other affected customers | 2025-01-25 10:36
|  |  | All other affected customers | 2025-01-25 13:28
|  |  | All other affected customers | 2025-01-25 13:33
In-Event (during) | De-Energized (Shutoff) | De-energization | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 05:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 06:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 09:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 10:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 11:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 13:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 14:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 15:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 22:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 22:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 00:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 01:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 01:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 02:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 02:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 03:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 03:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 04:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 08:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 10:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 10:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 16:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 16:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 17:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 19:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 21:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 22:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 01:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 02:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 03:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 03:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 04:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 04:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 04:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 06:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 07:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 08:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 09:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 15:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 07:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 22:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 22:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 23:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 03:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 03:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 04:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 12:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 13:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 14:30
|  |  | Critical Facilities & Infrastructure | 2025-01-20 05:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 06:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 07:00
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:25
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:26
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 09:33
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:27
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:28
|  |  | Critical Facilities & Infrastructure | 2025-01-20 10:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:12
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:16
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:17
|  |  | Critical Facilities & Infrastructure | 2025-01-20 11:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:21
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:37
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:41
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:52
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:55
|  |  | Critical Facilities & Infrastructure | 2025-01-20 13:59
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:02
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:11
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:47
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:50
|  |  | Critical Facilities & Infrastructure | 2025-01-20 14:58
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:01
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:22
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:41
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:46
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:48
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:51
|  |  | Critical Facilities & Infrastructure | 2025-01-20 15:57
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:12
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:33
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:45
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:48
|  |  | Critical Facilities & Infrastructure | 2025-01-20 16:54
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:53
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:54
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:56
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:57
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:04
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:30
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:40
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:49
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:59
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:09
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:10
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:20
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:29
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:37
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:39
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:41
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:09
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:10
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:16
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:17
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:19
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:23
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:38
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:53
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:08
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:25
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:27
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:35
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:40
|  |  | Critical Facilities & Infrastructure | 2025-01-20 22:06
|  |  | Critical Facilities & Infrastructure | 2025-01-20 22:34
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:31
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:15
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:18
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:23
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:41
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:57
|  |  | Critical Facilities & Infrastructure | 2025-01-21 00:58
|  |  | Critical Facilities & Infrastructure | 2025-01-21 01:17
|  |  | Critical Facilities & Infrastructure | 2025-01-21 02:02
|  |  | Critical Facilities & Infrastructure | 2025-01-21 02:12
|  |  | Critical Facilities & Infrastructure | 2025-01-21 03:47
|  |  | Critical Facilities & Infrastructure | 2025-01-21 04:07
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:11
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:21
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:33
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 06:39
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:02
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:29
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:49
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:54
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:55
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:57
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:09
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:08
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:43
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:46
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:49
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:18
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:19
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:14
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:15
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:23
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:03
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:16
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:04
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:59
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:41
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:45
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:20
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:06
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:07
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:52
|  |  | Critical Facilities & Infrastructure | 2025-01-22 08:26
|  |  | Critical Facilities & Infrastructure | 2025-01-22 08:27
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:18
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:19
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:28
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:41
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:51
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:57
|  |  | Critical Facilities & Infrastructure | 2025-01-22 10:30
|  |  | Critical Facilities & Infrastructure | 2025-01-22 10:58
|  |  | Critical Facilities & Infrastructure | 2025-01-22 11:47
|  |  | Critical Facilities & Infrastructure | 2025-01-22 11:48
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:09
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:13
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:16
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:18
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:19
|  |  | Critical Facilities & Infrastructure | 2025-01-22 15:27
|  |  | Critical Facilities & Infrastructure | 2025-01-22 16:02
|  |  | Critical Facilities & Infrastructure | 2025-01-22 16:06
|  |  | Critical Facilities & Infrastructure | 2025-01-22 16:26
|  |  | Critical Facilities & Infrastructure | 2025-01-22 17:09
|  |  | Critical Facilities & Infrastructure | 2025-01-22 17:11
|  |  | Critical Facilities & Infrastructure | 2025-01-22 17:12
|  |  | Critical Facilities & Infrastructure | 2025-01-22 19:20
|  |  | Critical Facilities & Infrastructure | 2025-01-22 21:00
|  |  | Critical Facilities & Infrastructure | 2025-01-22 22:58
|  |  | Critical Facilities & Infrastructure | 2025-01-23 01:23
|  |  | Critical Facilities & Infrastructure | 2025-01-23 01:56
|  |  | Critical Facilities & Infrastructure | 2025-01-23 01:59
|  |  | Critical Facilities & Infrastructure | 2025-01-23 02:00
|  |  | Critical Facilities & Infrastructure | 2025-01-23 03:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:27
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:38
|  |  | Critical Facilities & Infrastructure | 2025-01-23 05:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:17
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:36
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:38
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:56
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:57
|  |  | Critical Facilities & Infrastructure | 2025-01-23 06:58
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:34
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:35
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:40
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:51
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:54
|  |  | Critical Facilities & Infrastructure | 2025-01-23 07:58
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:00
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:27
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:29
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:30
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:32
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:36
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:38
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:39
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:46
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:49
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:50
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:54
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:03
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:06
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:12
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:26
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:29
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:31
|  |  | Critical Facilities & Infrastructure | 2025-01-23 09:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:01
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:07
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:14
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:18
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:19
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:24
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:31
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:34
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:35
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:43
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:47
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:51
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:54
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:06
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:07
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:09
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:17
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:21
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:23
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:26
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:29
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:33
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:56
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:01
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:06
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:27
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:32
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:50
|  |  | Critical Facilities & Infrastructure | 2025-01-23 15:40
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:00
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:52
|  |  | Critical Facilities & Infrastructure | 2025-01-24 07:16
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:50
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:10
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:40
|  |  | Critical Facilities & Infrastructure | 2025-01-25 03:26
|  |  | Critical Facilities & Infrastructure | 2025-01-25 04:46
|  |  | Critical Facilities & Infrastructure | 2025-01-25 04:47
|  |  | Critical Facilities & Infrastructure | 2025-01-25 04:49
|  |  | Critical Facilities & Infrastructure | 2025-01-25 11:18
|  |  | Critical Facilities & Infrastructure | 2025-01-25 13:15
|  |  | Critical Facilities & Infrastructure | 2025-01-25 13:33
|  |  | Critical Facilities & Infrastructure | 2025-01-26 19:10
|  |  | All other affected customers | 2025-01-20 05:38
|  |  | All other affected customers | 2025-01-20 06:38
|  |  | All other affected customers | 2025-01-20 07:00
|  |  | All other affected customers | 2025-01-20 09:16
|  |  | All other affected customers | 2025-01-20 09:25
|  |  | All other affected customers | 2025-01-20 09:26
|  |  | All other affected customers | 2025-01-20 09:29
|  |  | All other affected customers | 2025-01-20 09:33
|  |  | All other affected customers | 2025-01-20 10:07
|  |  | All other affected customers | 2025-01-20 10:08
|  |  | All other affected customers | 2025-01-20 10:27
|  |  | All other affected customers | 2025-01-20 10:28
|  |  | All other affected customers | 2025-01-20 10:39
|  |  | All other affected customers | 2025-01-20 11:12
|  |  | All other affected customers | 2025-01-20 11:16
|  |  | All other affected customers | 2025-01-20 11:17
|  |  | All other affected customers | 2025-01-20 11:29
|  |  | All other affected customers | 2025-01-20 13:21
|  |  | All other affected customers | 2025-01-20 13:29
|  |  | All other affected customers | 2025-01-20 13:37
|  |  | All other affected customers | 2025-01-20 13:41
|  |  | All other affected customers | 2025-01-20 13:52
|  |  | All other affected customers | 2025-01-20 13:55
|  |  | All other affected customers | 2025-01-20 13:59
|  |  | All other affected customers | 2025-01-20 14:02
|  |  | All other affected customers | 2025-01-20 14:03
|  |  | All other affected customers | 2025-01-20 14:07
|  |  | All other affected customers | 2025-01-20 14:11
|  |  | All other affected customers | 2025-01-20 14:45
|  |  | All other affected customers | 2025-01-20 14:47
|  |  | All other affected customers | 2025-01-20 14:50
|  |  | All other affected customers | 2025-01-20 14:58
|  |  | All other affected customers | 2025-01-20 15:22
|  |  | All other affected customers | 2025-01-20 15:41
|  |  | All other affected customers | 2025-01-20 15:46
|  |  | All other affected customers | 2025-01-20 15:48
|  |  | All other affected customers | 2025-01-20 15:51
|  |  | All other affected customers | 2025-01-20 15:57
|  |  | All other affected customers | 2025-01-20 16:12
|  |  | All other affected customers | 2025-01-20 16:27
|  |  | All other affected customers | 2025-01-20 16:33
|  |  | All other affected customers | 2025-01-20 16:48
|  |  | All other affected customers | 2025-01-20 16:54
|  |  | All other affected customers | 2025-01-20 17:27
|  |  | All other affected customers | 2025-01-20 17:53
|  |  | All other affected customers | 2025-01-20 17:54
|  |  | All other affected customers | 2025-01-20 17:56
|  |  | All other affected customers | 2025-01-20 17:57
|  |  | All other affected customers | 2025-01-20 18:04
|  |  | All other affected customers | 2025-01-20 18:07
|  |  | All other affected customers | 2025-01-20 18:30
|  |  | All other affected customers | 2025-01-20 18:40
|  |  | All other affected customers | 2025-01-20 18:49
|  |  | All other affected customers | 2025-01-20 18:57
|  |  | All other affected customers | 2025-01-20 18:59
|  |  | All other affected customers | 2025-01-20 19:09
|  |  | All other affected customers | 2025-01-20 19:10
|  |  | All other affected customers | 2025-01-20 19:20
|  |  | All other affected customers | 2025-01-20 19:29
|  |  | All other affected customers | 2025-01-20 19:37
|  |  | All other affected customers | 2025-01-20 19:38
|  |  | All other affected customers | 2025-01-20 19:39
|  |  | All other affected customers | 2025-01-20 19:41
|  |  | All other affected customers | 2025-01-20 20:07
|  |  | All other affected customers | 2025-01-20 20:09
|  |  | All other affected customers | 2025-01-20 20:10
|  |  | All other affected customers | 2025-01-20 20:16
|  |  | All other affected customers | 2025-01-20 20:17
|  |  | All other affected customers | 2025-01-20 20:19
|  |  | All other affected customers | 2025-01-20 20:23
|  |  | All other affected customers | 2025-01-20 20:38
|  |  | All other affected customers | 2025-01-20 20:53
|  |  | All other affected customers | 2025-01-20 21:07
|  |  | All other affected customers | 2025-01-20 21:08
|  |  | All other affected customers | 2025-01-20 21:25
|  |  | All other affected customers | 2025-01-20 21:27
|  |  | All other affected customers | 2025-01-20 21:35
|  |  | All other affected customers | 2025-01-20 22:06
|  |  | All other affected customers | 2025-01-20 22:34
|  |  | All other affected customers | 2025-01-20 23:31
|  |  | All other affected customers | 2025-01-21 00:15
|  |  | All other affected customers | 2025-01-21 00:18
|  |  | All other affected customers | 2025-01-21 00:23
|  |  | All other affected customers | 2025-01-21 00:41
|  |  | All other affected customers | 2025-01-21 00:43
|  |  | All other affected customers | 2025-01-21 00:57
|  |  | All other affected customers | 2025-01-21 00:58
|  |  | All other affected customers | 2025-01-21 01:17
|  |  | All other affected customers | 2025-01-21 02:02
|  |  | All other affected customers | 2025-01-21 02:12
|  |  | All other affected customers | 2025-01-21 03:47
|  |  | All other affected customers | 2025-01-21 04:07
|  |  | All other affected customers | 2025-01-21 06:11
|  |  | All other affected customers | 2025-01-21 06:21
|  |  | All other affected customers | 2025-01-21 06:33
|  |  | All other affected customers | 2025-01-21 06:35
|  |  | All other affected customers | 2025-01-21 06:39
|  |  | All other affected customers | 2025-01-21 07:02
|  |  | All other affected customers | 2025-01-21 07:27
|  |  | All other affected customers | 2025-01-21 07:29
|  |  | All other affected customers | 2025-01-21 07:49
|  |  | All other affected customers | 2025-01-21 07:54
|  |  | All other affected customers | 2025-01-21 08:09
|  |  | All other affected customers | 2025-01-21 09:06
|  |  | All other affected customers | 2025-01-21 09:08
|  |  | All other affected customers | 2025-01-21 09:43
|  |  | All other affected customers | 2025-01-21 09:46
|  |  | All other affected customers | 2025-01-21 09:49
|  |  | All other affected customers | 2025-01-21 10:06
|  |  | All other affected customers | 2025-01-21 10:18
|  |  | All other affected customers | 2025-01-21 10:19
|  |  | All other affected customers | 2025-01-21 10:35
|  |  | All other affected customers | 2025-01-21 10:48
|  |  | All other affected customers | 2025-01-21 11:10
|  |  | All other affected customers | 2025-01-21 11:14
|  |  | All other affected customers | 2025-01-21 11:15
|  |  | All other affected customers | 2025-01-21 11:23
|  |  | All other affected customers | 2025-01-21 11:34
|  |  | All other affected customers | 2025-01-21 12:03
|  |  | All other affected customers | 2025-01-21 12:06
|  |  | All other affected customers | 2025-01-21 12:16
|  |  | All other affected customers | 2025-01-21 12:22
|  |  | All other affected customers | 2025-01-21 12:42
|  |  | All other affected customers | 2025-01-21 13:04
|  |  | All other affected customers | 2025-01-21 14:59
|  |  | All other affected customers | 2025-01-21 16:25
|  |  | All other affected customers | 2025-01-21 16:41
|  |  | All other affected customers | 2025-01-21 16:45
|  |  | All other affected customers | 2025-01-21 17:20
|  |  | All other affected customers | 2025-01-22 04:06
|  |  | All other affected customers | 2025-01-22 04:07
|  |  | All other affected customers | 2025-01-22 04:52
|  |  | All other affected customers | 2025-01-22 08:26
|  |  | All other affected customers | 2025-01-22 08:27
|  |  | All other affected customers | 2025-01-22 09:18
|  |  | All other affected customers | 2025-01-22 09:19
|  |  | All other affected customers | 2025-01-22 09:28
|  |  | All other affected customers | 2025-01-22 09:41
|  |  | All other affected customers | 2025-01-22 09:51
|  |  | All other affected customers | 2025-01-22 10:30
|  |  | All other affected customers | 2025-01-22 10:58
|  |  | All other affected customers | 2025-01-22 11:21
|  |  | All other affected customers | 2025-01-22 11:47
|  |  | All other affected customers | 2025-01-22 11:48
|  |  | All other affected customers | 2025-01-22 12:09
|  |  | All other affected customers | 2025-01-22 12:13
|  |  | All other affected customers | 2025-01-22 12:16
|  |  | All other affected customers | 2025-01-22 12:25
|  |  | All other affected customers | 2025-01-22 13:18
|  |  | All other affected customers | 2025-01-22 13:19
|  |  | All other affected customers | 2025-01-22 15:27
|  |  | All other affected customers | 2025-01-22 16:02
|  |  | All other affected customers | 2025-01-22 16:06
|  |  | All other affected customers | 2025-01-22 16:08
|  |  | All other affected customers | 2025-01-22 16:26
|  |  | All other affected customers | 2025-01-22 17:09
|  |  | All other affected customers | 2025-01-22 17:11
|  |  | All other affected customers | 2025-01-22 17:12
|  |  | All other affected customers | 2025-01-22 19:20
|  |  | All other affected customers | 2025-01-22 21:00
|  |  | All other affected customers | 2025-01-22 22:58
|  |  | All other affected customers | 2025-01-23 01:23
|  |  | All other affected customers | 2025-01-23 01:56
|  |  | All other affected customers | 2025-01-23 01:59
|  |  | All other affected customers | 2025-01-23 02:00
|  |  | All other affected customers | 2025-01-23 03:52
|  |  | All other affected customers | 2025-01-23 04:15
|  |  | All other affected customers | 2025-01-23 04:27
|  |  | All other affected customers | 2025-01-23 04:28
|  |  | All other affected customers | 2025-01-23 04:37
|  |  | All other affected customers | 2025-01-23 04:38
|  |  | All other affected customers | 2025-01-23 05:04
|  |  | All other affected customers | 2025-01-23 06:17
|  |  | All other affected customers | 2025-01-23 06:28
|  |  | All other affected customers | 2025-01-23 06:36
|  |  | All other affected customers | 2025-01-23 06:37
|  |  | All other affected customers | 2025-01-23 06:38
|  |  | All other affected customers | 2025-01-23 06:39
|  |  | All other affected customers | 2025-01-23 06:56
|  |  | All other affected customers | 2025-01-23 06:57
|  |  | All other affected customers | 2025-01-23 06:58
|  |  | All other affected customers | 2025-01-23 07:02
|  |  | All other affected customers | 2025-01-23 07:34
|  |  | All other affected customers | 2025-01-23 07:35
|  |  | All other affected customers | 2025-01-23 07:37
|  |  | All other affected customers | 2025-01-23 07:40
|  |  | All other affected customers | 2025-01-23 07:42
|  |  | All other affected customers | 2025-01-23 07:51
|  |  | All other affected customers | 2025-01-23 07:54
|  |  | All other affected customers | 2025-01-23 07:58
|  |  | All other affected customers | 2025-01-23 08:00
|  |  | All other affected customers | 2025-01-23 08:02
|  |  | All other affected customers | 2025-01-23 08:16
|  |  | All other affected customers | 2025-01-23 08:20
|  |  | All other affected customers | 2025-01-23 08:27
|  |  | All other affected customers | 2025-01-23 08:28
|  |  | All other affected customers | 2025-01-23 08:29
|  |  | All other affected customers | 2025-01-23 08:30
|  |  | All other affected customers | 2025-01-23 08:36
|  |  | All other affected customers | 2025-01-23 08:37
|  |  | All other affected customers | 2025-01-23 08:38
|  |  | All other affected customers | 2025-01-23 08:39
|  |  | All other affected customers | 2025-01-23 08:46
|  |  | All other affected customers | 2025-01-23 08:49
|  |  | All other affected customers | 2025-01-23 08:50
|  |  | All other affected customers | 2025-01-23 08:52
|  |  | All other affected customers | 2025-01-23 08:54
|  |  | All other affected customers | 2025-01-23 09:03
|  |  | All other affected customers | 2025-01-23 09:06
|  |  | All other affected customers | 2025-01-23 09:12
|  |  | All other affected customers | 2025-01-23 09:20
|  |  | All other affected customers | 2025-01-23 09:26
|  |  | All other affected customers | 2025-01-23 09:28
|  |  | All other affected customers | 2025-01-23 09:29
|  |  | All other affected customers | 2025-01-23 09:31
|  |  | All other affected customers | 2025-01-23 09:42
|  |  | All other affected customers | 2025-01-23 10:01
|  |  | All other affected customers | 2025-01-23 10:07
|  |  | All other affected customers | 2025-01-23 10:11
|  |  | All other affected customers | 2025-01-23 10:14
|  |  | All other affected customers | 2025-01-23 10:18
|  |  | All other affected customers | 2025-01-23 10:19
|  |  | All other affected customers | 2025-01-23 10:24
|  |  | All other affected customers | 2025-01-23 10:31
|  |  | All other affected customers | 2025-01-23 10:34
|  |  | All other affected customers | 2025-01-23 10:35
|  |  | All other affected customers | 2025-01-23 10:43
|  |  | All other affected customers | 2025-01-23 10:45
|  |  | All other affected customers | 2025-01-23 10:47
|  |  | All other affected customers | 2025-01-23 10:51
|  |  | All other affected customers | 2025-01-23 10:52
|  |  | All other affected customers | 2025-01-23 10:54
|  |  | All other affected customers | 2025-01-23 11:06
|  |  | All other affected customers | 2025-01-23 11:07
|  |  | All other affected customers | 2025-01-23 11:09
|  |  | All other affected customers | 2025-01-23 11:11
|  |  | All other affected customers | 2025-01-23 11:17
|  |  | All other affected customers | 2025-01-23 11:21
|  |  | All other affected customers | 2025-01-23 11:23
|  |  | All other affected customers | 2025-01-23 11:26
|  |  | All other affected customers | 2025-01-23 11:28
|  |  | All other affected customers | 2025-01-23 11:29
|  |  | All other affected customers | 2025-01-23 11:33
|  |  | All other affected customers | 2025-01-23 11:56
|  |  | All other affected customers | 2025-01-23 12:01
|  |  | All other affected customers | 2025-01-23 12:04
|  |  | All other affected customers | 2025-01-23 12:11
|  |  | All other affected customers | 2025-01-23 12:16
|  |  | All other affected customers | 2025-01-23 12:45
|  |  | All other affected customers | 2025-01-23 12:52
|  |  | All other affected customers | 2025-01-23 13:02
|  |  | All other affected customers | 2025-01-23 13:06
|  |  | All other affected customers | 2025-01-23 13:27
|  |  | All other affected customers | 2025-01-23 13:28
|  |  | All other affected customers | 2025-01-23 13:37
|  |  | All other affected customers | 2025-01-23 14:20
|  |  | All other affected customers | 2025-01-23 15:40
|  |  | All other affected customers | 2025-01-23 16:00
|  |  | All other affected customers | 2025-01-23 19:52
|  |  | All other affected customers | 2025-01-24 07:16
|  |  | All other affected customers | 2025-01-24 22:50
|  |  | All other affected customers | 2025-01-24 23:40
|  |  | All other affected customers | 2025-01-25 03:26
|  |  | All other affected customers | 2025-01-25 04:46
|  |  | All other affected customers | 2025-01-25 04:47
|  |  | All other affected customers | 2025-01-25 04:49
|  |  | All other affected customers | 2025-01-25 11:18
|  |  | All other affected customers | 2025-01-25 12:57
|  |  | All other affected customers | 2025-01-25 13:15
|  |  | All other affected customers | 2025-01-25 13:33
|  |  | All other affected customers | 2025-01-25 14:32
|  |  | All other affected customers | 2025-01-26 19:10
Restoration (after) | Imminent Re-Energize (Prepare to Restore) | Imminent Re-energization | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 16:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 17:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 22:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 03:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 21:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 01:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 07:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 07:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 07:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 15:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 22:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 04:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 11:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 13:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 15:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 15:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 15:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 16:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 23:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 00:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 00:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 07:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 12:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 07:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 14:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 07:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 07:28
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:02
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:20
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:26
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:32
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:56
|  |  | Critical Facilities & Infrastructure | 2025-01-20 17:57
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:07
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:13
|  |  | Critical Facilities & Infrastructure | 2025-01-20 22:11
|  |  | Critical Facilities & Infrastructure | 2025-01-21 03:21
|  |  | Critical Facilities & Infrastructure | 2025-01-21 03:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:04
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:12
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:17
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:19
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:21
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:41
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:43
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:56
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:08
|  |  | Critical Facilities & Infrastructure | 2025-01-21 09:09
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:52
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:15
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:19
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:21
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:23
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:26
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:30
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:00
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:20
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:13
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:23
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:24
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:02
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:03
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:04
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:15
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:28
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:37
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:45
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:56
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:11
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:24
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:37
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:40
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:41
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:44
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:50
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:51
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:58
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:01
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:03
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:05
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:31
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:33
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:46
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:07
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:31
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:57
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:15
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:02
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:12
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:24
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:26
|  |  | Critical Facilities & Infrastructure | 2025-01-21 21:07
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:13
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:35
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:58
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:00
|  |  | Critical Facilities & Infrastructure | 2025-01-22 07:46
|  |  | Critical Facilities & Infrastructure | 2025-01-22 07:47
|  |  | Critical Facilities & Infrastructure | 2025-01-22 07:55
|  |  | Critical Facilities & Infrastructure | 2025-01-22 16:06
|  |  | Critical Facilities & Infrastructure | 2025-01-22 22:38
|  |  | Critical Facilities & Infrastructure | 2025-01-23 04:18
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:10
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 11:14
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:27
|  |  | Critical Facilities & Infrastructure | 2025-01-23 13:53
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:23
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:36
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:44
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:46
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:59
|  |  | Critical Facilities & Infrastructure | 2025-01-23 15:40
|  |  | Critical Facilities & Infrastructure | 2025-01-23 15:59
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:09
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:30
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:31
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:34
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:37
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:00
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:03
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:06
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:18
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:44
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:47
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:49
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:53
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:57
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:01
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:07
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:22
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:39
|  |  | Critical Facilities & Infrastructure | 2025-01-23 20:26
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:01
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:53
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:55
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:57
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:05
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:07
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:10
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:12
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:17
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:39
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:43
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:36
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:40
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:42
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:43
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:47
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:08
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:10
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:19
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:41
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:44
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:48
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:53
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:59
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:01
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:26
|  |  | Critical Facilities & Infrastructure | 2025-01-24 07:33
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:10
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:02
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:05
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:13
|  |  | Critical Facilities & Infrastructure | 2025-01-24 12:40
|  |  | Critical Facilities & Infrastructure | 2025-01-24 15:30
|  |  | Critical Facilities & Infrastructure | 2025-01-25 07:21
|  |  | Critical Facilities & Infrastructure | 2025-01-25 14:22
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:52
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:54
|  |  | Critical Facilities & Infrastructure | 2025-01-26 07:02
|  |  | Critical Facilities & Infrastructure | 2025-01-26 07:43
|  |  | Critical Facilities & Infrastructure | 2025-01-27 07:24
|  |  | All other affected customers | 2025-01-20 17:02
|  |  | All other affected customers | 2025-01-20 17:20
|  |  | All other affected customers | 2025-01-20 17:26
|  |  | All other affected customers | 2025-01-20 17:31
|  |  | All other affected customers | 2025-01-20 17:32
|  |  | All other affected customers | 2025-01-20 17:56
|  |  | All other affected customers | 2025-01-20 17:57
|  |  | All other affected customers | 2025-01-20 18:07
|  |  | All other affected customers | 2025-01-20 20:13
|  |  | All other affected customers | 2025-01-20 22:11
|  |  | All other affected customers | 2025-01-21 03:21
|  |  | All other affected customers | 2025-01-21 03:22
|  |  | All other affected customers | 2025-01-21 07:42
|  |  | All other affected customers | 2025-01-21 08:12
|  |  | All other affected customers | 2025-01-21 08:17
|  |  | All other affected customers | 2025-01-21 08:19
|  |  | All other affected customers | 2025-01-21 08:21
|  |  | All other affected customers | 2025-01-21 08:23
|  |  | All other affected customers | 2025-01-21 08:27
|  |  | All other affected customers | 2025-01-21 08:41
|  |  | All other affected customers | 2025-01-21 08:43
|  |  | All other affected customers | 2025-01-21 08:48
|  |  | All other affected customers | 2025-01-21 08:56
|  |  | All other affected customers | 2025-01-21 09:06
|  |  | All other affected customers | 2025-01-21 09:08
|  |  | All other affected customers | 2025-01-21 09:09
|  |  | All other affected customers | 2025-01-21 10:52
|  |  | All other affected customers | 2025-01-21 11:15
|  |  | All other affected customers | 2025-01-21 11:19
|  |  | All other affected customers | 2025-01-21 11:21
|  |  | All other affected customers | 2025-01-21 11:23
|  |  | All other affected customers | 2025-01-21 11:25
|  |  | All other affected customers | 2025-01-21 11:26
|  |  | All other affected customers | 2025-01-21 11:27
|  |  | All other affected customers | 2025-01-21 11:30
|  |  | All other affected customers | 2025-01-21 12:00
|  |  | All other affected customers | 2025-01-21 12:20
|  |  | All other affected customers | 2025-01-21 12:35
|  |  | All other affected customers | 2025-01-21 13:10
|  |  | All other affected customers | 2025-01-21 13:13
|  |  | All other affected customers | 2025-01-21 13:23
|  |  | All other affected customers | 2025-01-21 13:24
|  |  | All other affected customers | 2025-01-21 14:02
|  |  | All other affected customers | 2025-01-21 14:03
|  |  | All other affected customers | 2025-01-21 14:04
|  |  | All other affected customers | 2025-01-21 14:15
|  |  | All other affected customers | 2025-01-21 14:25
|  |  | All other affected customers | 2025-01-21 14:28
|  |  | All other affected customers | 2025-01-21 14:37
|  |  | All other affected customers | 2025-01-21 14:42
|  |  | All other affected customers | 2025-01-21 14:45
|  |  | All other affected customers | 2025-01-21 15:06
|  |  | All other affected customers | 2025-01-21 15:08
|  |  | All other affected customers | 2025-01-21 15:11
|  |  | All other affected customers | 2025-01-21 15:22
|  |  | All other affected customers | 2025-01-21 15:24
|  |  | All other affected customers | 2025-01-21 15:34
|  |  | All other affected customers | 2025-01-21 15:37
|  |  | All other affected customers | 2025-01-21 15:40
|  |  | All other affected customers | 2025-01-21 15:41
|  |  | All other affected customers | 2025-01-21 15:44
|  |  | All other affected customers | 2025-01-21 15:50
|  |  | All other affected customers | 2025-01-21 15:51
|  |  | All other affected customers | 2025-01-21 15:58
|  |  | All other affected customers | 2025-01-21 16:01
|  |  | All other affected customers | 2025-01-21 16:03
|  |  | All other affected customers | 2025-01-21 16:05
|  |  | All other affected customers | 2025-01-21 16:10
|  |  | All other affected customers | 2025-01-21 16:31
|  |  | All other affected customers | 2025-01-21 16:33
|  |  | All other affected customers | 2025-01-21 16:46
|  |  | All other affected customers | 2025-01-21 17:07
|  |  | All other affected customers | 2025-01-21 17:31
|  |  | All other affected customers | 2025-01-21 17:57
|  |  | All other affected customers | 2025-01-21 18:15
|  |  | All other affected customers | 2025-01-21 19:02
|  |  | All other affected customers | 2025-01-21 19:10
|  |  | All other affected customers | 2025-01-21 19:12
|  |  | All other affected customers | 2025-01-21 19:13
|  |  | All other affected customers | 2025-01-21 20:24
|  |  | All other affected customers | 2025-01-21 20:26
|  |  | All other affected customers | 2025-01-21 21:07
|  |  | All other affected customers | 2025-01-21 22:13
|  |  | All other affected customers | 2025-01-21 22:34
|  |  | All other affected customers | 2025-01-21 22:35
|  |  | All other affected customers | 2025-01-22 01:58
|  |  | All other affected customers | 2025-01-22 05:00
|  |  | All other affected customers | 2025-01-22 07:46
|  |  | All other affected customers | 2025-01-22 07:47
|  |  | All other affected customers | 2025-01-22 07:55
|  |  | All other affected customers | 2025-01-22 15:34
|  |  | All other affected customers | 2025-01-22 16:06
|  |  | All other affected customers | 2025-01-22 22:38
|  |  | All other affected customers | 2025-01-23 04:18
|  |  | All other affected customers | 2025-01-23 10:10
|  |  | All other affected customers | 2025-01-23 10:11
|  |  | All other affected customers | 2025-01-23 11:14
|  |  | All other affected customers | 2025-01-23 12:11
|  |  | All other affected customers | 2025-01-23 13:27
|  |  | All other affected customers | 2025-01-23 13:53
|  |  | All other affected customers | 2025-01-23 14:16
|  |  | All other affected customers | 2025-01-23 14:23
|  |  | All other affected customers | 2025-01-23 14:36
|  |  | All other affected customers | 2025-01-23 14:44
|  |  | All other affected customers | 2025-01-23 14:46
|  |  | All other affected customers | 2025-01-23 14:59
|  |  | All other affected customers | 2025-01-23 15:40
|  |  | All other affected customers | 2025-01-23 15:59
|  |  | All other affected customers | 2025-01-23 16:20
|  |  | All other affected customers | 2025-01-23 17:02
|  |  | All other affected customers | 2025-01-23 17:04
|  |  | All other affected customers | 2025-01-23 17:09
|  |  | All other affected customers | 2025-01-23 17:20
|  |  | All other affected customers | 2025-01-23 17:30
|  |  | All other affected customers | 2025-01-23 17:31
|  |  | All other affected customers | 2025-01-23 17:34
|  |  | All other affected customers | 2025-01-23 17:37
|  |  | All other affected customers | 2025-01-23 18:00
|  |  | All other affected customers | 2025-01-23 18:03
|  |  | All other affected customers | 2025-01-23 18:06
|  |  | All other affected customers | 2025-01-23 18:18
|  |  | All other affected customers | 2025-01-23 18:44
|  |  | All other affected customers | 2025-01-23 18:47
|  |  | All other affected customers | 2025-01-23 18:49
|  |  | All other affected customers | 2025-01-23 18:52
|  |  | All other affected customers | 2025-01-23 18:53
|  |  | All other affected customers | 2025-01-23 18:57
|  |  | All other affected customers | 2025-01-23 19:01
|  |  | All other affected customers | 2025-01-23 19:07
|  |  | All other affected customers | 2025-01-23 19:22
|  |  | All other affected customers | 2025-01-23 19:39
|  |  | All other affected customers | 2025-01-23 20:26
|  |  | All other affected customers | 2025-01-23 21:01
|  |  | All other affected customers | 2025-01-23 21:53
|  |  | All other affected customers | 2025-01-23 21:55
|  |  | All other affected customers | 2025-01-23 21:57
|  |  | All other affected customers | 2025-01-23 22:02
|  |  | All other affected customers | 2025-01-23 22:05
|  |  | All other affected customers | 2025-01-23 22:07
|  |  | All other affected customers | 2025-01-23 22:10
|  |  | All other affected customers | 2025-01-23 22:12
|  |  | All other affected customers | 2025-01-23 22:17
|  |  | All other affected customers | 2025-01-23 23:39
|  |  | All other affected customers | 2025-01-23 23:43
|  |  | All other affected customers | 2025-01-24 00:36
|  |  | All other affected customers | 2025-01-24 00:40
|  |  | All other affected customers | 2025-01-24 00:42
|  |  | All other affected customers | 2025-01-24 00:43
|  |  | All other affected customers | 2025-01-24 00:47
|  |  | All other affected customers | 2025-01-24 01:08
|  |  | All other affected customers | 2025-01-24 01:10
|  |  | All other affected customers | 2025-01-24 01:19
|  |  | All other affected customers | 2025-01-24 01:41
|  |  | All other affected customers | 2025-01-24 01:44
|  |  | All other affected customers | 2025-01-24 01:48
|  |  | All other affected customers | 2025-01-24 01:53
|  |  | All other affected customers | 2025-01-24 03:59
|  |  | All other affected customers | 2025-01-24 04:01
|  |  | All other affected customers | 2025-01-24 05:26
|  |  | All other affected customers | 2025-01-24 07:33
|  |  | All other affected customers | 2025-01-24 09:10
|  |  | All other affected customers | 2025-01-24 10:02
|  |  | All other affected customers | 2025-01-24 10:05
|  |  | All other affected customers | 2025-01-24 10:13
|  |  | All other affected customers | 2025-01-24 12:40
|  |  | All other affected customers | 2025-01-24 15:30
|  |  | All other affected customers | 2025-01-25 07:21
|  |  | All other affected customers | 2025-01-25 14:22
|  |  | All other affected customers | 2025-01-25 15:52
|  |  | All other affected customers | 2025-01-25 15:54
|  |  | All other affected customers | 2025-01-26 07:02
|  |  | All other affected customers | 2025-01-26 07:35
|  |  | All other affected customers | 2025-01-27 07:24
| Re-Energized (Restored In Scope and/or Restored No Longer in Scope) | Re-energization | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 18:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 19:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 20:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 21:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 22:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 22:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 23:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 04:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 04:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 07:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 09:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 10:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 11:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 12:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 13:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 15:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 21:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 21:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 21:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 23:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 23:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 23:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 23:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 00:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 01:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 02:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 05:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 07:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 07:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 07:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 08:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 09:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 10:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 11:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 12:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 13:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 16:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 18:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 01:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 05:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 10:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 12:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 14:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 15:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 16:18
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 16:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 16:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 16:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 19:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 20:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 23:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 23:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 23:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 23:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 00:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 00:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 03:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 04:43
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 06:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 06:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 08:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 08:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:47
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 09:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 10:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 11:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 12:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 12:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 12:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 12:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 12:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 13:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 14:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 14:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 14:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 14:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 16:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 16:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 16:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 17:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 17:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 18:10
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 00:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 09:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 09:42
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:46
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 16:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 17:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 17:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 17:33
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 17:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 09:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 14:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 14:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 15:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 15:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-26 18:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-27 15:12
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:01
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:21
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:22
|  |  | Critical Facilities & Infrastructure | 2025-01-20 18:49
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:05
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:35
|  |  | Critical Facilities & Infrastructure | 2025-01-20 19:45
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:10
|  |  | Critical Facilities & Infrastructure | 2025-01-20 20:54
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:05
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:14
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:27
|  |  | Critical Facilities & Infrastructure | 2025-01-20 21:36
|  |  | Critical Facilities & Infrastructure | 2025-01-20 22:02
|  |  | Critical Facilities & Infrastructure | 2025-01-20 22:26
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:20
|  |  | Critical Facilities & Infrastructure | 2025-01-20 23:31
|  |  | Critical Facilities & Infrastructure | 2025-01-21 04:50
|  |  | Critical Facilities & Infrastructure | 2025-01-21 04:53
|  |  | Critical Facilities & Infrastructure | 2025-01-21 07:55
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 10:36
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:14
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 11:44
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:29
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 12:49
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:00
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:13
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:23
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:32
|  |  | Critical Facilities & Infrastructure | 2025-01-21 13:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:12
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:28
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:55
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:59
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:14
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:16
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:18
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:56
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:58
|  |  | Critical Facilities & Infrastructure | 2025-01-21 15:59
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:06
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:13
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:23
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:37
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:39
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:45
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:46
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:55
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:57
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:59
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:01
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:20
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:24
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:29
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:33
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:04
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:13
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:41
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:57
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:02
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:33
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:36
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:59
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:17
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:19
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:34
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:37
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:44
|  |  | Critical Facilities & Infrastructure | 2025-01-21 20:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 21:20
|  |  | Critical Facilities & Infrastructure | 2025-01-21 21:36
|  |  | Critical Facilities & Infrastructure | 2025-01-21 21:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:17
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:39
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:46
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:53
|  |  | Critical Facilities & Infrastructure | 2025-01-21 23:16
|  |  | Critical Facilities & Infrastructure | 2025-01-21 23:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 23:49
|  |  | Critical Facilities & Infrastructure | 2025-01-21 23:55
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:10
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:20
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:30
|  |  | Critical Facilities & Infrastructure | 2025-01-22 02:23
|  |  | Critical Facilities & Infrastructure | 2025-01-22 02:45
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:40
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:46
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:50
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:07
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:09
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:10
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:27
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:56
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:41
|  |  | Critical Facilities & Infrastructure | 2025-01-22 07:34
|  |  | Critical Facilities & Infrastructure | 2025-01-22 07:46
|  |  | Critical Facilities & Infrastructure | 2025-01-22 09:51
|  |  | Critical Facilities & Infrastructure | 2025-01-22 10:03
|  |  | Critical Facilities & Infrastructure | 2025-01-22 10:30
|  |  | Critical Facilities & Infrastructure | 2025-01-22 11:07
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:01
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:02
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:38
|  |  | Critical Facilities & Infrastructure | 2025-01-22 12:44
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:28
|  |  | Critical Facilities & Infrastructure | 2025-01-22 13:49
|  |  | Critical Facilities & Infrastructure | 2025-01-22 18:21
|  |  | Critical Facilities & Infrastructure | 2025-01-23 01:47
|  |  | Critical Facilities & Infrastructure | 2025-01-23 05:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 10:14
|  |  | Critical Facilities & Infrastructure | 2025-01-23 12:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 14:36
|  |  | Critical Facilities & Infrastructure | 2025-01-23 15:59
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:45
|  |  | Critical Facilities & Infrastructure | 2025-01-23 16:49
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:00
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:19
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:23
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:30
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:55
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:05
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:06
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:09
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:20
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:25
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:41
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:44
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:47
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:48
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:19
|  |  | Critical Facilities & Infrastructure | 2025-01-23 19:52
|  |  | Critical Facilities & Infrastructure | 2025-01-23 20:13
|  |  | Critical Facilities & Infrastructure | 2025-01-23 20:18
|  |  | Critical Facilities & Infrastructure | 2025-01-23 20:19
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:08
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:12
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:17
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:44
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:47
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:49
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:51
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:59
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:07
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:10
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:12
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:15
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:17
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:18
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:27
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:28
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:30
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:38
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:56
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:15
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:24
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:32
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:35
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:51
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:53
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:11
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:15
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:50
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:52
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:12
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:44
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:48
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:53
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:54
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:29
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:43
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:44
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:46
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:48
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:58
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:05
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:13
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:15
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:27
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:28
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:32
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:40
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:47
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:48
|  |  | Critical Facilities & Infrastructure | 2025-01-24 03:58
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:01
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:04
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:08
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:11
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:19
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:26
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:41
|  |  | Critical Facilities & Infrastructure | 2025-01-24 04:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:31
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:36
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:37
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:38
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:41
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:44
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:47
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:52
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:53
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:01
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:10
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:15
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:19
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:27
|  |  | Critical Facilities & Infrastructure | 2025-01-24 06:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 08:31
|  |  | Critical Facilities & Infrastructure | 2025-01-24 08:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:09
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:29
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:33
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:48
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:49
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:51
|  |  | Critical Facilities & Infrastructure | 2025-01-24 09:56
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:01
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:02
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:13
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:16
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:26
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:32
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:39
|  |  | Critical Facilities & Infrastructure | 2025-01-24 10:42
|  |  | Critical Facilities & Infrastructure | 2025-01-24 11:02
|  |  | Critical Facilities & Infrastructure | 2025-01-24 11:23
|  |  | Critical Facilities & Infrastructure | 2025-01-24 11:27
|  |  | Critical Facilities & Infrastructure | 2025-01-24 11:52
|  |  | Critical Facilities & Infrastructure | 2025-01-24 12:18
|  |  | Critical Facilities & Infrastructure | 2025-01-24 12:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 12:40
|  |  | Critical Facilities & Infrastructure | 2025-01-24 12:57
|  |  | Critical Facilities & Infrastructure | 2025-01-24 13:05
|  |  | Critical Facilities & Infrastructure | 2025-01-24 13:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 13:33
|  |  | Critical Facilities & Infrastructure | 2025-01-24 13:43
|  |  | Critical Facilities & Infrastructure | 2025-01-24 13:50
|  |  | Critical Facilities & Infrastructure | 2025-01-24 14:17
|  |  | Critical Facilities & Infrastructure | 2025-01-24 14:21
|  |  | Critical Facilities & Infrastructure | 2025-01-24 14:54
|  |  | Critical Facilities & Infrastructure | 2025-01-24 15:09
|  |  | Critical Facilities & Infrastructure | 2025-01-24 15:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 15:34
|  |  | Critical Facilities & Infrastructure | 2025-01-24 16:16
|  |  | Critical Facilities & Infrastructure | 2025-01-24 17:17
|  |  | Critical Facilities & Infrastructure | 2025-01-24 18:21
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:35
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:42
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:09
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:10
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:26
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:50
|  |  | Critical Facilities & Infrastructure | 2025-01-25 01:10
|  |  | Critical Facilities & Infrastructure | 2025-01-25 01:18
|  |  | Critical Facilities & Infrastructure | 2025-01-25 01:52
|  |  | Critical Facilities & Infrastructure | 2025-01-25 09:26
|  |  | Critical Facilities & Infrastructure | 2025-01-25 09:55
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:07
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:35
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:57
|  |  | Critical Facilities & Infrastructure | 2025-01-25 16:24
|  |  | Critical Facilities & Infrastructure | 2025-01-25 16:27
|  |  | Critical Facilities & Infrastructure | 2025-01-25 17:32
|  |  | Critical Facilities & Infrastructure | 2025-01-25 17:38
|  |  | Critical Facilities & Infrastructure | 2025-01-25 18:40
|  |  | Critical Facilities & Infrastructure | 2025-01-25 19:34
|  |  | Critical Facilities & Infrastructure | 2025-01-26 10:12
|  |  | Critical Facilities & Infrastructure | 2025-01-26 10:18
|  |  | Critical Facilities & Infrastructure | 2025-01-26 14:04
|  |  | Critical Facilities & Infrastructure | 2025-01-26 14:33
|  |  | Critical Facilities & Infrastructure | 2025-01-26 15:05
|  |  | Critical Facilities & Infrastructure | 2025-01-26 18:07
|  |  | Critical Facilities & Infrastructure | 2025-01-26 18:46
|  |  | Critical Facilities & Infrastructure | 2025-01-27 15:09
|  |  | All other affected customers | 2025-01-20 18:21
|  |  | All other affected customers | 2025-01-20 18:22
|  |  | All other affected customers | 2025-01-20 18:49
|  |  | All other affected customers | 2025-01-20 19:01
|  |  | All other affected customers | 2025-01-20 19:05
|  |  | All other affected customers | 2025-01-20 19:35
|  |  | All other affected customers | 2025-01-20 19:45
|  |  | All other affected customers | 2025-01-20 20:10
|  |  | All other affected customers | 2025-01-20 20:54
|  |  | All other affected customers | 2025-01-20 21:05
|  |  | All other affected customers | 2025-01-20 21:14
|  |  | All other affected customers | 2025-01-20 21:27
|  |  | All other affected customers | 2025-01-20 21:36
|  |  | All other affected customers | 2025-01-20 22:02
|  |  | All other affected customers | 2025-01-20 22:26
|  |  | All other affected customers | 2025-01-20 23:20
|  |  | All other affected customers | 2025-01-20 23:31
|  |  | All other affected customers | 2025-01-21 04:50
|  |  | All other affected customers | 2025-01-21 04:53
|  |  | All other affected customers | 2025-01-21 07:55
|  |  | All other affected customers | 2025-01-21 09:20
|  |  | All other affected customers | 2025-01-21 10:03
|  |  | All other affected customers | 2025-01-21 10:35
|  |  | All other affected customers | 2025-01-21 10:36
|  |  | All other affected customers | 2025-01-21 11:14
|  |  | All other affected customers | 2025-01-21 11:34
|  |  | All other affected customers | 2025-01-21 11:35
|  |  | All other affected customers | 2025-01-21 11:44
|  |  | All other affected customers | 2025-01-21 12:00
|  |  | All other affected customers | 2025-01-21 12:29
|  |  | All other affected customers | 2025-01-21 12:35
|  |  | All other affected customers | 2025-01-21 13:13
|  |  | All other affected customers | 2025-01-21 13:23
|  |  | All other affected customers | 2025-01-21 13:32
|  |  | All other affected customers | 2025-01-21 13:48
|  |  | All other affected customers | 2025-01-21 14:25
|  |  | All other affected customers | 2025-01-21 14:28
|  |  | All other affected customers | 2025-01-21 14:42
|  |  | All other affected customers | 2025-01-21 14:55
|  |  | All other affected customers | 2025-01-21 14:59
|  |  | All other affected customers | 2025-01-21 15:14
|  |  | All other affected customers | 2025-01-21 15:16
|  |  | All other affected customers | 2025-01-21 15:18
|  |  | All other affected customers | 2025-01-21 15:34
|  |  | All other affected customers | 2025-01-21 15:48
|  |  | All other affected customers | 2025-01-21 15:56
|  |  | All other affected customers | 2025-01-21 15:58
|  |  | All other affected customers | 2025-01-21 15:59
|  |  | All other affected customers | 2025-01-21 16:06
|  |  | All other affected customers | 2025-01-21 16:13
|  |  | All other affected customers | 2025-01-21 16:23
|  |  | All other affected customers | 2025-01-21 16:25
|  |  | All other affected customers | 2025-01-21 16:34
|  |  | All other affected customers | 2025-01-21 16:37
|  |  | All other affected customers | 2025-01-21 16:39
|  |  | All other affected customers | 2025-01-21 16:45
|  |  | All other affected customers | 2025-01-21 16:46
|  |  | All other affected customers | 2025-01-21 16:55
|  |  | All other affected customers | 2025-01-21 16:57
|  |  | All other affected customers | 2025-01-21 16:59
|  |  | All other affected customers | 2025-01-21 17:01
|  |  | All other affected customers | 2025-01-21 17:20
|  |  | All other affected customers | 2025-01-21 17:24
|  |  | All other affected customers | 2025-01-21 17:29
|  |  | All other affected customers | 2025-01-21 17:33
|  |  | All other affected customers | 2025-01-21 17:34
|  |  | All other affected customers | 2025-01-21 18:04
|  |  | All other affected customers | 2025-01-21 18:13
|  |  | All other affected customers | 2025-01-21 18:22
|  |  | All other affected customers | 2025-01-21 18:41
|  |  | All other affected customers | 2025-01-21 18:42
|  |  | All other affected customers | 2025-01-21 18:57
|  |  | All other affected customers | 2025-01-21 19:02
|  |  | All other affected customers | 2025-01-21 19:10
|  |  | All other affected customers | 2025-01-21 19:22
|  |  | All other affected customers | 2025-01-21 19:33
|  |  | All other affected customers | 2025-01-21 19:35
|  |  | All other affected customers | 2025-01-21 19:36
|  |  | All other affected customers | 2025-01-21 19:39
|  |  | All other affected customers | 2025-01-21 19:59
|  |  | All other affected customers | 2025-01-21 20:17
|  |  | All other affected customers | 2025-01-21 20:19
|  |  | All other affected customers | 2025-01-21 20:22
|  |  | All other affected customers | 2025-01-21 20:27
|  |  | All other affected customers | 2025-01-21 20:34
|  |  | All other affected customers | 2025-01-21 20:35
|  |  | All other affected customers | 2025-01-21 20:37
|  |  | All other affected customers | 2025-01-21 20:42
|  |  | All other affected customers | 2025-01-21 20:44
|  |  | All other affected customers | 2025-01-21 20:48
|  |  | All other affected customers | 2025-01-21 21:20
|  |  | All other affected customers | 2025-01-21 21:36
|  |  | All other affected customers | 2025-01-21 22:17
|  |  | All other affected customers | 2025-01-21 22:39
|  |  | All other affected customers | 2025-01-21 22:46
|  |  | All other affected customers | 2025-01-21 22:53
|  |  | All other affected customers | 2025-01-21 23:16
|  |  | All other affected customers | 2025-01-21 23:25
|  |  | All other affected customers | 2025-01-21 23:49
|  |  | All other affected customers | 2025-01-21 23:55
|  |  | All other affected customers | 2025-01-22 01:10
|  |  | All other affected customers | 2025-01-22 01:20
|  |  | All other affected customers | 2025-01-22 01:30
|  |  | All other affected customers | 2025-01-22 02:23
|  |  | All other affected customers | 2025-01-22 02:45
|  |  | All other affected customers | 2025-01-22 03:40
|  |  | All other affected customers | 2025-01-22 03:46
|  |  | All other affected customers | 2025-01-22 03:50
|  |  | All other affected customers | 2025-01-22 04:07
|  |  | All other affected customers | 2025-01-22 04:09
|  |  | All other affected customers | 2025-01-22 04:10
|  |  | All other affected customers | 2025-01-22 04:27
|  |  | All other affected customers | 2025-01-22 04:37
|  |  | All other affected customers | 2025-01-22 04:56
|  |  | All other affected customers | 2025-01-22 05:01
|  |  | All other affected customers | 2025-01-22 05:09
|  |  | All other affected customers | 2025-01-22 05:41
|  |  | All other affected customers | 2025-01-22 05:44
|  |  | All other affected customers | 2025-01-22 07:34
|  |  | All other affected customers | 2025-01-22 07:46
|  |  | All other affected customers | 2025-01-22 08:26
|  |  | All other affected customers | 2025-01-22 09:19
|  |  | All other affected customers | 2025-01-22 09:51
|  |  | All other affected customers | 2025-01-22 10:03
|  |  | All other affected customers | 2025-01-22 10:30
|  |  | All other affected customers | 2025-01-22 11:07
|  |  | All other affected customers | 2025-01-22 11:37
|  |  | All other affected customers | 2025-01-22 12:01
|  |  | All other affected customers | 2025-01-22 12:02
|  |  | All other affected customers | 2025-01-22 12:38
|  |  | All other affected customers | 2025-01-22 12:44
|  |  | All other affected customers | 2025-01-22 13:49
|  |  | All other affected customers | 2025-01-22 16:50
|  |  | All other affected customers | 2025-01-22 18:21
|  |  | All other affected customers | 2025-01-23 01:47
|  |  | All other affected customers | 2025-01-23 05:04
|  |  | All other affected customers | 2025-01-23 10:14
|  |  | All other affected customers | 2025-01-23 12:45
|  |  | All other affected customers | 2025-01-23 13:06
|  |  | All other affected customers | 2025-01-23 14:36
|  |  | All other affected customers | 2025-01-23 15:59
|  |  | All other affected customers | 2025-01-23 16:20
|  |  | All other affected customers | 2025-01-23 16:42
|  |  | All other affected customers | 2025-01-23 16:45
|  |  | All other affected customers | 2025-01-23 16:49
|  |  | All other affected customers | 2025-01-23 17:00
|  |  | All other affected customers | 2025-01-23 17:19
|  |  | All other affected customers | 2025-01-23 17:20
|  |  | All other affected customers | 2025-01-23 17:23
|  |  | All other affected customers | 2025-01-23 17:30
|  |  | All other affected customers | 2025-01-23 17:55
|  |  | All other affected customers | 2025-01-23 18:05
|  |  | All other affected customers | 2025-01-23 18:06
|  |  | All other affected customers | 2025-01-23 18:09
|  |  | All other affected customers | 2025-01-23 18:20
|  |  | All other affected customers | 2025-01-23 18:25
|  |  | All other affected customers | 2025-01-23 18:41
|  |  | All other affected customers | 2025-01-23 18:44
|  |  | All other affected customers | 2025-01-23 18:47
|  |  | All other affected customers | 2025-01-23 18:48
|  |  | All other affected customers | 2025-01-23 19:19
|  |  | All other affected customers | 2025-01-23 19:52
|  |  | All other affected customers | 2025-01-23 20:13
|  |  | All other affected customers | 2025-01-23 20:18
|  |  | All other affected customers | 2025-01-23 20:19
|  |  | All other affected customers | 2025-01-23 21:02
|  |  | All other affected customers | 2025-01-23 21:08
|  |  | All other affected customers | 2025-01-23 21:12
|  |  | All other affected customers | 2025-01-23 21:16
|  |  | All other affected customers | 2025-01-23 21:17
|  |  | All other affected customers | 2025-01-23 21:18
|  |  | All other affected customers | 2025-01-23 21:42
|  |  | All other affected customers | 2025-01-23 21:44
|  |  | All other affected customers | 2025-01-23 21:47
|  |  | All other affected customers | 2025-01-23 21:49
|  |  | All other affected customers | 2025-01-23 21:51
|  |  | All other affected customers | 2025-01-23 21:59
|  |  | All other affected customers | 2025-01-23 22:04
|  |  | All other affected customers | 2025-01-23 22:07
|  |  | All other affected customers | 2025-01-23 22:10
|  |  | All other affected customers | 2025-01-23 22:12
|  |  | All other affected customers | 2025-01-23 22:15
|  |  | All other affected customers | 2025-01-23 22:17
|  |  | All other affected customers | 2025-01-23 22:18
|  |  | All other affected customers | 2025-01-23 22:27
|  |  | All other affected customers | 2025-01-23 22:28
|  |  | All other affected customers | 2025-01-23 22:30
|  |  | All other affected customers | 2025-01-23 22:38
|  |  | All other affected customers | 2025-01-23 23:04
|  |  | All other affected customers | 2025-01-23 23:15
|  |  | All other affected customers | 2025-01-23 23:24
|  |  | All other affected customers | 2025-01-23 23:32
|  |  | All other affected customers | 2025-01-23 23:35
|  |  | All other affected customers | 2025-01-23 23:51
|  |  | All other affected customers | 2025-01-23 23:53
|  |  | All other affected customers | 2025-01-24 00:11
|  |  | All other affected customers | 2025-01-24 00:15
|  |  | All other affected customers | 2025-01-24 00:50
|  |  | All other affected customers | 2025-01-24 00:52
|  |  | All other affected customers | 2025-01-24 01:12
|  |  | All other affected customers | 2025-01-24 01:20
|  |  | All other affected customers | 2025-01-24 01:44
|  |  | All other affected customers | 2025-01-24 01:48
|  |  | All other affected customers | 2025-01-24 01:53
|  |  | All other affected customers | 2025-01-24 01:54
|  |  | All other affected customers | 2025-01-24 02:29
|  |  | All other affected customers | 2025-01-24 02:30
|  |  | All other affected customers | 2025-01-24 02:43
|  |  | All other affected customers | 2025-01-24 02:44
|  |  | All other affected customers | 2025-01-24 02:45
|  |  | All other affected customers | 2025-01-24 02:46
|  |  | All other affected customers | 2025-01-24 02:48
|  |  | All other affected customers | 2025-01-24 02:58
|  |  | All other affected customers | 2025-01-24 03:05
|  |  | All other affected customers | 2025-01-24 03:13
|  |  | All other affected customers | 2025-01-24 03:27
|  |  | All other affected customers | 2025-01-24 03:28
|  |  | All other affected customers | 2025-01-24 03:32
|  |  | All other affected customers | 2025-01-24 03:40
|  |  | All other affected customers | 2025-01-24 03:47
|  |  | All other affected customers | 2025-01-24 03:48
|  |  | All other affected customers | 2025-01-24 03:58
|  |  | All other affected customers | 2025-01-24 04:04
|  |  | All other affected customers | 2025-01-24 04:08
|  |  | All other affected customers | 2025-01-24 04:11
|  |  | All other affected customers | 2025-01-24 04:19
|  |  | All other affected customers | 2025-01-24 04:26
|  |  | All other affected customers | 2025-01-24 04:30
|  |  | All other affected customers | 2025-01-24 04:41
|  |  | All other affected customers | 2025-01-24 04:45
|  |  | All other affected customers | 2025-01-24 04:49
|  |  | All other affected customers | 2025-01-24 05:31
|  |  | All other affected customers | 2025-01-24 05:36
|  |  | All other affected customers | 2025-01-24 05:37
|  |  | All other affected customers | 2025-01-24 05:38
|  |  | All other affected customers | 2025-01-24 05:47
|  |  | All other affected customers | 2025-01-24 05:52
|  |  | All other affected customers | 2025-01-24 05:53
|  |  | All other affected customers | 2025-01-24 06:01
|  |  | All other affected customers | 2025-01-24 06:10
|  |  | All other affected customers | 2025-01-24 06:15
|  |  | All other affected customers | 2025-01-24 06:19
|  |  | All other affected customers | 2025-01-24 06:27
|  |  | All other affected customers | 2025-01-24 06:45
|  |  | All other affected customers | 2025-01-24 08:31
|  |  | All other affected customers | 2025-01-24 08:42
|  |  | All other affected customers | 2025-01-24 08:45
|  |  | All other affected customers | 2025-01-24 09:09
|  |  | All other affected customers | 2025-01-24 09:29
|  |  | All other affected customers | 2025-01-24 09:33
|  |  | All other affected customers | 2025-01-24 09:43
|  |  | All other affected customers | 2025-01-24 09:45
|  |  | All other affected customers | 2025-01-24 09:48
|  |  | All other affected customers | 2025-01-24 09:49
|  |  | All other affected customers | 2025-01-24 09:51
|  |  | All other affected customers | 2025-01-24 09:56
|  |  | All other affected customers | 2025-01-24 10:01
|  |  | All other affected customers | 2025-01-24 10:02
|  |  | All other affected customers | 2025-01-24 10:13
|  |  | All other affected customers | 2025-01-24 10:16
|  |  | All other affected customers | 2025-01-24 10:26
|  |  | All other affected customers | 2025-01-24 10:32
|  |  | All other affected customers | 2025-01-24 10:39
|  |  | All other affected customers | 2025-01-24 10:42
|  |  | All other affected customers | 2025-01-24 10:47
|  |  | All other affected customers | 2025-01-24 11:02
|  |  | All other affected customers | 2025-01-24 11:23
|  |  | All other affected customers | 2025-01-24 11:27
|  |  | All other affected customers | 2025-01-24 11:52
|  |  | All other affected customers | 2025-01-24 12:18
|  |  | All other affected customers | 2025-01-24 12:30
|  |  | All other affected customers | 2025-01-24 12:40
|  |  | All other affected customers | 2025-01-24 12:57
|  |  | All other affected customers | 2025-01-24 13:05
|  |  | All other affected customers | 2025-01-24 13:30
|  |  | All other affected customers | 2025-01-24 13:33
|  |  | All other affected customers | 2025-01-24 13:43
|  |  | All other affected customers | 2025-01-24 13:50
|  |  | All other affected customers | 2025-01-24 14:17
|  |  | All other affected customers | 2025-01-24 14:21
|  |  | All other affected customers | 2025-01-24 14:54
|  |  | All other affected customers | 2025-01-24 15:09
|  |  | All other affected customers | 2025-01-24 15:30
|  |  | All other affected customers | 2025-01-24 15:34
|  |  | All other affected customers | 2025-01-24 16:16
|  |  | All other affected customers | 2025-01-24 16:58
|  |  | All other affected customers | 2025-01-24 17:17
|  |  | All other affected customers | 2025-01-24 18:21
|  |  | All other affected customers | 2025-01-24 22:35
|  |  | All other affected customers | 2025-01-24 22:36
|  |  | All other affected customers | 2025-01-24 22:42
|  |  | All other affected customers | 2025-01-24 23:09
|  |  | All other affected customers | 2025-01-24 23:10
|  |  | All other affected customers | 2025-01-24 23:26
|  |  | All other affected customers | 2025-01-24 23:50
|  |  | All other affected customers | 2025-01-25 00:24
|  |  | All other affected customers | 2025-01-25 01:10
|  |  | All other affected customers | 2025-01-25 01:18
|  |  | All other affected customers | 2025-01-25 01:52
|  |  | All other affected customers | 2025-01-25 01:53
|  |  | All other affected customers | 2025-01-25 09:26
|  |  | All other affected customers | 2025-01-25 09:55
|  |  | All other affected customers | 2025-01-25 15:07
|  |  | All other affected customers | 2025-01-25 15:35
|  |  | All other affected customers | 2025-01-25 15:57
|  |  | All other affected customers | 2025-01-25 16:24
|  |  | All other affected customers | 2025-01-25 16:27
|  |  | All other affected customers | 2025-01-25 16:48
|  |  | All other affected customers | 2025-01-25 17:20
|  |  | All other affected customers | 2025-01-25 17:32
|  |  | All other affected customers | 2025-01-25 17:38
|  |  | All other affected customers | 2025-01-25 17:56
|  |  | All other affected customers | 2025-01-25 18:40
|  |  | All other affected customers | 2025-01-25 19:34
|  |  | All other affected customers | 2025-01-26 10:12
|  |  | All other affected customers | 2025-01-26 10:18
|  |  | All other affected customers | 2025-01-26 14:04
|  |  | All other affected customers | 2025-01-26 14:33
|  |  | All other affected customers | 2025-01-26 15:05
|  |  | All other affected customers | 2025-01-26 15:41
|  |  | All other affected customers | 2025-01-26 18:07
|  |  | All other affected customers | 2025-01-26 18:46
|  |  | All other affected customers | 2025-01-27 15:09
| Event Concluded (Cancellation) | All Clear | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-20 04:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-18 14:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-19 14:02
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 06:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 08:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:48
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 14:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:15
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 16:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:03
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:29
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:38
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:41
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 17:58
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 18:07
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 19:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 20:45
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-21 22:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 01:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 02:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:09
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:31
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 03:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:01
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:17
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 04:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-22 17:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 02:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 16:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:50
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:52
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 17:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 18:06
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:32
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:37
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:44
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 21:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:30
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 22:35
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-23 23:49
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 00:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 00:59
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:08
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:12
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 01:14
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:05
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 02:27
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:28
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:39
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:40
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:53
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 05:55
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 08:54
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 08:56
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 08:57
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-24 15:11
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 04:04
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 14:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 14:51
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:00
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:13
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:16
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:19
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:20
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:21
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:22
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:23
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:25
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:34
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 15:36
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 16:26
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-25 17:24
|  |  | Public Safety Partners excluding Critical Facilities and Infrastructure | 2025-01-27 15:44
|  |  | Critical Facilities & Infrastructure | 2025-01-18 14:00
|  |  | Critical Facilities & Infrastructure | 2025-01-18 14:01
|  |  | Critical Facilities & Infrastructure | 2025-01-19 13:31
|  |  | Critical Facilities & Infrastructure | 2025-01-20 04:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 08:27
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:02
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:15
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 14:42
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:03
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:10
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:16
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:19
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:22
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:25
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:35
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:38
|  |  | Critical Facilities & Infrastructure | 2025-01-21 16:40
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:29
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:38
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:41
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:43
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:46
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:48
|  |  | Critical Facilities & Infrastructure | 2025-01-21 17:55
|  |  | Critical Facilities & Infrastructure | 2025-01-21 18:01
|  |  | Critical Facilities & Infrastructure | 2025-01-21 19:58
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:17
|  |  | Critical Facilities & Infrastructure | 2025-01-21 22:23
|  |  | Critical Facilities & Infrastructure | 2025-01-22 01:49
|  |  | Critical Facilities & Infrastructure | 2025-01-22 02:23
|  |  | Critical Facilities & Infrastructure | 2025-01-22 02:26
|  |  | Critical Facilities & Infrastructure | 2025-01-22 02:33
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:07
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:15
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:32
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:34
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:35
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:36
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:41
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:45
|  |  | Critical Facilities & Infrastructure | 2025-01-22 03:57
|  |  | Critical Facilities & Infrastructure | 2025-01-22 04:58
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:03
|  |  | Critical Facilities & Infrastructure | 2025-01-22 05:41
|  |  | Critical Facilities & Infrastructure | 2025-01-22 17:37
|  |  | Critical Facilities & Infrastructure | 2025-01-22 20:53
|  |  | Critical Facilities & Infrastructure | 2025-01-22 22:55
|  |  | Critical Facilities & Infrastructure | 2025-01-22 22:58
|  |  | Critical Facilities & Infrastructure | 2025-01-23 02:11
|  |  | Critical Facilities & Infrastructure | 2025-01-23 08:05
|  |  | Critical Facilities & Infrastructure | 2025-01-23 15:40
|  |  | Critical Facilities & Infrastructure | 2025-01-23 15:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 17:55
|  |  | Critical Facilities & Infrastructure | 2025-01-23 18:17
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:42
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:47
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:48
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:50
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:56
|  |  | Critical Facilities & Infrastructure | 2025-01-23 21:58
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:00
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:02
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:04
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:07
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:10
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:13
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:16
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:21
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:24
|  |  | Critical Facilities & Infrastructure | 2025-01-23 22:26
|  |  | Critical Facilities & Infrastructure | 2025-01-23 23:44
|  |  | Critical Facilities & Infrastructure | 2025-01-24 00:48
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:06
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:14
|  |  | Critical Facilities & Infrastructure | 2025-01-24 01:20
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:36
|  |  | Critical Facilities & Infrastructure | 2025-01-24 02:39
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:34
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:39
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:41
|  |  | Critical Facilities & Infrastructure | 2025-01-24 05:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 08:44
|  |  | Critical Facilities & Infrastructure | 2025-01-24 08:45
|  |  | Critical Facilities & Infrastructure | 2025-01-24 12:40
|  |  | Critical Facilities & Infrastructure | 2025-01-24 13:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 15:30
|  |  | Critical Facilities & Infrastructure | 2025-01-24 16:16
|  |  | Critical Facilities & Infrastructure | 2025-01-24 16:26
|  |  | Critical Facilities & Infrastructure | 2025-01-24 20:04
|  |  | Critical Facilities & Infrastructure | 2025-01-24 20:50
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:08
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:18
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:28
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:35
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:36
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:50
|  |  | Critical Facilities & Infrastructure | 2025-01-24 22:57
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:10
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:26
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:40
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:43
|  |  | Critical Facilities & Infrastructure | 2025-01-24 23:59
|  |  | Critical Facilities & Infrastructure | 2025-01-25 00:54
|  |  | Critical Facilities & Infrastructure | 2025-01-25 01:01
|  |  | Critical Facilities & Infrastructure | 2025-01-25 12:55
|  |  | Critical Facilities & Infrastructure | 2025-01-25 14:32
|  |  | Critical Facilities & Infrastructure | 2025-01-25 14:43
|  |  | Critical Facilities & Infrastructure | 2025-01-25 14:58
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:04
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:10
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:12
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:35
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:37
|  |  | Critical Facilities & Infrastructure | 2025-01-25 15:50
|  |  | Critical Facilities & Infrastructure | 2025-01-25 16:33
|  |  | Critical Facilities & Infrastructure | 2025-01-25 16:39
|  |  | Critical Facilities & Infrastructure | 2025-01-25 17:32
|  |  | Critical Facilities & Infrastructure | 2025-01-25 20:11
|  |  | Critical Facilities & Infrastructure | 2025-01-25 20:24
|  |  | Critical Facilities & Infrastructure | 2025-01-26 07:48
|  |  | All other affected customers | 2025-01-18 14:00
|  |  | All other affected customers | 2025-01-18 14:01
|  |  | All other affected customers | 2025-01-19 13:31
|  |  | All other affected customers | 2025-01-20 04:42
|  |  | All other affected customers | 2025-01-21 08:27
|  |  | All other affected customers | 2025-01-21 14:02
|  |  | All other affected customers | 2025-01-21 14:15
|  |  | All other affected customers | 2025-01-21 14:25
|  |  | All other affected customers | 2025-01-21 14:42
|  |  | All other affected customers | 2025-01-21 16:03
|  |  | All other affected customers | 2025-01-21 16:10
|  |  | All other affected customers | 2025-01-21 16:16
|  |  | All other affected customers | 2025-01-21 16:19
|  |  | All other affected customers | 2025-01-21 16:22
|  |  | All other affected customers | 2025-01-21 16:25
|  |  | All other affected customers | 2025-01-21 16:35
|  |  | All other affected customers | 2025-01-21 16:38
|  |  | All other affected customers | 2025-01-21 16:40
|  |  | All other affected customers | 2025-01-21 17:29
|  |  | All other affected customers | 2025-01-21 17:33
|  |  | All other affected customers | 2025-01-21 17:38
|  |  | All other affected customers | 2025-01-21 17:41
|  |  | All other affected customers | 2025-01-21 17:43
|  |  | All other affected customers | 2025-01-21 17:46
|  |  | All other affected customers | 2025-01-21 17:48
|  |  | All other affected customers | 2025-01-21 17:55
|  |  | All other affected customers | 2025-01-21 18:01
|  |  | All other affected customers | 2025-01-21 19:58
|  |  | All other affected customers | 2025-01-21 22:17
|  |  | All other affected customers | 2025-01-21 22:23
|  |  | All other affected customers | 2025-01-22 01:49
|  |  | All other affected customers | 2025-01-22 02:23
|  |  | All other affected customers | 2025-01-22 02:26
|  |  | All other affected customers | 2025-01-22 02:33
|  |  | All other affected customers | 2025-01-22 03:07
|  |  | All other affected customers | 2025-01-22 03:15
|  |  | All other affected customers | 2025-01-22 03:32
|  |  | All other affected customers | 2025-01-22 03:34
|  |  | All other affected customers | 2025-01-22 03:35
|  |  | All other affected customers | 2025-01-22 03:36
|  |  | All other affected customers | 2025-01-22 03:41
|  |  | All other affected customers | 2025-01-22 03:45
|  |  | All other affected customers | 2025-01-22 03:57
|  |  | All other affected customers | 2025-01-22 04:58
|  |  | All other affected customers | 2025-01-22 05:03
|  |  | All other affected customers | 2025-01-22 05:41
|  |  | All other affected customers | 2025-01-22 17:37
|  |  | All other affected customers | 2025-01-22 20:53
|  |  | All other affected customers | 2025-01-22 22:55
|  |  | All other affected customers | 2025-01-22 22:58
|  |  | All other affected customers | 2025-01-23 02:11
|  |  | All other affected customers | 2025-01-23 08:05
|  |  | All other affected customers | 2025-01-23 15:40
|  |  | All other affected customers | 2025-01-23 15:42
|  |  | All other affected customers | 2025-01-23 17:55
|  |  | All other affected customers | 2025-01-23 18:17
|  |  | All other affected customers | 2025-01-23 21:42
|  |  | All other affected customers | 2025-01-23 21:47
|  |  | All other affected customers | 2025-01-23 21:48
|  |  | All other affected customers | 2025-01-23 21:50
|  |  | All other affected customers | 2025-01-23 21:56
|  |  | All other affected customers | 2025-01-23 21:58
|  |  | All other affected customers | 2025-01-23 22:00
|  |  | All other affected customers | 2025-01-23 22:02
|  |  | All other affected customers | 2025-01-23 22:04
|  |  | All other affected customers | 2025-01-23 22:07
|  |  | All other affected customers | 2025-01-23 22:10
|  |  | All other affected customers | 2025-01-23 22:13
|  |  | All other affected customers | 2025-01-23 22:16
|  |  | All other affected customers | 2025-01-23 22:21
|  |  | All other affected customers | 2025-01-23 22:24
|  |  | All other affected customers | 2025-01-23 22:26
|  |  | All other affected customers | 2025-01-23 23:44
|  |  | All other affected customers | 2025-01-24 00:48
|  |  | All other affected customers | 2025-01-24 01:06
|  |  | All other affected customers | 2025-01-24 01:14
|  |  | All other affected customers | 2025-01-24 01:20
|  |  | All other affected customers | 2025-01-24 02:36
|  |  | All other affected customers | 2025-01-24 02:39
|  |  | All other affected customers | 2025-01-24 05:34
|  |  | All other affected customers | 2025-01-24 05:39
|  |  | All other affected customers | 2025-01-24 05:41
|  |  | All other affected customers | 2025-01-24 05:45
|  |  | All other affected customers | 2025-01-24 08:44
|  |  | All other affected customers | 2025-01-24 08:45
|  |  | All other affected customers | 2025-01-24 12:40
|  |  | All other affected customers | 2025-01-24 13:30
|  |  | All other affected customers | 2025-01-24 16:16
|  |  | All other affected customers | 2025-01-24 20:04
|  |  | All other affected customers | 2025-01-24 20:50
|  |  | All other affected customers | 2025-01-24 22:08
|  |  | All other affected customers | 2025-01-24 22:18
|  |  | All other affected customers | 2025-01-24 22:28
|  |  | All other affected customers | 2025-01-24 22:35
|  |  | All other affected customers | 2025-01-24 22:36
|  |  | All other affected customers | 2025-01-24 22:50
|  |  | All other affected customers | 2025-01-24 22:57
|  |  | All other affected customers | 2025-01-24 23:10
|  |  | All other affected customers | 2025-01-24 23:26
|  |  | All other affected customers | 2025-01-24 23:40
|  |  | All other affected customers | 2025-01-24 23:43
|  |  | All other affected customers | 2025-01-24 23:59
|  |  | All other affected customers | 2025-01-25 00:54
|  |  | All other affected customers | 2025-01-25 01:01
|  |  | All other affected customers | 2025-01-25 12:55
|  |  | All other affected customers | 2025-01-25 14:32
|  |  | All other affected customers | 2025-01-25 14:43
|  |  | All other affected customers | 2025-01-25 14:58
|  |  | All other affected customers | 2025-01-25 15:04
|  |  | All other affected customers | 2025-01-25 15:10
|  |  | All other affected customers | 2025-01-25 15:12
|  |  | All other affected customers | 2025-01-25 15:35
|  |  | All other affected customers | 2025-01-25 15:37
|  |  | All other affected customers | 2025-01-25 15:50
|  |  | All other affected customers | 2025-01-25 16:33
|  |  | All other affected customers | 2025-01-25 16:39
|  |  | All other affected customers | 2025-01-25 17:32
|  |  | All other affected customers | 2025-01-25 20:11
|  |  | All other affected customers | 2025-01-25 20:24
|  |  | All other affected customers | 2025-01-26 07:48
Notification Timeline (SDG&E Shared Customers)
Event Order | Notification Type | Requirement Timeline | Notification Sent To | Approximate Time Sent | Notes
Pre-De-Energization (prior) | Initial Notice for PSPS Event (Advanced Initial or Initial) | 72-48 hours | N/A | N/A | N/A
| Initial Notice for PSPS Event (Initial or Update) | 48-24 hours | All affected customers | 01.23.25 at 0209 | Condor
| Imminent De-Energize (Expected) | 4-1 hour | All affected customers | 01.23.25 at 0738 | Condor
In-Event (during) | De-Energized (Shutoff) | De-energization | All affected customers
Restoration (after) | Imminent Re-Energize (Prepare to Restore) | Imminent Re-energization | All affected customers
| Re-Energized (Restored In Scope and/or Restored No Longer in Scope) | Re-energization | All affected customers
| Event Concluded (Cancellation) | All Clear | N/A | 01.23.25 at 1957 | Condor
Notification Timeline (SDG&E Shared Customers)
Event Order | Notification Type | Requirement Timeline | Notification Sent To | Approximate Time Sent | Notes
Pre-De-Energization (prior) | Initial Notice for PSPS Event (Advanced Initial or Initial) | 72-48 hours | N/A | N/A | N/A
| Initial Notice for PSPS Event (Initial or Update) | 48-24 hours | All affected customers | 01.23.25 at 0216 01.22.25 at 1748 (Initial) 01.23.25 at 0547 (Update) | Pascal Chawa Chawa
| Imminent De-Energize (Expected) | 4-1 hour | All affected customers | 01.23.25 at 0834 | Pascal
In-Event (during) | De-Energized (Shutoff) | De-energization | All affected customers | 91.23.25 at 1034 | Chawa
Restoration (after) | Imminent Re-Energize (Prepare to Restore) | Imminent Re-energization | All affected customers | 01.24.25 at 0109 | Chawa
| Re-Energized (Restored In Scope and/or Restored No Longer in Scope) | Re-energization | All affected customers | 01.24.25 at 1503 | Chawa
| Event Concluded (Cancellation) | All Clear | N/A | N/A | N/A

## T09
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 05: Notifications
Breakdown of Notification Failures
Notifications sent to | Notification Failure Description | Number of Entities or Customer Counts | Explanation
Public Safety Partners excluding Critical Facilities and Infrastructure | Entities who did not receive 48-to 72-hour advance notification. | 17 | campaign authorized less than 48 hours, successfully sent - 5 missing authorized campaign/message sent error - 12
| Entities who did not receive 1–4-hour imminent notification. | 12 | missing authorized campaign - 12
| Entities who did not receive any notifications before de-energization. | 12 | missing authorized campaign/message sent error - 12
| Entities who were not notified immediately before re-energization. | 12 | missing authorized campaign/message sent error - 12
| Entities who did not receive cancellation notification within two hours of the decision to cancel. | 0 | N/A
Critical Facilities and Infrastructure | Facilities who did not receive 48–72-hour advance notification. | 1094 | campaign authorized less than 48 hours, successfully sent - 480 no contact information / message send error - 1 missing authorized campaign - 613
| Facilities who did not receive 1-4 hour of imminent notifications. | 271 | missing authorized campaign - 270 no contact information / message send error - 1
| Facilities who did not receive any notifications before de-energization. | 102 | missing authorized campaign - 100 no contact information / message send error - 2
| Facilities who were not notified at de-energization initiation. | 23 | missing authorized campaign - 21 no contact information / message send error - 2
| Facilities who were not notified immediately before re- energization. | 113 | missing authorized campaign - 57 no contact information / message send error - 2 campaign authorized after re-energization - 54
| Facilities who were not notified when re-energization is complete. | 27 | missing authorized campaign - 25 no contact information / message send error - 2
| Facilities who did not receive cancellation notification within two hours of the decision to cancel. | 62 | received deen notifications, was not deen, missing authorized campaign - 61 missing authorized campaign - 1
All other affected customers | Customers who did not receive 24–48-hour advance notifications. | 40919 | campaign authorized less than 24 hours, successfully sent - 5,941 missing authorized campaign - 34,536 no contact information / message send error - 442
| Customers who did not receive 1–4-hour imminent notifications. | 13032 | no contact information / message send error - 360 missing authorized campaign - 12,672
| Customers who did not receive any notifications before de-energization. | 4804 | missing authorized campaign - 4,235 no contact information / message send error - 569
| Customers who were not notified at de-energization initiation. | 1837 | missing authorized campaign - 1,223 no contact information / message send error - 614
| Customers who were not notified immediately before re-energization. | 7931 | campaign authorized after re-energization - 3,305 missing authorized campaign - 4,048 no contact information / message send error - 578
| Customers who were not notified when re-energization is complete. | 1878 | no contact information / message send error - 560 missing authorized campaign - 1,318
| Customers who did not receive cancellation notification within two hours of the decision to cancel. | 6231 | missing authorized campaign - 36 received deen notifications, was not deen, missing authorized campaign - 6,017 no contact information / message send error - 178

## T10
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 06: Local and State Public Safety Partner Engagement
Public Safety Partners Contacted
Jurisdiction / Organization | Title | HFTD Tier | Date/Time Contacted
Agoura Hills | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Agoura Hills | City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Agoura Hills | Communications Manager/PIO | Non HFRA, T3, T2 | 2025-01-19 14:02
Agoura Hills | Councilmember | Non HFRA, T3, T2 | 2025-01-19 14:02
Agoura Hills | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Agoura Hills | Management Analyst | Non HFRA, T3, T2 | 2025-01-19 14:02
Agoura Hills | Public Works Project Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Aliso Viejo | City Manager | Non HFRA, T3, T2 | 2025-01-23 17:48
Aliso Viejo | Director of Public Works | Non HFRA, T3, T2 | 2025-01-23 17:48
Aliso Viejo | Sr. Emergency Management Program Coordinator | Non HFRA, T3, T2 | 2025-01-23 17:48
Avalon | City Manager | Non HFRA, T3, T2 | 2025-01-20 16:40
Avalon | Councilmember | Non HFRA, T3, T2 | 2025-01-20 16:40
Avalon | Emergency Contact | Non HFRA, T3, T2 | 2025-01-20 16:40
Avalon | Fire Chief | Non HFRA, T3, T2 | 2025-01-20 16:40
Avalon | Maintenance Superintendent | Non HFRA, T3, T2 | 2025-01-20 16:40
Avalon | Mayor | Non HFRA, T3, T2 | 2025-01-20 16:40
Avalon | Public Works Director | Non HFRA, T3, T2 | 2025-01-20 16:40
Azusa | Assistant Director of Utilities - Electric Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
Azusa | Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
Azusa | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Azusa | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Azusa |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Chief Plant Operator | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Community Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Council Member | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Management Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Police Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Beaumont | Public Information Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Brea | Acting Building Official | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Administrative Clerk II | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Assistant City Engineer | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Building Supervisor | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | City Clerk | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | City Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Communications & Marketing Manager/PIO | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Community Development Director | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Community Development Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Councilmember | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Deputy Fire Chief (Acting) | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Director of Public Works / City Engineer | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Emergency Preparedness Coordinator | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Environmental Services Coordinator | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Executive Assistant | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | IT Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | IT Supervisor | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Maintenance Services Crew Leader | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Mayor | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Parks & Landscape Supervisor | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Police Captain | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Police Chief | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Street, Sewer Storm Drain & Sanitation Division Supervisor | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Superintendent | Non HFRA, T3, T2 | 2025-01-20 00:02
Brea | Water Division Supervisor | Non HFRA, T3, T2 | 2025-01-20 00:02
Calabasas | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Assistant Director of Public Safety and Emergency Preparedness | Non HFRA, T3, T2 | 2025-01-27 15:44
Calabasas | City Clerk | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Councilmember | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Emergency Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Mayor | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Ms. | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | N/a | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Public Works Inspector | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Sheriff Watch Commander | Non HFRA, T3, T2 | 2025-01-18 14:32
Calabasas | Station Captain | Non HFRA, T3, T2 | 2025-01-18 14:32
Calimesa | Associate Engineer | Non HFRA, T3, T2 | 2025-01-19 14:02
Calimesa | City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Calimesa | Executive Assistant/Deputy City Clerk | Non HFRA, T3, T2 | 2025-01-19 14:02
Calimesa | Fire Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Calimesa | Maintenance Superintendent | Non HFRA, T3, T2 | 2025-01-19 14:02
Calimesa | Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Administrative Specialist | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Community Relations Officer | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Councilmember | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Director of Administrative Services | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Executive Assistant | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Finance Director | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Mayor | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Mr. | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Ms. | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Police Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Public Works Director | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Undersheriff | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Utilities Operations Supervisor | Non HFRA, T3, T2 | 2025-01-19 14:02
Camarillo | Vice Mayor | Non HFRA, T3, T2 | 2025-01-19 14:02
Canyon Lake | Adminstrative Services Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Canyon Lake | Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Chino | Chino PD Dispatch Center | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Communications Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Deputy Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino | Water Utilities Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Capital Project and Support Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Community Development Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Community Relations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Community Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Engineering Manager-DPW | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Fire Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Chino Hills | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Public Information Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Public Works / Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Public Works Director/City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Public Works/Utilities Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
Chino Hills | Vice Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Clean Power Alliance | CCA Primary Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Community Services Director/PIO | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Development Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Electric Utility Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Human Resources Director/Risk Management Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Senior Energy Services Specialist | Non HFRA, T3, T2 | 2025-01-17 19:52
Colton | Substation Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Corona | Assistant Director of Utilities | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Assistant Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Corona | Business Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Chief Distribution Operator | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Chief Reclamations Operator | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Chief Water Operator | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Corona | City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | City Traffic Engineer | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Construction Superintendent | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Councilmember | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Deputy Chief Operator - Water | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Director of Utilities | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Emergency Contact | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Finance Director | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Fire Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Maintenance Planner | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Management Analyst | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Mayor | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Police Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Public Information Officer | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Public Works Director | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona | Traffic Signal Coordinator | Non HFRA, T3, T2 | 2025-01-19 14:02
Corona |  | Non HFRA, T3, T2 | 2025-01-19 14:02
Covina | Asst. City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Covina | Asst. Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Covina | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Covina | Community Development Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Covina | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Covina | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Covina | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Desert Community Energy | CCA Contact | Non HFRA, T3, T2 | 2025-01-20 19:21
Desert Community Energy | CCA Primary Contact | Non HFRA, T3, T2 | 2025-01-20 19:21
Desert Community Energy | Management Analyst | Non HFRA, T3, T2 | 2025-01-20 19:21
Desert Community Energy | Program Specialist | Non HFRA, T3, T2 | 2025-01-20 19:21
Desert Hot Springs | Assistant City Manager/City Engineer | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | City Clerk | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | City Manager | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Communications Manager | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Councilmember | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Deputy Police Chief | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Emergency Contact | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Fire Chief | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Mayor | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Police Chief | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Public Works Director | Non HFRA, T3, T2 | 2025-01-21 16:10
Desert Hot Springs | Recreation and Community Services Director | Non HFRA, T3, T2 | 2025-01-21 16:10
Diamond Bar | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Associate Engineer | Non HFRA, T3, T2 | 2025-01-23 15:12
Diamond Bar | City Clerk | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | City Manager | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Councilmember | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Director, Information Systems | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Mayor | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Public Information Manager | Non HFRA, T3, T2 | 2025-01-20 19:41
Diamond Bar | Public Works Director | Non HFRA, T3, T2 | 2025-01-20 19:41
Eastvale | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Eastvale | Battalion Chief/CalFire | Non HFRA, T3, T2 | 2025-01-20 00:02
Eastvale | Deputy Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Energy for Palmdale's Independent Choice | Innovation and Environmental Manage | Non HFRA, T3, T2 | 2025-01-25 13:05
Energy for Palmdale's Independent Choice | Sr. Management Analyst | Non HFRA, T3, T2 | 2025-01-25 13:05
Fillmore | Deputy City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Fillmore | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Fillmore | Interim City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Fontana | Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
Fontana | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Fontana | Deputy City Manager, Administrative Services | Non HFRA, T3, T2 | 2025-01-17 19:52
Fontana | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Fontana | Emergency Services Coodinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Glendale | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Glendora | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Glendora | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Glendora | SCE Notifications | Non HFRA, T3, T2 | 2025-01-17 19:52
Glendora | Watch Commander | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Grand Terrace | Planning Dir | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | Economic Development Manager | Non HFRA, T3, T2 | 2025-01-21 14:00
Hemet | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | IT Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Hemet | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Hesperia | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Hesperia | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Hesperia | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Hesperia |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Administrative Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Assistant Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Assistant Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Battalion Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Community Development Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Lieutenant | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Mayor Pro tempore | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Public Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Public Work Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Highland | Public Works Director/City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Industry | Acting Assistant Fire Chief | Non HFRA, T3, T2 | 2025-01-20 19:41
Industry | Assistant City Mgr/Public Affairs Mgr | Non HFRA, T3, T2 | 2025-01-20 19:41
Industry | Asst. City Mgr. | Non HFRA, T3, T2 | 2025-01-20 19:41
Industry | Battalion Chief | Non HFRA, T3, T2 | 2025-01-20 19:41
Industry | Captain | Non HFRA, T3, T2 | 2025-01-20 19:41
Industry | City Manager | Non HFRA, T3, T2 | 2025-01-20 19:41
Industry | Mayor | Non HFRA, T3, T2 | 2025-01-20 19:41
Irvine | Assistant Chief of Police | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Assistant City Engineer | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Chief of Staff to Mayor Khan | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | City Clerk | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | City Engineer | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Commander - Patrol Division | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Commander - Special Operations Division | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Councilmember | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Deputy Director of Community Development/ Building Official | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Director of Community Development | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Director, Communications & Engagement | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Emergency Contact | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Executive Manager - Admin Services Division | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Irvine Unified School District Director of Risk Management | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | IUSD Superintendent | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | IVC President | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Manager, Emergency Services | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Mayor | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Parks & Open Space Administrator | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Police Chief | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Public Works Administrator | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Senior Management Analyst | Non HFRA, T3, T2 | 2025-01-23 06:01
Irvine | Vice Mayor | Non HFRA, T3, T2 | 2025-01-23 06:01
Irwindale | Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Irwindale | City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Irwindale | Public Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Irwindale | Strobehn@IrwindaleCA.gov | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Marketing and Communications Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Jurupa Valley | Public Works Director/City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Assistant Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Chair | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Deputy Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Deputy Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Duty Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Fire Chief & Director of Emergency Services | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Interim Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Planning Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | PSPS Notification | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Sheriff | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Kern County | Undersheriff | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Asst. Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Director of Administrative Services | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Interim Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Mayor pro tem | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Public Safety Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
La Canada Flintridge | Senior Management Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
La Habra | Assistant Fire Chief | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Building Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Captain | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | City Manager | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Community Srvc Liaison | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Councilmember | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Director of Community & Economic Development | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Dispatch Supervisor | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Finance Manager | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Influential/Opinion Leader | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Police Chief | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Police Watch Commander Duty | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Public Works Director | Non HFRA, T3, T2 | 2025-01-23 17:48
La Habra | Sergeant | Non HFRA, T3, T2 | 2025-01-23 17:48
La Verne | Battalion Chief | Non HFRA, T3, T2 | 2025-01-21 06:46
La Verne | City Manager | Non HFRA, T3, T2 | 2025-01-21 06:46
La Verne | Councilmember | Non HFRA, T3, T2 | 2025-01-21 06:46
La Verne | Fire Chief | Non HFRA, T3, T2 | 2025-01-21 06:46
La Verne | Fire Engineer | Non HFRA, T3, T2 | 2025-01-21 06:46
La Verne | Mayor | Non HFRA, T3, T2 | 2025-01-21 06:46
La Verne | Mayor pro tem | Non HFRA, T3, T2 | 2025-01-21 06:46
Laguna Beach | 24 hour Police Watch Commander | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | 24 hr Public Safety Dispatch | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Battalian Chief On Duty | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Building Official | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Chief of Police | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | City Clerk | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | City Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Council Member | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Deputy City Engineer | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Deputy Director - Public Works | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Deputy Director - Wastewater Division | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Deputy Fire Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Director of Community Development | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Director of Finance | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Director of Transit and Community Services | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Emergency Operations Coordinator | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Executive Assistant | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Fire Chief | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Marine Safety Captain | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Project Director | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Public Safety Dispatch | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Public Works Director | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Public Works Technician | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Support Services Supervisor | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Beach | Undergrounding Project Manager | Non HFRA, T3, T2 | 2025-01-19 14:02
Laguna Niguel | Sr. Emergency Management Coordinator | Non HFRA, T3, T2 | 2025-01-19 14:02
Lake Elsinore | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Community Support Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Economic Development Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Emergency Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Public Works Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Elsinore | Public Works Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Chief Lake Forest Police Services | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Chief of Lake Forest Police Services | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Community Services Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Contract Public Works Inspector | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Council Member | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Director of Community Development | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Director of Public Works | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Public Works Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Senior Communications and Marketing Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Senior Management Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Lake Forest | Traffic Engineer Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Lancaster | Coordinator III | Non HFRA, T3, T2 | 2025-01-22 20:36
Lancaster | Emergency Manager | Non HFRA, T3, T2 | 2025-01-22 20:36
Lancaster | Utility Services Manager | Non HFRA, T3, T2 | 2025-01-22 20:36
Lancaster Energy | CCA Additional Contact | Non HFRA, T3, T2 | 2025-01-18 14:32
Lancaster Energy | CCA Primary Contact | Non HFRA, T3, T2 | 2025-01-18 14:32
Lancaster Energy | CCA Secondary Contact | Non HFRA, T3, T2 | 2025-01-18 14:32
Lancaster Energy | CCA Tertiary Contact | Non HFRA, T3, T2 | 2025-01-18 14:32
Lancaster Energy |  | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | Battalion Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | City Clerk | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | Councilmember | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | Emergency Contact | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | Fire Marshal | Non HFRA, T3, T2 | 2025-01-18 14:32
Loma Linda | Mayor | Non HFRA, T3, T2 | 2025-01-18 14:32
Los Angeles County | Asst. Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Cheif of Staff for Supervisor Barger | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Chief of Community and Marketing Services Division | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Deputy | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Deputy Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Director, Office of Emergency Management | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disabilities, Access and Functional Needs Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Area Coordinator, Area B | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Area Coordinator, Area C | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Area Coordinator, Area D | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Area Coordinator, Area G | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Management Area Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Management Area Coordinator, Area E | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Disaster Services Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Division Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Duty Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Emergency Prepardness Offcer | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Emergency Services.. Coordinator, Area A | Non HFRA, T3, T2 | 2025-01-18 14:32
Los Angeles County | Field Deputy | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Fire Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Office of OEM/EOC | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Planning Deputy | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Senior Civil Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County | Senior Deputy, Supervisor Kathryn Barger | Non HFRA, T3, T2 | 2025-01-17 19:52
Los Angeles County |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Malibu | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Assistant Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Caltrans | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Captain | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | CERT Team Leader | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | CHP - Task Force | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | CHP - West Valley Captian | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Community Services Liaison | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Councilmember | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Emergency Contact | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Executive Assistant | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Fire Safety Liaison | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Media Information Officer | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Public Safety Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Public Safety Liaison | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Public Works Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Public Works Super | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Publisher | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Senior Public Works Inspector/Superintendent | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | Thousand Oaks District Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Malibu | VOP Team Leader | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Associate Planner | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Captain - Menifee Police | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Chief Information Officer | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | City Clerk | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Community Development Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Councilmember | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Emergency Management Analyst | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Fire Marshal | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Fire Systems Inspector | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Management Analyst | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Parks/Landscape Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Police Captain | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Public Information Officer | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Public Works Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Menifee | Sr. Civil Engineer | Non HFRA, T3, T2 | 2025-01-18 14:32
Mission Viejo | Assistant City Manager/ Director of Public Services | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Council Member, District 2 | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Council Member, District 5 | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Director of Community Relations | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Director Of Public Works | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Emergency Operations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Executive Administrator for CM and City Council | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Maintenance Operations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Mission Viejo | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Division Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Information Systems Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | MUSD Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Parks and Recreation Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Moorpark | Sheriff's Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Assistant City Manager - Development | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Council Member | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Electric Utilities Division Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Emergency Operations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Lietuenant | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Maintenance & Operations Division Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Media Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Moreno Valley |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Assistant CEO | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Chairman | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Chief Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Deputy Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Emergency Management | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Executive Administrative Assistant | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Realty Administrator | Non HFRA, T3, T2 | 2025-01-17 19:52
Morongo Band Of Mission Indians | Tribal Vice Chairperson | Non HFRA, T3, T2 | 2025-01-17 19:52
Murrieta | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Captain | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | City Clerk | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Communications Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Deputy Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Director of Public Works/City Engineer | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Disaster Preparedness Coordinator | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Division Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Economic Development - Deputy Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | IT Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Lieutenant | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Parks Superintendent | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Public Information Officer | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Public Works Construction Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta | Senior Civil Engineer | Non HFRA, T3, T2 | 2025-01-18 14:32
Murrieta |  | Non HFRA, T3, T2 | 2025-01-18 14:32
Norco | Animal Control Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | City Manager | Non HFRA, T3, T2 | 2025-01-27 15:44
Norco | Communications Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Director of Community Services | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Director of Facilities and Maintenance | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Director of Planning & Building Safety | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Division Chief Cal Fire | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Facilities and Maintenance Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Interim City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | IT Administrator | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Lieutenant | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Parks & Public Buildings Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Public Works Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Norco | Public Works Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Ojai | City Manager | Non HFRA, T3, T2 | 2025-01-20 16:40
Orange | Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Chief Clerk & Elected City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Chief of Police (efffective 7-4-21) | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Deputy Director/City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Fire Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Police Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange | Supervisor on Duty | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | 24-hr Warning Point | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Acting Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Assistant Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Assistant Emergency Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Assistant Sheriff | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Capital Improvement Programs Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | CEO/Real Estate | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Chief of Staff - Supervisor Sarmiento | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Chief of Staff, Andrew Do | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Chief Real Estate Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Commander - North Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Commander - Southwest Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | County Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Deputy County Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Deputy Director of Emergency Management | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Director of Emergency Management | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Director, Government & Community Relations | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Dispatch | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Division Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Duty Officer (Control One) | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Election Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Emergency Contact-Public Works | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Emergency Notifications | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Facilities Operations Manager - OCPW | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Manager Central Utility Facility | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Operations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Orange County Waste Recycling Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Policy Advisor, Supervisor Doug Chaffee | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Policy Advisor, Supervisor Wagner | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Public Works Manager Equipment Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Public Works Manager General Maintenance | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Public Works PIO | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Secretary to Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Southeast Operations Commander | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Sr Emergency Management Program Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Supervisor, District 1 | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Supervisor, District 3 | Non HFRA, T3, T2 | 2025-01-17 19:52
Orange County | Vice Chairman | Non HFRA, T3, T2 | 2025-01-17 19:52
Palm Springs | Building Official/Director of Building & Safety | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Captain - Palm Springs Fire Department | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Chief Communications Officer | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Chief Deputy City Clerk | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Chief Economic Development Officer | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | City Clerk | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | City Engineer | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | City Manager | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Community Engagement/PS ONE | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Councilmember | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Director of Sustainability | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Emergency Manager | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Executive Assistant - City Manager | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Fire Chief | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Mayor | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Police Chief | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Public Works Director | Non HFRA, T3, T2 | 2025-01-21 16:10
Palm Springs | Senior Cogeneration Technician | Non HFRA, T3, T2 | 2025-01-21 16:10
Palmdale | Emergency Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Community Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Interim Parks and Community Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Lieutenant | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Perris | Public Works Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Council Member | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Deputy Director of Director of Engineering | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Deputy Director of Public Works | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Deputy Director of Utilities-Enviro | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Director of Engineering/City Engineer | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Emergency Management Specialist | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Lieutenant | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Public Information Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Cucamonga | Rancho Cucamonga Fire | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Administrative Sergeant | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Associate Planner | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Battalion Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Council Member | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Development Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Influential/Opinion Leader | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Public Information Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Rancho Santa Margarita | Public Works Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Redlands | Deputy Fire Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Redlands | Emergency Operations Specialist | Non HFRA, T3, T2 | 2025-01-18 14:32
Rialto | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Captain | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Deputy Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Executive Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Interim City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Public Works Assistance | Non HFRA, T3, T2 | 2025-01-17 19:52
Rialto | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Riverside County | EMD Duty Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Riverside County | EMD Duty Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Riverside County | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Acting Assist. Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Acting Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Associate Planner | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Chief of Staff for Councilman Alexander | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | City Engineer / Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Executive Assistant | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Government Affairs | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Lietuenant (Executive Officer) | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Lieutenant | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Lieutenant (Eastern District Command) | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Lieutenant (Northern District Command) | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Lieutenant/Patrol Watch Commander | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Neighborhood and Customer Services Operations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Police Chief - CSUSB | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Public Information Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino | Public Works, Permitting | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Assistant Director for Public Works | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Assistant Director Public Health | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Assistant Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Captain/SBSD Emergency Services | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | CEO Administrative Aide | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Chief Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Communications Director | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Community Svs Liaison, Supervisor Hagman | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Corporal - Public Affairs Division Sheriff's Dept | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Deputy Chief of Administration | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Deputy Chief of Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Deputy Director-DPW | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Deputy Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Deputy Fire Chief Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Deputy Fire Marshal | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Director | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Director of Real Estate Services Department | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Director of the Office of Emergency Services | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Director, ROV | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Dispatch for Fac. Management | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Dispatch Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | District Director, 1st District | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | District Director, 5th District | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Division Chief- EHS | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Division Manager, Water and Sanitation | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Emergency Services Coordinator / SBSD Emer Operations | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Emergency Services Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | EMS Agency Duty Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Engineering Construction | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Engineering Manager-DPW | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Executive Admin Assist for Luther Snoke Deputy CEO | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Executive Admin Assistant | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Executive Aide to Supervisor Rowe | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Executive Secretary | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Executive Secretary, Supervisor Armendarez | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Field Representative | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Fire Chief/Fire Warden | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Fire Marshal | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Manager - Real Estate Services | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Media Specialist-OES | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | OES Duty Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Parks Operations Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Policy Advisor, 4th District | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Project Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Public Health Duty Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Public Health Program Mananger | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Public Information Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Public Information Officer, SBFIRE | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Senior Advisor | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Senior Planner | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Supervising Emergency Services Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
San Bernardino County | Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
San Dimas | Asst. City Manager | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Captain | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | City Manager | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Councilmember | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Matthew Bodell | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Mayor | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Mayor pro tem | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Operaions Lieutenant | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Public Works Director | Non HFRA, T3, T2 | 2025-01-21 06:46
San Dimas | Watch Commander | Non HFRA, T3, T2 | 2025-01-21 06:46
San Fernando | Lieutenant/City Emergency Coordinator | Non HFRA, T3, T2 | 2025-01-18 14:32
San Fernando | Watch Commander Office | Non HFRA, T3, T2 | 2025-01-18 14:32
San Fernando |  | Non HFRA, T3, T2 | 2025-01-18 14:32
San Jacinto | Chief of Public Utilities | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Deputy City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Division Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Duepty City Manager - Development Services | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Economic Development Administrator | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Public Utilities Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
San Jacinto | Water Utility Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Clarita | Community Services Liaison, Los Angeles County Fire Department Division III | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Clarita | Emergency Operations Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Clarita | Intergovernmental Relations Analyst | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Clarita |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Commander | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Community & Economic Development Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Finance Director/Treasurer | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Human Resources Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Parks and Recreation Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Police Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Street Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Streets Maintenance Lead Worker | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Vice Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Water Distribution Lead Worker | Non HFRA, T3, T2 | 2025-01-17 19:52
Santa Paula | Water Ops Superintendent | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | City Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Deputy Director Maintenance | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Emergency Operations Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Environmental Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Mayor Pro Tem | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Principal Engineer – Sanitation | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Principal Engineer – Water | Non HFRA, T3, T2 | 2025-01-17 19:52
Simi Valley | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | Administrative Assistant/ Outage Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | City Clerk/Airport Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | City Inspecter | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | Councilmember | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | Deputy Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | Development Services Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Tehachapi | test | Non HFRA, T3, T2 | 2025-01-17 19:52
Temecula | Councilmember | Non HFRA, T3, T2 | 2025-01-18 14:32
Temecula | Emergency Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Temecula | Outage Notification Distribution | Non HFRA, T3, T2 | 2025-01-18 14:32
Temecula | PSPS Notification Distribution | Non HFRA, T3, T2 | 2025-01-18 14:32
Temecula | Public Works Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | City Attorney | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | City Facilities Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | City Facilitiies Staff | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Comm. Development Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | CRPD General Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Deputy City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Deputy PW Director - Engineering | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Deputy PW Director - Operations | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Economic Development Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Finance Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Fleet Services Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | HCTP Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | HCTP Operations Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Landscape Maintenance Crew Leader | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | MSC Superintendent | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Public Information | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Public Works Director | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Risk Services Administrator | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Senior Energy Analyst | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Senior Sustainability Analyst | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Street Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Traffic Engineer | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Wastewater Utilities Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Water Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Thousand Oaks | Water Utilities Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-18 14:32
Tulare County | County Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Tulare County | Director, Resource Management Agency | Non HFRA, T3, T2 | 2025-01-17 19:52
Tulare County | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Tulare County | OES Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Upland | Administrative Aide | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Administrative Officer, Upland CERT | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Assistant Fire Chief | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | City Manager | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Councilmember | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Development Services Director | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Emergency Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Upland | Emergency Services Coordinator | Non HFRA, T3, T2 | 2025-01-27 15:44
Upland | Exec Assistant to City Manager | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Mayor | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | Police Chief | Non HFRA, T3, T2 | 2025-01-20 19:57
Upland | School Unified Director | Non HFRA, T3, T2 | 2025-01-20 19:57
Ventura | Assistant Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Assistant Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Battalion Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | City Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Deputy Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Deputy Public Works Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Emergency Contact | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Fleet and Facilities Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Interim Chief of Police | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Assistant County Executive Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Assistant Director of Public Works | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Assistant Sheriff | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Chief Deputy Director | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Chief of Staff | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | County Clerk | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | County Supervisor | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Director of Roads & Transportation | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Disability Access Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Division Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Division Fire Chief | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Emergency Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | IT Manager | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Law Enforcement | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Mr. | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Ms | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Program Administrator, Sustainability Division | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Public Works Safety Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Senior Code Compliance Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Sustainability Officer | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County | Traffic Engineering Manager | Non HFRA, T3, T2 | 2025-01-23 14:02
Ventura County | Wildfire Liaison | Non HFRA, T3, T2 | 2025-01-17 19:52
Ventura County |  | Non HFRA, T3, T2 | 2025-01-17 19:52
Villa Park | 24-Hour Contact | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | Building Official | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | Chief of Police Services | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | City Engineer | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | City Manager/City Clerk | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | Councilmember | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | Maintenance Supervisor | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | Management Analyst | Non HFRA, T3, T2 | 2025-01-20 00:02
Villa Park | Senior Management Analyst | Non HFRA, T3, T2 | 2025-01-20 00:02
Westlake Village | Administrative Analyst | Non HFRA, T3, T2 | 2025-01-18 14:32
Westlake Village | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Westlake Village | City Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Westlake Village | Deputy City Engineer | Non HFRA, T3, T2 | 2025-01-18 14:32
Wildomar | Economic Development Director/PIO | Non HFRA, T3, T2 | 2025-01-18 14:32
Wildomar | Emergency Management | Non HFRA, T3, T2 | 2025-01-18 14:32
Wildomar | Management Analyst I Code Enforcement and Emergency Services | Non HFRA, T3, T2 | 2025-01-18 14:32
Yorba Linda | Assistant City Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Assistant to the City Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Building Official | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Chief of Police Services | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | City Clerk | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | City Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Community Development Director | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Councilmember | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Deputy Public Works Director/Asst. City Engineer | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Economic Development Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Emergency Management Coordinator | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Management Analyst - Communications | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Mayor | Non HFRA, T3, T2 | 2025-01-17 19:52
Yorba Linda | Parks and Facilities Superintendent | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Planning Manager | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Principal Management Analyst | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Public Works Director/City Engineer | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Public Works Superintendent | Non HFRA, T3, T2 | 2025-01-20 00:02
Yorba Linda | Senior Civil Engineer | Non HFRA, T3, T2 | 2025-01-20 00:02
Yucaipa | Battalion Chief | Non HFRA, T3, T2 | 2025-01-18 14:32
Yucaipa | Emergency Services Manager | Non HFRA, T3, T2 | 2025-01-18 14:32
Yucaipa |  | Non HFRA, T3, T2 | 2025-01-18 14:32
ABRAHAM HAMI |  | Non HFRA, T3, T2 | 2025-01-19 14:20
ABRAMS,M AND ABRAMS,L |  | T3 | 2025-01-18 14:35
ACE ASSOCIATES, LLC |  | T3 | 2025-01-17 20:29
AFP MUTUAL WATER CO |  | T3, T2 | 2025-01-17 20:29
AH4882 LLC |  | Non HFRA, T3 | 2025-01-17 20:29
AIR COMMUNICATION SERVICES INC |  | T3 | 2025-01-17 20:29
AIR TOUCH CELLULAR |  | Non HFRA, T3, T2 | 2025-01-17 20:29
ALICIA ROBISON |  | T3 | 2025-01-17 20:29
ALL PRO BROADCASTING |  | T3 | 2025-01-18 14:35
ALPINE WATER USERS ASSOCIATION |  | T3 | 2025-01-17 20:29
ALTIS MASTER ASSOCIATION |  | Non HFRA, T3, T2 | 2025-01-17 19:30
ALY BAZZI |  | T3 | 2025-01-18 14:35
AM PCS CA INC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
AMAIRANI DESAULNIERS |  | Non HFRA, T3 | 2025-01-18 14:35
AMANDA SALTER |  | Non HFRA, T3, T2 | 2025-01-19 14:20
AMATURO GP LTD, THE |  | Non HFRA, T3, T2 | 2025-01-17 20:29
AMERICAN BROADCASTING COMPANY |  | T3 | 2025-01-17 20:29
AMERICAN TOWER CORPORATION |  | Non HFRA, T3, T2 | 2025-01-17 20:29
ANTELOPE EXPANSION 2, LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
ANTELOPE VALLEY E KERN WTR AGY |  | Non HFRA, T3, T2 | 2025-01-20 23:47
ANTHONY TOOLEY |  | T3 | 2025-01-18 14:35
APALLA KARIM |  | T3 | 2025-01-22 05:52
AROWBEAR CO PARK |  | T3 | 2025-01-17 20:29
ARROW BEAR PK CO WATER DIST |  | T3 | 2025-01-17 20:29
ARROWHEAD VILLAS MUTUAL SERV |  | T3 | 2025-01-17 20:29
ARUSYAK KARAPETYAN |  | Non HFRA, T3, T2 | 2025-01-21 16:21
ASPIRE COMMUNICATIONS LLC |  | T3 | 2025-01-19 14:20
AT & T LIGHTSPEED |  | T3 | 2025-01-23 16:48
AT&T CORPORATION |  | Non HFRA, T3, T2 | 2025-01-17 19:30
AT&T MOBILITY |  | Non HFRA, T3, T2 | 2025-01-17 20:29
AT&T WIRELESS SERVICES |  | Non HFRA, T3, T2 | 2025-01-17 19:30
AVOTOPIA LLC |  | T3 | 2025-01-18 14:35
AVSR1, LLC |  | Non HFRA, T3, T2 | 2025-01-20 23:47
B PER ELECTRONICS INC |  | T2 | 2025-01-18 14:35
BANNING HEIGHTS WATER |  | T3, T2 | 2025-01-17 19:30
BANNING, CITY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
BARTON FLATS CAMP ASSOCIATION |  | T3 | 2025-01-18 14:35
BAYSHORE SOLAR A, LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
BEAR VALLEY COMM SERV DIST |  | T3, T2 | 2025-01-19 14:20
BEAUMONT CHERRY VALLEY WATER |  | Non HFRA, T3, T2 | 2025-01-17 19:30
BENJAMIN VASQUEZ |  | Non HFRA, T3, T2 | 2025-01-22 17:57
BLANCA TENORIO |  | T3 | 2025-01-17 20:29
BLEICHFLAT MUTUAL WATER |  | Non HFRA, T3, T2 | 2025-01-20 23:47
BMB 355 |  | Non HFRA, T3 | 2025-01-17 20:29
BOOM RANCH LLC |  | T3 | 2025-01-17 20:29
Braverde Community Association |  | Non HFRA, T2 | 2025-01-22 01:30
BREA, CITY OF |  | Non HFRA, T3, T2 | 2025-01-20 00:12
BRENT MCCAULEY |  | T3 | 2025-01-17 20:29
BRIANNE MCGRATH |  | Non HFRA, T3, T2 | 2025-01-22 17:57
BRIARWOOD COMMUNITY ASSOCIATIO |  | T3 | 2025-01-23 16:48
BRIDGE NEWS, LLC |  |  | 2025-01-17 20:29
BRIGHT HOUSE NETWORKS, LLC |  | T3, T2 | 2025-01-17 20:29
BRIGHT LAKE MUTUAL WATER CO. |  | T3, T2 | 2025-01-17 20:29
BROWNSTONE MUTUAL |  | Non HFRA, T3, T2 | 2025-01-18 14:35
BRUCE WADDELL |  | T3 | 2025-01-18 14:35
CABAZON WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CALABASAS, CITY OF |  | T3, T2 | 2025-01-19 16:21
CALIFORNIA AMERICAN WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CALIFORNIA STATE HIGHWY PATROL |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CALIFORNIA WATER SERVICES, CO |  | T3, T2 | 2025-01-17 20:29
CALLEGUAS MUNICIPAL WATER DIST |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CALTRANS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CAMARILLO, CITY OF |  | Non HFRA, T3, T2 | 2025-01-19 14:20
CAMP BARTLETT |  | Non HFRA, T3 | 2025-01-17 20:29
CAMP WATERMAN MUT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CAMROSA WATER DISTRICT |  | Non HFRA, T3 | 2025-01-17 20:29
CANYON IRRIGATION COMPANY |  | Non HFRA, T3 | 2025-01-17 20:29
CATALINA WILLS |  | T3 | 2025-01-17 20:29
CATHY SHEPARD |  | T3 | 2025-01-17 20:29
CEI, INC |  | T3 | 2025-01-20 23:45
CENTRAL ANTELOPE DRY RANCH C |  | Non HFRA, T3, T2 | 2025-01-25 13:42
CHANCELLOR MEDIA CORPORATION |  |  | 2025-01-17 20:29
CHARLES BOWMAN |  | T3 | 2025-01-18 14:35
CHARLES LUCKMAN III |  | T3, T2 | 2025-01-18 14:35
CHARTER COMMUNICATIONS |  | Non HFRA, T3, T2 | 2025-01-17 19:30
CHARTER COMMUNICATIONS INC |  | Non HFRA, T3, T2 | 2025-01-17 19:30
CHERISE PETERS |  | T3 | 2025-01-23 01:56
CHERRY VALLEY WATER, CO |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CHINO BASIN DESALTER AUTHORITY |  | Non HFRA, T2 | 2025-01-17 20:29
CHINO HILLS, CITY OF |  | Non HFRA, T3, T2 | 2025-01-19 23:59
CHINO, CITY OF |  | Non HFRA, T2 | 2025-01-17 20:29
CHIP ANZALONE |  | T3 | 2025-01-17 20:29
CHRISTOPHER ROSS |  | T3 | 2025-01-17 20:29
CINGULAR WIRELESS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CINGULAR WIRELESS LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CITRUS MUTUAL WATER |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CITY OF GRAND TERRACE |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CITY OF MURRIETA |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CITY OF YUCAIPA |  | Non HFRA, T2 | 2025-01-21 14:42
CLAYTON TRUSSELL |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CLEAR WIRE COMMUNICATIONS LLC |  | Non HFRA, T3, T2 | 2025-01-19 14:20
CMP ANGLS TRCT LND |  | T3 | 2025-01-18 14:35
CODY LASSEN |  | T3 | 2025-01-18 14:35
COLLINS TOWER CORPORATION |  | Non HFRA, T2 | 2025-01-23 01:56
COMMUNICATIONS RELAY, LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
COMMUNITY TV OF SO CAL INC |  |  | 2025-01-17 20:29
COMSAT |  | Non HFRA, T3 | 2025-01-17 20:29
COMSTOCK HOMES |  | Non HFRA, T3, T2 | 2025-01-22 17:57
COSTA DE ORO TV INC |  |  | 2025-01-17 20:29
COUNTY OF KERN |  | T3, T2 | 2025-01-19 14:20
COX COMMUNICATIONS CALIF, LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CPG PARTNERS LP |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CR & R INCORPORATED |  | Non HFRA, T2 | 2025-01-17 19:30
CRAIG STEHSEL |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CRESCENTA VALLEY COUNTY WATER |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CRESTLINE LAKE ARROWHEAD WATER |  | T3 | 2025-01-17 20:29
CRESTLINE SANITATION DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CRESTLINE VILLAGE WATER DIST |  | T3 | 2025-01-17 20:29
CROWN CASTLE |  | Non HFRA, T3, T2 | 2025-01-17 20:29
CROWN CASTLE NG WEST LLC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CT AM Venture LLC |  | Non HFRA, T2 | 2025-01-18 14:35
CUCAMONGA VALLEY WATER DIST |  | Non HFRA, T3, T2 | 2025-01-18 14:35
CURTIS JOHNSON |  | T3 | 2025-01-19 14:20
CVIN, LLC |  | T3, T2 | 2025-01-18 14:35
D.R. HORTON, INC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
DALE CISNEROS |  | T3, T2 | 2025-01-17 20:29
DANIELLE WITHERS |  | T3 | 2025-01-18 14:35
DAVID GRIFFITH |  | T3 | 2025-01-20 23:45
DEBROAH ROBERTS |  | T3 | 2025-01-18 14:35
DENNIS HUGHES |  | T3 | 2025-01-17 20:29
DEPARTMENT OF AGRICULTURE |  | T3 | 2025-01-17 20:29
DEVORE MUTUAL WATER |  | Non HFRA, T3, T2 | 2025-01-17 20:29
DEVORE WATER COMPANY |  | Non HFRA, T3, T2 | 2025-01-17 20:29
DIAMOND VALLEY SOLAR, LLC |  | Non HFRA, T2 | 2025-01-21 11:15
DISH WIRELESS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
DISH WIRELESS HOLDING, LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
DOGWOOD/BLUEJAY WATER |  | T3 | 2025-01-17 20:29
DOWN-TO-EARTH ECO LLC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
DR HORTON INC |  | Non HFRA, T2 | 2025-01-18 14:35
DSHAUN SHAMBURGER |  | Non HFRA, T3, T2 | 2025-01-20 23:47
DUANE RUSSELL |  | Non HFRA, T3, T2 | 2025-01-20 23:47
DWR - STATE WATER PROJECTS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
EAST ORANGE CO WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
EAST VALLEY WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
EASTERN MUNICIPAL WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 19:30
EDUCATIONAL MEDIA FOUNDATION |  | T3 | 2025-01-19 14:20
EDWARD GATHRIGHT |  | Non HFRA, T3, T2 | 2025-01-22 17:57
ELECTRIC LIGHT WAVE |  | Non HFRA, T3, T2 | 2025-01-17 20:29
ELIETTE RAMOS |  | T3 | 2025-01-17 20:29
ELSINORE VALLEY MUN WATER DIST |  | Non HFRA, T3, T2 | 2025-01-17 20:29
EMANUEL ALVAREZ GLEMKSTEIN |  | Non HFRA, T3 | 2025-01-17 20:29
EPWORTH WATER GROUP |  | T3 | 2025-01-17 20:29
FALCON HOLDING GROUP LP |  | T3, T2 | 2025-01-17 19:30
FALLSVALE SERVICE CO |  | T3 | 2025-01-18 14:35
FANNIE MAE |  | T3, T2 | 2025-01-22 17:48
FARRAH LANE |  | Non HFRA, T3, T2 | 2025-01-18 14:35
FEDERAL BUREAU OF INVSTIGATION |  | T3 | 2025-01-17 20:29
FERN VALLEY WATER DISTRICT |  | T3 | 2025-01-18 14:35
FILLMORE IRRIGATION COMPANY |  | Non HFRA, T3, T2 | 2025-01-18 14:35
FILLMORE, CITY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
FLORENCIO SOTO |  | Non HFRA, T3, T2 | 2025-01-21 14:42
FLORENCIO VILLASENOR |  | T3 | 2025-01-18 14:35
FONTANA UNION WATER |  | Non HFRA, T3, T2 | 2025-01-17 20:29
FONTANA, CITY OF |  | Non HFRA, T2 | 2025-01-19 14:20
Forestar (USA) Real Estate Group, Inc. |  | Non HFRA, T2 | 2025-01-22 01:30
FOX TELEVISION STATIONS INC |  |  | 2025-01-17 20:29
FRED PARKER |  | T3 | 2025-01-18 14:35
FRONTIER COMMUNICATIONS PARENT INC |  | Non HFRA, T3, T2 | 2025-01-17 19:30
FULLER FALLS MUTUAL WTR CO |  | Non HFRA, T3 | 2025-01-17 20:29
GLEN MARTIN MUTUAL WATER CO |  | T3, T2 | 2025-01-18 14:35
GLENDALE ELECTRONIC |  | T3 | 2025-01-17 20:29
GLOBAL SIGNAL INC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
GOLDEN STATE WATER COMPANY |  | Non HFRA, T3, T2 | 2025-01-18 14:35
GOODENOUGH MUTUAL WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
GREEN VALLEY MUTUAL WATER |  | T3 | 2025-01-17 19:30
GREER RANCH COMMUNITY ASSOC |  | T2 | 2025-01-18 14:35
GTE MOBILENET INCORPORATED |  | T3, T2 | 2025-01-19 14:20
GUADALASCA MUTUAL WATER CO |  | Non HFRA, T2 | 2025-01-23 01:56
GUADALUPE PUENTE |  | Non HFRA, T3, T2 | 2025-01-21 14:42
HARRIS CORPORATION |  | Non HFRA, T3, T2 | 2025-01-18 14:35
HARSHABA ZALA |  | T3 | 2025-01-23 01:56
HAYDEE MOLINA |  | Non HFRA, T3, T2 | 2025-01-17 20:29
HDH WATER SYSTEM |  | Non HFRA, T3, T2 | 2025-01-17 20:29
HEMET, CITY OF |  | Non HFRA, T2 | 2025-01-18 14:35
HERRITAGE POINTE & PLACE COMM ASSO |  | Non HFRA, T3, T2 | 2025-01-18 14:35
HIDDEN OAKS ESTATES HOA |  | T3 | 2025-01-18 14:35
HIGH DESERT BROADCASTING |  | Non HFRA, T3, T2 | 2025-01-25 13:42
HIGH VALLEYS WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
HOSOPO CORPORATION |  | Non HFRA, T2 | 2025-01-24 22:08
I10 LOGISTICS OWNER, LLC |  | Non HFRA, T3, T2 | 2025-01-19 14:20
IDYLLWILD FIRE DEPT |  | T3 | 2025-01-18 14:35
IDYLLWILD WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-18 14:35
IHEARTCOMMUNICATIONS INC |  | T3 | 2025-01-19 14:20
INDUSTRY, CITY OF |  | Non HFRA, T3, T2 | 2025-01-21 00:26
INLAND EMPIRE UTILITIES AGENCY |  | Non HFRA, T3, T2 | 2025-01-17 20:29
INTELSAT CORPORATION |  | Non HFRA, T3, T2 | 2025-01-17 20:29
INTERNAL REVENUE SERVICE |  | T3 | 2025-01-17 20:29
IRVINE RANCH WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
J R ENERGY ENTERPRISES, INC |  | T3 | 2025-01-18 14:35
J5T RANCH, LLC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
JACK MURPHY |  | T3, T2 | 2025-01-17 20:29
JACOB SCHWENSON |  | Non HFRA, T3, T2 | 2025-01-17 20:29
JAIME LOPEZ |  | Non HFRA, T2 | 2025-01-23 01:56
JAMES TOONE |  | T3 | 2025-01-20 23:45
JBS CAPITAL, LLC |  | Non HFRA, T3, T2 | 2025-01-22 17:57
JERI SERATTI |  | T3 | 2025-01-18 14:35
JESSICA JIMENEZ |  | Non HFRA, T2 | 2025-01-17 19:30
JIM DOERING |  | T3 | 2025-01-18 14:35
JOHN ANDERSON |  | T3 | 2025-01-24 01:14
JOHN BAKER |  | T3, T2 | 2025-01-22 17:48
JOHN LEE |  | Non HFRA, T3, T2 | 2025-01-17 20:29
JOSE MEDINA LUNA |  | T3, T2 | 2025-01-22 17:48
JULIO TAWATA |  | T3 | 2025-01-23 01:56
julio torres |  | Non HFRA, T3, T2 | 2025-01-22 17:57
JURUPA COMMUNITY SERVICES DISTRICT |  | Non HFRA, T2 | 2025-01-17 20:29
JURUPA VALLEY, CITY OF |  | Non HFRA, T2 | 2025-01-17 19:30
K2TOWERSIII LLC |  | T3 | 2025-01-17 20:29
KAITLYN HILL |  | T3 | 2025-01-20 23:45
KB HOME |  | Non HFRA, T2 | 2025-01-23 16:37
KB HOMES COASTAL INC |  | Non HFRA, T2 | 2025-01-23 16:37
KCBS/KCAL |  |  | 2025-01-17 20:29
KDAY RADIO LLC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
KHPY RADIO |  | T3 | 2025-01-23 01:56
KIERTON INC. |  | T3 | 2025-01-17 20:29
KIMBERLY KING |  | T3 | 2025-01-17 20:29
KOCE-TV/DT |  |  | 2025-01-18 10:20
KPWR RADIO |  |  | 2025-01-17 20:29
KRISTA PERRY |  | Non HFRA, T3 | 2025-01-17 20:29
KSGN INC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
KTLA INCORPORATED |  |  | 2025-01-17 20:29
KVMD TV |  | T3 | 2025-01-18 14:35
LA CANADA IRRIGATION DISTRICT |  | Non HFRA, T3, T2 | 2025-01-18 14:35
LAKE ARROWHEAD C S D |  | T3 | 2025-01-17 19:30
LAKE ELSINORE, CITY OF |  | Non HFRA, T3, T2 | 2025-01-19 14:20
LAKE HEMET MUNICIPAL WATER DIS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LAKEMASTER |  | Non HFRA, T3, T2 | 2025-01-26 07:48
LAS VIRGENES MUNICIPAL WTR DST |  | T3, T2 | 2025-01-18 14:35
LAZER BROADCASTING |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LDDS WORLDCOM |  | T3, T2 | 2025-01-18 14:35
LENNAR HOMES OF CALIFORNIA |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LEVINE, SAUL R DBA |  |  | 2025-01-17 20:29
LIBERMAN BROADCASTING, INC |  | Non HFRA, T3, T2 | 2025-01-19 14:20
LODESTAR TOWERS, INC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LOMA LINDA BROADCSTNG NTK, INC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
LOMA LINDA, CITY OF |  | Non HFRA, T3, T2 | 2025-01-18 14:35
LOREE SNYDER |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LOS ANGELES COUNTY FIRE DEPT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LOS ANGELES COUNTY ISD |  | Non HFRA, T3, T2 | 2025-01-17 20:29
Los Angeles County LARICS-ISD |  | Non HFRA, T3, T2 | 2025-01-21 12:16
LOS ANGELES COUNTY PUBLIC WORK |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LOS ANGELES DEPT OF WTR & POWR |  | T3 | 2025-01-17 20:29
LOS ANGELES, CITY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
LUNDE WATER LLC |  | T3 | 2025-01-18 14:35
LYTLE SPRINGS WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
MABROUK LEGACY LLC |  | T3 | 2025-01-18 14:35
MAKAYLA KING |  | T3 | 2025-01-18 14:35
MALIBU, CITY OF |  | T3, T2 | 2025-01-18 14:35
MANUEL ENRIQUEZ |  | T3 | 2025-01-18 14:35
MARCUS CABLE ASSOCIATION |  | Non HFRA, T3, T2 | 2025-01-17 20:29
MARK RATTO |  | Non HFRA, T3, T2 | 2025-01-18 14:35
MARTHA GREEN-WHITNEY |  | T3 | 2025-01-18 14:35
MARTHA ROBLES |  | Non HFRA, T2 | 2025-01-18 14:35
MARTIN TREACY |  | T3 | 2025-01-20 23:45
MCSWEENY FARMS COMMUNITY ASSOC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
MEADOW BAY NO HOME |  | T3 | 2025-01-17 19:30
MEDIACOM, LLC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
METROPOLITAN WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
MFE WATER WELL |  | Non HFRA, T3 | 2025-01-17 20:29
MICHAEL ALEXANDER |  | T3 | 2025-01-18 14:35
MICHELE MADEIRA |  | T3 | 2025-01-18 14:35
MIGUEL FRANCO |  | Non HFRA, T2 | 2025-01-18 14:35
MIGUEL MAGDALENO |  | Non HFRA, T3 | 2025-01-17 20:29
MISSION SPRINGS WATER DISTRICT |  | T3, T2 | 2025-01-18 14:35
MKK PROPERTIES |  | Non HFRA, T3, T2 | 2025-01-20 23:47
MOBILE RELAY ASSOC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
MOBILITIE INVESTMENTS II LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
MOBILITIE LLC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
MONTES, ABEL |  | Non HFRA, T3, T2 | 2025-01-18 14:35
MONTI MIDGETTE |  | T3 | 2025-01-18 14:35
MORONGO BAND MISSION INDIANS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
MOUNTAIN INVESTMENT |  | Non HFRA, T3, T2 | 2025-01-18 14:35
MOUNTAIN REPEATER ASSOC, INC |  | Non HFRA, T3, T2 | 2025-01-18 14:35
MT BALDY FIRE DEPT |  | Non HFRA, T3, T2 | 2025-01-19 14:20
MURUGESA THANGAVEL |  | Non HFRA, T3 | 2025-01-17 20:29
MUSCOY MUTUAL WATER CO 1 |  | Non HFRA, T3, T2 | 2025-01-23 16:48
MUTUAL WATER CO |  | Non HFRA, T2 | 2025-01-23 01:56
NANDOR KASA |  | Non HFRA, T2 | 2025-01-22 01:30
NATALIE GREENBERGE |  | Non HFRA, T3 | 2025-01-17 20:29
NATIONAL FARM WORKERS SERVICE |  | T3, T2 | 2025-01-19 14:20
NBC UNIVERSAL INCORPORATED |  |  | 2025-01-17 20:29
NBC UNIVERSAL LLC |  |  | 2025-01-17 20:29
NEEDHAM RANCH PHASE 2B BUILDING 11 LLC |  | T3 | 2025-01-17 20:29
NEPTUNE WATER GROUP |  | T3 | 2025-01-17 20:29
NEW INSPIRATION INC |  |  | 2025-01-17 20:29
NEXTEL COMMUNICATIONS, INC |  | T3 | 2025-01-18 14:35
NICHOLS RANCH HOA |  | Non HFRA, T3, T2 | 2025-01-19 14:20
NISHA KUMAR |  | T3 | 2025-01-20 23:45
NORTH TRAILS MUTUAL WATER CO |  | T3 | 2025-01-18 14:35
NRG SOLAR ALPINE |  | Non HFRA, T2 | 2025-01-22 17:29
NUEVO WATER CO |  | Non HFRA, T2 | 2025-01-18 14:35
OASIS KAINGA INC |  | T3 | 2025-01-18 14:35
OJAI FARMS, INC |  | Non HFRA, T3, T2 | 2025-01-22 17:57
OJAI VALLEY SANITATION DIST |  | Non HFRA, T3 | 2025-01-17 20:29
OLGA CARDENAS |  | Non HFRA, T3, T2 | 2025-01-22 17:57
ONE DOT SIX CORP, DBA LIGHTSQU |  | Non HFRA, T3, T2 | 2025-01-20 00:12
ORANGE COUNTY FIRE AUTHORITY |  | Non HFRA, T3, T2 | 2025-01-17 20:29
ORANGE, CITY OF |  | Non HFRA, T2 | 2025-01-19 23:59
ORANGE, COUNTY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
OXNARD, CITY OF |  | Non HFRA, T3 | 2025-01-17 20:29
PACIFIC AVE WATER CO LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
PACIFIC BELL CORP |  | Non HFRA, T3, T2 | 2025-01-17 19:30
PACIFIC GAS & ELECTRIC COMPANY |  | T3, T2 | 2025-01-17 20:29
PACIFICA FOUNDATION |  |  | 2025-01-17 20:29
PALO VERDE IRRIGATION DISTRICT |  | T3, T2 | 2025-01-18 14:35
PECHANGA INDIAN RESERVATION |  | T3, T2 | 2025-01-22 17:48
PEDLEY LAND COMPANY LLC |  | Non HFRA, T2 | 2025-01-17 20:29
PHILIP BERARDI |  | Non HFRA, T3 | 2025-01-17 20:29
PHILLIP MAYS |  | T3 | 2025-01-18 14:35
PINE COVE WATER DISTRICT |  | T3 | 2025-01-18 14:35
PLACIDO GONZALEZ |  | T3 | 2025-01-18 14:35
PRAMOD KOLANU |  | T3, T2 | 2025-01-18 14:35
PRESERVE MASTER MAINTENANCE CO |  | Non HFRA, T2 | 2025-01-17 20:29
PRESIDIO WH PIRU 169 LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
PUBLIC SAFETY COMM DIV (PSCD) |  | T3 | 2025-01-17 20:29
PULTE HOME CO LLC |  | Non HFRA, T2 | 2025-01-18 14:35
QUALITY AG INC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
RACE COMMUNICATION |  | T3, T2 | 2025-01-19 14:20
RADIANCE SOLAR 4 LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
RADIANCE SOLAR 5 LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
RAMIRO SILVA |  | T3 | 2025-01-19 14:20
RANCHO CAL WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-18 14:35
Rancho GG Western Wear |  | Non HFRA, T2 | 2025-01-18 14:35
RANCHO MAR LLC |  | T3 | 2025-01-20 00:42
REAL ESTATE REIMAGINED LLC |  | T3 | 2025-01-24 01:14
RED MOUNTAIN RANCH |  | T3 | 2025-01-24 01:14
REDLANDS, CITY OF |  | Non HFRA, T3, T2 | 2025-01-18 14:35
RICARDO SALDANA |  | T3, T2 | 2025-01-22 17:48
RICHARD STEVENS |  | Non HFRA, T3, T2 | 2025-01-22 17:57
RICHARD WILSON |  | Non HFRA, T3, T2 | 2025-01-17 20:29
RIVERSIDE HIGHLAND WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
RIVERSIDE TELEPORT CORPORATION |  | Non HFRA, T2 | 2025-01-18 14:35
RIVERSIDE, CITY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
RIVERSIDE, COUNTY OF |  | Non HFRA, T3, T2 | 2025-01-17 19:30
ROBERT REYES |  | T3 | 2025-01-18 14:35
ROBERT RUIZ |  | Non HFRA, T3, T2 | 2025-01-17 20:29
ROBERT WILLIAM COMPANY |  | Non HFRA, T3, T2 | 2025-01-17 20:29
RODEO SOLAR C2 LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
RODEO SOLAR D2, LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
RODNEY AUTO SERVICE INC |  | T3 | 2025-01-17 20:29
RONALD KIDD |  | T3 | 2025-01-19 14:20
ROWLAND WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-20 23:39
RUBIDOUX COMMUNITY SERVICES DISTRICT |  | Non HFRA, T2 | 2025-01-17 19:30
RUNNING SPRINGS WATER DISTRICT |  | T3 | 2025-01-17 20:29
SAI BALAJI RVP |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SALKA CABAZON WIND LLC |  | T3, T2 | 2025-01-18 14:35
SALVADOR DOMINGUEZ |  | Non HFRA, T3, T2 | 2025-01-18 14:35
SAN ANTONIO WATER COMPANY INC |  | Non HFRA, T3, T2 | 2025-01-19 14:20
SAN BERNARDINO VALLEY MWD |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SAN BERNARDINO WATER DEPT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SAN BERNARDINO, COUNTY OF |  | Non HFRA, T3, T2 | 2025-01-17 19:30
SAN CAYETANO WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SAN DIEGO GAS & ELECTRIC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SAN FERNANDO, CITY OF |  | Non HFRA, T3, T2 | 2025-01-18 14:35
SAN GABRIEL VALLEY WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SAN MANUEL BAND OF INDIANS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SAN RIVER RADIO |  | T3 | 2025-01-17 20:29
SAND CANYON WATER GROUP |  | Non HFRA, T3, T2 | 2025-01-19 14:20
SANDRA ENERGY LLC |  | Non HFRA, T3, T2 | 2025-01-25 13:42
SANTA ANA WATERSHED PROJECT |  | Non HFRA, T2 | 2025-01-17 20:29
SANTA CLARITA VALLEY WTR AGNCY |  | T3, T2 | 2025-01-17 20:29
SANTA CLARITA, CITY OF |  | T3 | 2025-01-17 20:29
SANTA MARGARITA WATER DISTRICT |  | T3 | 2025-01-17 20:29
SANTA PAULA, CITY OF |  | Non HFRA, T3 | 2025-01-17 20:29
SCE/CONTRACT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SERRANO IRRIGATION DISTRICT |  | Non HFRA, T2 | 2025-01-19 23:59
SESPE AGRI WATER CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SHARON RYAN |  | T3 | 2025-01-22 05:52
SHARONDALE MESA OWNERS ASSOC |  | Non HFRA, T3, T2 | 2025-01-22 17:57
SIERRA HEIGHTS MHC ASSOCIATES LP |  | T3 | 2025-01-17 20:29
SILENT SPRINGS LLC |  | T3 | 2025-01-19 14:20
SIMI VALLEY, CITY OF |  | T3 | 2025-01-18 14:35
SKYFOREST MUTUAL |  | T3 | 2025-01-17 20:29
SLEEPY VAL WATER CO |  | T3 | 2025-01-18 14:35
SNOWCREST HEIGHTS IMPRVMT ASSC |  | Non HFRA, T3, T2 | 2025-01-19 14:20
SO MTN MUTUAL WATER |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SOBOBA BAND OF LUISENO INDIANS |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SOLAR STAR CALIFORNIA XIX, LLC |  | Non HFRA, T3, T2 | 2025-01-20 23:47
SOUTH MESA WATER COMPANY |  | Non HFRA, T3, T2 | 2025-01-22 17:48
SOUTHERN CALIFORNIA EDISON CO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SOUTHERN CALIFORNIA GAS CO |  | Non HFRA, T3, T2 | 2025-01-17 19:30
SOUTHSIDE IMPRO CO |  | Non HFRA, T3, T2 | 2025-01-22 17:57
SPECTRASITE COMMUNICATION INC. |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SPECTRUM |  | Non HFRA, T3, T2 | 2025-01-17 19:30
SPRINT NEXTEL CORPORATION |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SPRINT PCS ASSETS |  | Non HFRA, T3, T2 | 2025-01-19 14:20
SPRINT TELEPHONY PCS L.P |  | T3, T2 | 2025-01-17 20:29
SPRINT UNITED MANAGEMENT CO |  | Non HFRA, T3, T2 | 2025-01-18 14:35
SPRINT UTILITIES |  | T3 | 2025-01-17 20:29
SPV WATER CO |  | T3 | 2025-01-18 14:35
STALLION SPRINGS C S D |  | T3, T2 | 2025-01-19 14:20
STANLEY DELGADO |  | Non HFRA, T3, T2 | 2025-01-17 20:29
STEFAN CASTLE |  | Non HFRA, T3 | 2025-01-17 20:29
STEPHEN MARINACCIO |  | T3 | 2025-01-17 20:29
STEPHEN MASCARO |  | T3 | 2025-01-18 14:35
STONE CREEK WTR CO |  | T3 | 2025-01-18 14:35
STRAW LDG MUT WTR |  | T3 | 2025-01-17 20:29
STRAWBERRY LODGE MUTUAL WATER |  | T3 | 2025-01-17 20:29
SUBCARRIER COMMUNICATION INC |  | T3 | 2025-01-17 20:29
SUE VOLK |  | T3 | 2025-01-24 01:14
SUMMIT FARM LLC |  | T3 | 2025-01-18 14:35
SUNE DB APNL, LLC |  | Non HFRA, T3, T2 | 2025-01-17 20:29
SUNSHINE GAS PRODUCERS, LLC |  | T3 | 2025-01-17 20:29
T MOBILE USA |  | Non HFRA, T3, T2 | 2025-01-17 19:30
T MOBILE WEST, LLC |  | Non HFRA, T3, T2 | 2025-01-17 19:30
TEHACHAPI CUMMINGS COUNTY WATR |  | T3, T2 | 2025-01-17 20:29
TEMECULA, CITY OF |  | Non HFRA, T3 | 2025-01-18 14:35
TERESA BESERRA TRUST |  | Non HFRA, T3, T2 | 2025-01-17 20:29
THALIA MORENO |  | T3 | 2025-01-18 14:35
THERMAL FARMS LLC |  | T3 | 2025-01-23 01:56
THERMIC MUT WAT CO |  | T3 | 2025-01-17 20:29
THOMAS BRICE |  | T3 | 2025-01-18 14:35
THOMAS CANTERBURY LLC |  | T3 | 2025-01-18 14:35
THOUSAND OAKS, CITY OF |  | T3 | 2025-01-19 14:20
TIMBER CANYON MUTUAL WATER |  | Non HFRA, T3, T2 | 2025-01-18 14:35
TIME WARNER CABLE |  | Non HFRA, T3, T2 | 2025-01-17 19:30
T-MOBILE USA |  | Non HFRA, T3, T2 | 2025-01-17 20:29
TOUCHTEL CORP |  | Non HFRA, T3, T2 | 2025-01-17 20:29
TOURNAMENT HILLS COMMUNITY ASSOCIATION |  | Non HFRA, T3, T2 | 2025-01-19 14:20
TRABUCO CANYON WATER |  | T3 | 2025-01-17 20:29
TRAVIS RISNER |  | Non HFRA, T3, T2 | 2025-01-18 14:35
TRINITY CHRISTIAN CNTR OF SNTA |  |  | 2025-01-17 20:29
TYLER HOUCK |  | T3 | 2025-01-18 14:35
U L B WATER ASSOC |  | T3 | 2025-01-17 19:30
UNITED STATES ARMY CORP OF ENG |  | Non HFRA, T3, T2 | 2025-01-19 14:20
UNITED STATES FOREST SERVICE |  | Non HFRA, T3, T2 | 2025-01-17 19:30
UNITED STATES SECRET SERVICE |  | T3 | 2025-01-17 20:29
UNITED WATER CONSERVATION DIST |  | Non HFRA, T3, T2 | 2025-01-17 20:29
UNIVISION COMMUNICATIONS INC |  |  | 2025-01-17 20:29
UNIVISION RADIO LOS ANGLES,INC |  |  | 2025-01-17 20:29
UPLAND, CITY OF |  | Non HFRA, T3, T2 | 2025-01-19 14:20
US DEPARTMENT OF THE INTERIOR |  | T3 | 2025-01-20 00:42
US HORTICULTURE FARMLAND LLC |  | Non HFRA, T3, T2 | 2025-01-19 14:20
USA BROADCASTING OF SOUTHERN C |  |  | 2025-01-17 20:29
VALENCIA HEIGHTS WATER |  | T3 | 2025-01-18 14:35
VALHALLA WTR ASSN |  | Non HFRA, T3, T2 | 2025-01-17 20:29
VALLEY OF ENCHANTMENT MUT WTR |  | T3 | 2025-01-17 20:29
VALLEY VIEW PARK MUTUAL WATER |  | T3 | 2025-01-17 20:29
VENESS VINEYARDS LLC |  | T3 | 2025-01-24 22:35
VENTURA COUNTY WATERWKS 8 |  | T3 | 2025-01-18 14:35
VENTURA REGIONAL SANITATION DT |  | Non HFRA, T3, T2 | 2025-01-17 20:29
VENTURA, CITY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
VENTURA, COUNTY OF |  | Non HFRA, T3, T2 | 2025-01-17 20:29
VENTURE TECH GROUP |  | Non HFRA, T3, T2 | 2025-01-20 00:12
VEOLIA NORTH AMERICA SERV INC |  | Non HFRA, T3, T2 | 2025-01-22 17:57
VERIZON |  | Non HFRA, T3, T2 | 2025-01-17 20:29
VERIZON WIRELESS |  | Non HFRA, T3, T2 | 2025-01-17 19:30
VICTOR HERNANDEZ |  | Non HFRA, T3, T2 | 2025-01-17 20:29
VILLA PARK, CITY OF |  | Non HFRA, T2 | 2025-01-19 23:59
VYVX, INC |  | Non HFRA, T3, T2 | 2025-01-21 14:42
WAGON TRAIN ROAD LLC |  | T3, T2 | 2025-01-17 20:29
WALNUT VALLEY WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-20 23:39
WATERS RD DMSTC USE |  | Non HFRA, T3 | 2025-01-17 20:29
WEIMING ZHANG |  | T3 | 2025-01-18 14:35
WEST VALLEY WATER DIST |  | Non HFRA, T3, T2 | 2025-01-17 20:29
WESTERN HEIGHTS WATER COMPANY |  | Non HFRA, T2 | 2025-01-21 14:42
WESTERN MUNICIPAL WATER DIST |  | Non HFRA, T3, T2 | 2025-01-18 14:35
WILLIAM KELSEY |  | Non HFRA, T3, T2 | 2025-01-19 14:20
WORLDWIDE TELECOMMUNICATIONS |  | T3, T2 | 2025-01-19 16:21
YERBA BUENA WATER COMPANY |  | T3, T2 | 2025-01-18 14:35
YUCAIPA VALLEY WATER DISTRICT |  | Non HFRA, T3, T2 | 2025-01-19 14:20
YVONNE THOME |  | T3 | 2025-01-20 23:45
ZONE MUTUAL WATER |  | Non HFRA, T3, T2 | 2025-01-19 14:20

## T11
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 06: Local and State Public Safety Partner Engagement
Entities Invited to SCE Emergency Operations Center
Entity | Type
CalOES Warning Center | Public Safety Partners
Cal Fire | Public Safety Partners
California Governor's Office of Emergemcy Services (CalOES) | Public Safety Partners
California Health and Human Services (CHHS) | Public Safety Partners
California Public Utilities Commission (CPUC) | Public Safety Partners
Energy Safety | Public Safety Partners
Kern County OEM | Public Safety Partners
Los Angeles County OEM | Public Safety Partners
Mono County OEM | Public Safety Partners
Orange County OEM | Public Safety Partners
Riverside County OEM | Public Safety Partners
San Bernardino County OEM | Public Safety Partners
Ventura County OEM | Public Safety Partners
1051 MACLAY AVE LLC | Critical Facilities and Critical Infrastructure
A-ALERT COURIER SERVICES INC | Critical Facilities and Critical Infrastructure
ACCELERATED URGENT CARE | Critical Facilities and Critical Infrastructure
ACCUMBENS PROPERTY LLC | Critical Facilities and Critical Infrastructure
ACE ASSOCIATES, LLC | Critical Facilities and Critical Infrastructure
ACOSTA HEATING & AC | Critical Facilities and Critical Infrastructure
ACTON AGUA DULCE SCHOOL DIST | Critical Facilities and Critical Infrastructure
AERA ENERGY LLC | Critical Facilities and Critical Infrastructure
AFP MUTUAL WATER CO | Critical Facilities and Critical Infrastructure
AGUA DULCE AIR PARK LLC | Critical Facilities and Critical Infrastructure
AH4882 LLC | Critical Facilities and Critical Infrastructure
AIR TOUCH CELLULAR | Critical Facilities and Critical Infrastructure
ALL PRO BROADCASTING | Critical Facilities and Critical Infrastructure
ALPINE WATER USERS ASSOCIATION | Critical Facilities and Critical Infrastructure
ALTIS MASTER ASSOCIATION | Critical Facilities and Critical Infrastructure
AM PCS CA INC | Critical Facilities and Critical Infrastructure
AMATURO GP LTD, THE | Critical Facilities and Critical Infrastructure
AMERICAN BROADCASTING COMPANY | Critical Facilities and Critical Infrastructure
AMERICAN TOWER CORPORATION | Critical Facilities and Critical Infrastructure
AMERICAN TOWERS | Critical Facilities and Critical Infrastructure
AMS EVENT RENTALS LLC | Critical Facilities and Critical Infrastructure
AQUA-SERV ENG, INC. | Critical Facilities and Critical Infrastructure
AROWBEAR CO PARK | Critical Facilities and Critical Infrastructure
ARROW BEAR PK CO WATER DIST | Critical Facilities and Critical Infrastructure
ARROWHEAD VILLAS MUTUAL SERV | Critical Facilities and Critical Infrastructure
ASPIRE COMMUNICATIONS LLC | Critical Facilities and Critical Infrastructure
AT&T | Critical Facilities and Critical Infrastructure
AT&T CORPORATION | Critical Facilities and Critical Infrastructure
AT&T INCORPORATED | Critical Facilities and Critical Infrastructure
AT&T MOBILITY | Critical Facilities and Critical Infrastructure
AT&T WIRELESS SERVICES | Critical Facilities and Critical Infrastructure
ATT MOBILITY | Critical Facilities and Critical Infrastructure
AVOTOPIA LLC | Critical Facilities and Critical Infrastructure
B PER ELECTRONICS INC | Critical Facilities and Critical Infrastructure
BAKO LIVING INC | Critical Facilities and Critical Infrastructure
BANNING HEIGHTS WATER | Critical Facilities and Critical Infrastructure
BANNING UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
BANNING, CITY OF | Critical Facilities and Critical Infrastructure
BARTON FLATS CAMP ASSOCIATION | Critical Facilities and Critical Infrastructure
BCP COATINGS, INC | Critical Facilities and Critical Infrastructure
BEAR VALLEY COMM SERV DIST | Critical Facilities and Critical Infrastructure
BEAR VALLEY UNIFIED SCH DIST | Critical Facilities and Critical Infrastructure
BEAUMONT CHERRY VALLEY WATER | Critical Facilities and Critical Infrastructure
BEAUMONT UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
BeMobile, INC | Critical Facilities and Critical Infrastructure
BIG BUS TOURS LOS ANGELES | Critical Facilities and Critical Infrastructure
BIRTHCHOICE/TEMECUL | Critical Facilities and Critical Infrastructure
BLAKE ELEMENTARY | Critical Facilities and Critical Infrastructure
BLANCA TENORIO | Critical Facilities and Critical Infrastructure
BLDG GENERATION INTL SERVICES | Critical Facilities and Critical Infrastructure
BLOCK CROSSFIT LLC | Critical Facilities and Critical Infrastructure
BNSF Railway Company | Critical Facilities and Critical Infrastructure
BOOM RANCH LLC | Critical Facilities and Critical Infrastructure
BRASWELL ENTERPRISES INC | Critical Facilities and Critical Infrastructure
BRAZWELL ENT INC | Critical Facilities and Critical Infrastructure
BRIDGE NEWS, LLC | Critical Facilities and Critical Infrastructure
BRIGHT HOUSE NETWORKS, LLC | Critical Facilities and Critical Infrastructure
BURLINGTON NORTHERN SANTA FE | Critical Facilities and Critical Infrastructure
CA DEPARTMENT OF THE MILITARY | Critical Facilities and Critical Infrastructure
CA DEPT OF CORRECTIONS & REHAB | Critical Facilities and Critical Infrastructure
CABAZON WATER DISTRICT | Critical Facilities and Critical Infrastructure
CALABASAS, CITY OF | Critical Facilities and Critical Infrastructure
CALIFORNIA AMERICAN WATER CO | Critical Facilities and Critical Infrastructure
CALIFORNIA INSTITUTE OF TECH | Critical Facilities and Critical Infrastructure
CALIFORNIA LUTHERAN UNIVERSITY | Critical Facilities and Critical Infrastructure
CALIFORNIA STATE HIGHWY PATROL | Critical Facilities and Critical Infrastructure
CALIFORNIA VIRTUAL ACADEMYS | Critical Facilities and Critical Infrastructure
CALIFORNIA WATER SERVICES, CO | Critical Facilities and Critical Infrastructure
CALLEGUAS MUNICIPAL WATER DIST | Critical Facilities and Critical Infrastructure
CALNEV PIPE LINE CO | Critical Facilities and Critical Infrastructure
CalNRG Operating, LLC | Critical Facilities and Critical Infrastructure
CALTRANS | Critical Facilities and Critical Infrastructure
CAMARILLO, CITY OF | Critical Facilities and Critical Infrastructure
CAMP BARTLETT | Critical Facilities and Critical Infrastructure
CAMPANERO OAKS | Critical Facilities and Critical Infrastructure
CAMROSA WATER DISTRICT | Critical Facilities and Critical Infrastructure
CANYON COUNTRY DIALYSIS LLC | Critical Facilities and Critical Infrastructure
CANYON LAKE HOSPICE INC | Critical Facilities and Critical Infrastructure
CANYON LAKE, CITY OF | Critical Facilities and Critical Infrastructure
CARBON CALIFORNIA COMPANY LLC | Critical Facilities and Critical Infrastructure
CASA DULCE ESTATES | Critical Facilities and Critical Infrastructure
CASTAIC UNION SCHOOL DIST | Critical Facilities and Critical Infrastructure
CEDAR PINES PARK MUTUAL WATER | Critical Facilities and Critical Infrastructure
CHARTER COMMUNICATIONS | Critical Facilities and Critical Infrastructure
CHARTER COMMUNICATIONS HOLDING | Critical Facilities and Critical Infrastructure
CHARTER COMMUNICATIONS INC | Critical Facilities and Critical Infrastructure
CHEM ASSIST | Critical Facilities and Critical Infrastructure
CHERRY VALLEY WATER, CO | Critical Facilities and Critical Infrastructure
CHILTON & LESTE MANAGEMENT | Critical Facilities and Critical Infrastructure
CHINO BASIN DESALTER AUTHORITY | Critical Facilities and Critical Infrastructure
CHINO, CITY OF | Critical Facilities and Critical Infrastructure
CINGULAR WIRELESS | Critical Facilities and Critical Infrastructure
CITY OF GRAND TERRACE | Critical Facilities and Critical Infrastructure
CITY OF MURRIETA | Critical Facilities and Critical Infrastructure
CITY OF YUCAIPA | Critical Facilities and Critical Infrastructure
CK-17, LP | Critical Facilities and Critical Infrastructure
CLEAR WIRE COMMUNICATIONS LLC | Critical Facilities and Critical Infrastructure
CMP ANGLS TRCT LND | Critical Facilities and Critical Infrastructure
COLTON JOINT UNIFIED SCHL DIST | Critical Facilities and Critical Infrastructure
COMMUNICATIONS RELAY, LLC | Critical Facilities and Critical Infrastructure
COMMUNITY TV OF SO CAL INC | Critical Facilities and Critical Infrastructure
COMSAT | Critical Facilities and Critical Infrastructure
CONEJO VALLEY UNIFIED SCHOOL | Critical Facilities and Critical Infrastructure
CORONA, CITY OF | Critical Facilities and Critical Infrastructure
CORONA-NORCO SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
COSPHERIC LLC | Critical Facilities and Critical Infrastructure
COSTA DE ORO TV INC | Critical Facilities and Critical Infrastructure
COUNTY OF KERN | Critical Facilities and Critical Infrastructure
COWBOYS FOR A CAUSE | Critical Facilities and Critical Infrastructure
COX COMMUNICATIONS CALIF, LLC | Critical Facilities and Critical Infrastructure
COX COMMUNICATIONS INC | Critical Facilities and Critical Infrastructure
COX ENTERPRISES INC | Critical Facilities and Critical Infrastructure
CPG PARTNERS LP | Critical Facilities and Critical Infrastructure
CR & R INCORPORATED | Critical Facilities and Critical Infrastructure
CRESCENTA VALLEY COUNTY WATER | Critical Facilities and Critical Infrastructure
CRESTLINE LAKE ARROWHEAD WATER | Critical Facilities and Critical Infrastructure
CRESTLINE SANITATION DISTRICT | Critical Facilities and Critical Infrastructure
CRESTLINE VILLAGE WATER DIST | Critical Facilities and Critical Infrastructure
CROWN CASTLE | Critical Facilities and Critical Infrastructure
CUCAMONGA VALLEY WATER DIST | Critical Facilities and Critical Infrastructure
CVIN, LLC | Critical Facilities and Critical Infrastructure
D.R. HORTON, INC | Critical Facilities and Critical Infrastructure
DAN ADIVI | Critical Facilities and Critical Infrastructure
DAVITA INC | Critical Facilities and Critical Infrastructure
DCOR, LLC | Critical Facilities and Critical Infrastructure
DEL ORO WATER COMPANY | Critical Facilities and Critical Infrastructure
DELL HOME HEALTH CARE INC | Critical Facilities and Critical Infrastructure
DEPARTMENT OF AGRICULTURE | Critical Facilities and Critical Infrastructure
DEPARTMENT OF MOTOR VEHICLES | Critical Facilities and Critical Infrastructure
DISH WIRELESS | Critical Facilities and Critical Infrastructure
DISH WIRELESS HOLDING, LLC | Critical Facilities and Critical Infrastructure
DORTEN ENTERPRIZES | Critical Facilities and Critical Infrastructure
DOWN-TO-EARTH ECO LLC | Critical Facilities and Critical Infrastructure
DR HORTON INC | Critical Facilities and Critical Infrastructure
DR HORTON, INC | Critical Facilities and Critical Infrastructure
DURA COAT PRODUCT I | Critical Facilities and Critical Infrastructure
DWR - STATE WATER PROJECTS | Critical Facilities and Critical Infrastructure
EAST ORANGE CO WATER DISTRICT | Critical Facilities and Critical Infrastructure
EAST VALLEY WATER DISTRICT | Critical Facilities and Critical Infrastructure
EASTERN MUNICIPAL WATER DISTRICT | Critical Facilities and Critical Infrastructure
EDUCATIONAL MEDIA FOUNDATION | Critical Facilities and Critical Infrastructure
ELECTRIC LIGHT WAVE | Critical Facilities and Critical Infrastructure
ELITE ACADEMIC ACADEMY | Critical Facilities and Critical Infrastructure
ELSINORE VALLEY MUN WATER DIST | Critical Facilities and Critical Infrastructure
EMANUEL ALVAREZ GLEMKSTEIN | Critical Facilities and Critical Infrastructure
ENTRAVISION COMMUNICATIONS CORP | Critical Facilities and Critical Infrastructure
EPWORTH WATER GROUP | Critical Facilities and Critical Infrastructure
ETIWANDA SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
FALCON HOLDING GROUP LP | Critical Facilities and Critical Infrastructure
FALLSVALE SERVICE CO | Critical Facilities and Critical Infrastructure
FARM MUTUAL WATER, THE | Critical Facilities and Critical Infrastructure
FEDERAL AVIATION ADMINISTRATIO | Critical Facilities and Critical Infrastructure
FEDERAL BUREAU OF INVSTIGATION | Critical Facilities and Critical Infrastructure
FEDEX FREIGHT WEST | Critical Facilities and Critical Infrastructure
FEDEX GROUND | Critical Facilities and Critical Infrastructure
FENIX HOME HEALTH, LLC | Critical Facilities and Critical Infrastructure
FERN VALLEY WATER DISTRICT | Critical Facilities and Critical Infrastructure
FERNANDENO TATAVIAM BAND OF | Critical Facilities and Critical Infrastructure
FILLMORE IRRIGATION COMPANY | Critical Facilities and Critical Infrastructure
FILLMORE UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
FILLMORE, CITY OF | Critical Facilities and Critical Infrastructure
FLABOB AIRPORT LLC | Critical Facilities and Critical Infrastructure
FONTANA UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
FONTANA UNION WATER | Critical Facilities and Critical Infrastructure
FONTANA, CITY OF | Critical Facilities and Critical Infrastructure
FOREST PK MUTWATER | Critical Facilities and Critical Infrastructure
FOX TELEVISION STATIONS INC | Critical Facilities and Critical Infrastructure
FRESENIUS MEDICAL CARE AG | Critical Facilities and Critical Infrastructure
FRONTIER COMMUNICATIONS | Critical Facilities and Critical Infrastructure
FRONTIER COMMUNICATIONS CORP | Critical Facilities and Critical Infrastructure
FRONTIER COMMUNICATIONS PARENT INC | Critical Facilities and Critical Infrastructure
FULLER FALLS MUTUAL WTR CO | Critical Facilities and Critical Infrastructure
GLENDALE ELECTRONIC | Critical Facilities and Critical Infrastructure
GLENDALE UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
GLENNVILLE MUTUAL WATER CO | Critical Facilities and Critical Infrastructure
GLOBAL SIGNAL INC | Critical Facilities and Critical Infrastructure
Golden State Water Co. | Critical Facilities and Critical Infrastructure
Golden State Water Company | Critical Facilities and Critical Infrastructure
GREER RANCH COMMUNITY ASSOC | Critical Facilities and Critical Infrastructure
GTE MOBILENET INCORPORATED | Critical Facilities and Critical Infrastructure
H G N CORONA PARTNERS LLC | Critical Facilities and Critical Infrastructure
HARRIS CORPORATION | Critical Facilities and Critical Infrastructure
HEMET UNIFIED SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
HERRITAGE POINTE & PLACE COMM ASSO | Critical Facilities and Critical Infrastructure
HIGH VALLEYS WATER DISTRICT | Critical Facilities and Critical Infrastructure
HILLSIDE SCHOOL & LEARNING CTR | Critical Facilities and Critical Infrastructure
HOSPICE CARE OF THE VALLEY | Critical Facilities and Critical Infrastructure
HYDAM GROUP INC | Critical Facilities and Critical Infrastructure
IDYLLWILD ARTS FOUNDATION | Critical Facilities and Critical Infrastructure
IDYLLWILD FIRE DEPT | Critical Facilities and Critical Infrastructure
IDYLLWILD WATER DISTRICT | Critical Facilities and Critical Infrastructure
ILEAD AGUA DULCE CORP | Critical Facilities and Critical Infrastructure
IMRAE CORPORATION | Critical Facilities and Critical Infrastructure
INLAND EMPIRE UTILITIES AGENCY | Critical Facilities and Critical Infrastructure
INTELSAT CORPORATION | Critical Facilities and Critical Infrastructure
INTERNAL REVENUE SERVICE | Critical Facilities and Critical Infrastructure
IRVINE RANCH WATER DISTRICT | Critical Facilities and Critical Infrastructure
IV TECH CHARTER SCHOOL | Critical Facilities and Critical Infrastructure
J5T RANCH, LLC | Critical Facilities and Critical Infrastructure
JAKE AND LILLY, LLC | Critical Facilities and Critical Infrastructure
JESSICA JIMENEZ | Critical Facilities and Critical Infrastructure
JURUPA COMMUNITY SERVICES DISTRICT | Critical Facilities and Critical Infrastructure
JURUPA UNIFIED SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
JURUPA VALLEY, CITY OF | Critical Facilities and Critical Infrastructure
K2TOWERSIII LLC | Critical Facilities and Critical Infrastructure
KARESAFE HEALTH SOLUTIONS, INC | Critical Facilities and Critical Infrastructure
KB HOME | Critical Facilities and Critical Infrastructure
KB HOMES | Critical Facilities and Critical Infrastructure
KB HOMES COASTAL INC | Critical Facilities and Critical Infrastructure
KCBS/KCAL | Critical Facilities and Critical Infrastructure
KEY MUTUAL WATER CO | Critical Facilities and Critical Infrastructure
KIERTON INC. | Critical Facilities and Critical Infrastructure
Kinder Morgan | Critical Facilities and Critical Infrastructure
KINNELOA IRRIGATION | Critical Facilities and Critical Infrastructure
KOCE-TV/DT | Critical Facilities and Critical Infrastructure
KPWR RADIO | Critical Facilities and Critical Infrastructure
KSGN INC | Critical Facilities and Critical Infrastructure
KTLA INCORPORATED | Critical Facilities and Critical Infrastructure
KVMD TV | Critical Facilities and Critical Infrastructure
LA CANADA IRRIGATION DISTRICT | Critical Facilities and Critical Infrastructure
LA CANADA UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
LA CO W VECTOR CONTROL DIST | Critical Facilities and Critical Infrastructure
LAGUNA BEACH COUNTY WTR DIST | Critical Facilities and Critical Infrastructure
LAGUNA BEACH UNIFIED SCH DIST | Critical Facilities and Critical Infrastructure
LAGUNA BEACH, CITY OF | Critical Facilities and Critical Infrastructure
LAKE ARROWHEAD C S D | Critical Facilities and Critical Infrastructure
LAKE ELSINORE UNIFIED SCHOOL D | Critical Facilities and Critical Infrastructure
LAKE ELSINORE, CITY OF | Critical Facilities and Critical Infrastructure
LAKE HEMET MUNICIPAL WATER DIS | Critical Facilities and Critical Infrastructure
LAS VIRGENES MUNICIPAL WTR DST | Critical Facilities and Critical Infrastructure
LAS VIRGENES UNIFIED SCHL DST | Critical Facilities and Critical Infrastructure
LAZER BROADCASTING | Critical Facilities and Critical Infrastructure
LDDS WORLDCOM | Critical Facilities and Critical Infrastructure
LENNAR HOMES OF CALIF INC | Critical Facilities and Critical Infrastructure
LEVINE, SAUL R DBA | Critical Facilities and Critical Infrastructure
LIBERMAN BROADCASTING, INC | Critical Facilities and Critical Infrastructure
LINNS VALLEY POSO FLAT USD | Critical Facilities and Critical Infrastructure
LODESTAR TOWERS, INC | Critical Facilities and Critical Infrastructure
LOMA LINDA BROADCSTNG NTK, INC | Critical Facilities and Critical Infrastructure
LOMA LINDA SURGICAL INSTITUTE | Critical Facilities and Critical Infrastructure
LOMA LINDA, CITY OF | Critical Facilities and Critical Infrastructure
LOS ANGELES COUNTY FIRE DEPT | Critical Facilities and Critical Infrastructure
LOS ANGELES COUNTY ISD | Critical Facilities and Critical Infrastructure
LOS ANGELES COUNTY PUBLIC WORK | Critical Facilities and Critical Infrastructure
LOS ANGELES DEPT OF WTR & POWR | Critical Facilities and Critical Infrastructure
LOS ANGELES UNIFIED SCHL DIST | Critical Facilities and Critical Infrastructure
LOS ANGELES, CITY OF | Critical Facilities and Critical Infrastructure
LOTUS OXNARD CORPORATION | Critical Facilities and Critical Infrastructure
MABROUK LEGACY LLC | Critical Facilities and Critical Infrastructure
MALIBU CANYON URGENT CARE | Critical Facilities and Critical Infrastructure
MALIBU, CITY OF | Critical Facilities and Critical Infrastructure
MAURAN AMBULANCE SERVICE, INC | Critical Facilities and Critical Infrastructure
MCSWEENY FARMS COMMUNITY ASSOC | Critical Facilities and Critical Infrastructure
MEADOWBROOK POST-ACUTE LLC | Critical Facilities and Critical Infrastructure
MEDIACOM, LLC | Critical Facilities and Critical Infrastructure
MENIFEE UNION ELEMENTARY SCHOOL DIST | Critical Facilities and Critical Infrastructure
MENIFEE UNION SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
MESIVTA CORP | Critical Facilities and Critical Infrastructure
METROLINK | Critical Facilities and Critical Infrastructure
METROPOLITAN WATER DISTRICT | Critical Facilities and Critical Infrastructure
MFE WATER WELL | Critical Facilities and Critical Infrastructure
MISSION SPRINGS WATER DISTRICT | Critical Facilities and Critical Infrastructure
MOBILE RELAY ASSOC | Critical Facilities and Critical Infrastructure
MOBILITIE INVESTMENTS II LLC | Critical Facilities and Critical Infrastructure
MOBILITIE LLC | Critical Facilities and Critical Infrastructure
MONTES, ABEL | Critical Facilities and Critical Infrastructure
MONTESSORI AT THE PARK | Critical Facilities and Critical Infrastructure
MOORPARK UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
MOORPARK, CITY OF | Critical Facilities and Critical Infrastructure
MORONGO BAND MISSION INDIANS | Critical Facilities and Critical Infrastructure
MOUNTAIN INVESTMENT | Critical Facilities and Critical Infrastructure
MOUNTAIN REPEATER ASSOC, INC | Critical Facilities and Critical Infrastructure
MSP HEAT AND AIR | Critical Facilities and Critical Infrastructure
MT BALDY FIRE DEPT | Critical Facilities and Critical Infrastructure
MT BALDY JOINT ELEMENTARY SD | Critical Facilities and Critical Infrastructure
MT R R H INC | Critical Facilities and Critical Infrastructure
MUPU ELEMENTARY SCH DIST | Critical Facilities and Critical Infrastructure
MURRIETA VALLEY UNIFIED SD | Critical Facilities and Critical Infrastructure
NATIONAL FARM WORKERS SERVICE | Critical Facilities and Critical Infrastructure
NBC UNIVERSAL INCORPORATED | Critical Facilities and Critical Infrastructure
NBC UNIVERSAL LLC | Critical Facilities and Critical Infrastructure
NEPTUNE WATER GROUP | Critical Facilities and Critical Infrastructure
NEW VISTA HEALTH SERVICES LLC | Critical Facilities and Critical Infrastructure
NEWBURY PARK ADVENTIST ACADEMY | Critical Facilities and Critical Infrastructure
NEWHALL SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
NEXTEL COMMUNICATIONS, INC | Critical Facilities and Critical Infrastructure
NEXUS HOSPICE CARE INC | Critical Facilities and Critical Infrastructure
NINAS HOME HEALTH CARE | Critical Facilities and Critical Infrastructure
NUEVO WATER CO | Critical Facilities and Critical Infrastructure
NUVIEW UNION SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
OAK PARK UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
OAKGLEN DOM WATER | Critical Facilities and Critical Infrastructure
OASIS KAINGA INC | Critical Facilities and Critical Infrastructure
OJAI OIL COMPANY | Critical Facilities and Critical Infrastructure
OJAI VALLEY SANITATION DIST | Critical Facilities and Critical Infrastructure
ORANGE COUNTY FIRE AUTHORITY | Critical Facilities and Critical Infrastructure
ORANGE COUNTY TRANSPORTATION AUTHORITY | Critical Facilities and Critical Infrastructure
ORANGE EMPIRE RAILWAY MUSEUM | Critical Facilities and Critical Infrastructure
ORANGE, COUNTY OF | Critical Facilities and Critical Infrastructure
ORO GRANDE SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
OXNARD, CITY OF | Critical Facilities and Critical Infrastructure
P W OIL CO | Critical Facilities and Critical Infrastructure
PACIFIC BELL CORP | Critical Facilities and Critical Infrastructure
PACIFIC GAS & ELECTRIC COMPANY | Critical Facilities and Critical Infrastructure
PACIFICA FOUNDATION | Critical Facilities and Critical Infrastructure
PALO VERDE IRRIGATION DISTRICT | Critical Facilities and Critical Infrastructure
PAN HTS PROP OWNERS | Critical Facilities and Critical Infrastructure
PANORAMA PARK | Critical Facilities and Critical Infrastructure
PATRIOT RESOURCES, LLC | Critical Facilities and Critical Infrastructure
PBF ENERGY COMPANY LLC | Critical Facilities and Critical Infrastructure
PEDLEY LAND COMPANY LLC | Critical Facilities and Critical Infrastructure
PERRIS ELEMENTARY SCHOOL DIST | Critical Facilities and Critical Infrastructure
PERRIS UNION HIGH SCHOOL DIST | Critical Facilities and Critical Infrastructure
PERRIS, CITY OF | Critical Facilities and Critical Infrastructure
PINE COVE WATER DISTRICT | Critical Facilities and Critical Infrastructure
PINNACLE AT WOODRANCH | Critical Facilities and Critical Infrastructure
PLEASANT VALLEY SCHOOL DIST | Critical Facilities and Critical Infrastructure
POSO PARK ASSOC | Critical Facilities and Critical Infrastructure
PRESERVE MASTER MAINTENANCE CO | Critical Facilities and Critical Infrastructure
PRESIDIO WH PIRU 169 LLC | Critical Facilities and Critical Infrastructure
PRINCE OF PEACE HOME CARE SERVICES LLC | Critical Facilities and Critical Infrastructure
PUBLIC SAFETY COMM DIV (PSCD) | Critical Facilities and Critical Infrastructure
Q & M PHYSICAN ASSISTANT CORP | Critical Facilities and Critical Infrastructure
Qualia The School For Deeper Learning | Critical Facilities and Critical Infrastructure
QUALITY AG INC | Critical Facilities and Critical Infrastructure
QUALITY LONG TERM CARE INC | Critical Facilities and Critical Infrastructure
R C T C | Critical Facilities and Critical Infrastructure
RACE COMMUNICATION | Critical Facilities and Critical Infrastructure
RANCHO CAL WATER DISTRICT | Critical Facilities and Critical Infrastructure
Rancho GG Western Wear | Critical Facilities and Critical Infrastructure
REDLANDS UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
REDLANDS, CITY OF | Critical Facilities and Critical Infrastructure
REGENTS OF THE UCLA | Critical Facilities and Critical Infrastructure
REMOTE COMMUNICATION SYST INC | Critical Facilities and Critical Infrastructure
RESEARCH FOR LIFE LLC | Critical Facilities and Critical Infrastructure
RESPONSIBLE MEDICAL SOLUTIONS | Critical Facilities and Critical Infrastructure
REVCHEM COMPOSITES, INC | Critical Facilities and Critical Infrastructure
RIALTO UNIFIED SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
RIALTO, CITY OF | Critical Facilities and Critical Infrastructure
RICHMOND AMERICAN HOMES | Critical Facilities and Critical Infrastructure
RICHMOND AMERICAN HOMES MRYLND | Critical Facilities and Critical Infrastructure
RIM OF THE WORLD UNIF SCH DIST | Critical Facilities and Critical Infrastructure
RIVER SPRINGS CHARTER SCHOOL | Critical Facilities and Critical Infrastructure
RIVERSIDE COUNTY OFC EDUCATION | Critical Facilities and Critical Infrastructure
RIVERSIDE COUNTY TRANS | Critical Facilities and Critical Infrastructure
RIVERSIDE HIGHLAND WATER CO | Critical Facilities and Critical Infrastructure
RIVERSIDE TELEPORT CORPORATION | Critical Facilities and Critical Infrastructure
RIVERSIDE, CITY OF | Critical Facilities and Critical Infrastructure
RIVERSIDE, COUNTY OF | Critical Facilities and Critical Infrastructure
RODNEY AUTO SERVICE INC | Critical Facilities and Critical Infrastructure
ROMOLAND SCHOOL DISTRICT | Critical Facilities and Critical Infrastructure
RUBIDOUX COMMUNITY SERVICES DISTRICT | Critical Facilities and Critical Infrastructure
RUNNING SPRINGS WATER DISTRICT | Critical Facilities and Critical Infrastructure
SADDLEBACK VALLEY UNIF SCH DST | Critical Facilities and Critical Infrastructure
SAGE MOUNTAIN SENIOR HOUSING P | Critical Facilities and Critical Infrastructure
SAI BALAJI RVP | Critical Facilities and Critical Infrastructure
SAN ANTONIO WATER COMPANY INC | Critical Facilities and Critical Infrastructure
SAN BERNARDINO CITY UNIF SCH | Critical Facilities and Critical Infrastructure
SAN BERNARDINO MTNS COMM HOSP | Critical Facilities and Critical Infrastructure
SAN BERNARDINO WATER DEPT | Critical Facilities and Critical Infrastructure
SAN BERNARDINO, CITY OF | Critical Facilities and Critical Infrastructure
SAN BERNARDINO, COUNTY OF | Critical Facilities and Critical Infrastructure
SAN CAYETANO WATER CO | Critical Facilities and Critical Infrastructure
SAN DIEGO GAS & ELECTRIC | Critical Facilities and Critical Infrastructure
SAN DIEGO STATE UNIVERSITY | Critical Facilities and Critical Infrastructure
SAN FERNANDO, CITY OF | Critical Facilities and Critical Infrastructure
SAN GABRIEL VALLEY WATER CO | Critical Facilities and Critical Infrastructure
SAN MANUEL BAND OF INDIANS | Critical Facilities and Critical Infrastructure
SAND CANYON WATER GROUP | Critical Facilities and Critical Infrastructure
SANTA ANA WATERSHED PROJECT | Critical Facilities and Critical Infrastructure
SANTA CLARITA VALLEY WTR AGNCY | Critical Facilities and Critical Infrastructure
SANTA CLARITA, CITY OF | Critical Facilities and Critical Infrastructure
SANTA MARGARITA WATER DISTRICT | Critical Facilities and Critical Infrastructure
SANTA MONICA MALIBU UNIFIED | Critical Facilities and Critical Infrastructure
SANTA PAULA UNIFIED SCH DIST | Critical Facilities and Critical Infrastructure
SANTA PAULA, CITY OF | Critical Facilities and Critical Infrastructure
SENIOR JOY INC. | Critical Facilities and Critical Infrastructure
SESPE AGRI WATER CO | Critical Facilities and Critical Infrastructure
SEVLASER ASTHETICS, LLC | Critical Facilities and Critical Infrastructure
Shadow Wolf Energy LLC | Critical Facilities and Critical Infrastructure
SILENT SPRINGS LLC | Critical Facilities and Critical Infrastructure
SIMI VALLEY HOSPITAL | Critical Facilities and Critical Infrastructure
SIMI VALLEY UNIFIED SCHOOL DIS | Critical Facilities and Critical Infrastructure
SIMI VALLEY, CITY OF | Critical Facilities and Critical Infrastructure
SIMS | Critical Facilities and Critical Infrastructure
SNOWCREST HEIGHTS IMPRVMT ASSC | Critical Facilities and Critical Infrastructure
So Cal Gas | Critical Facilities and Critical Infrastructure
SO MTN MUTUAL WATER | Critical Facilities and Critical Infrastructure
SOBOBA BAND OF LUISENO INDIANS | Critical Facilities and Critical Infrastructure
SOUTH MOUNTAIN WATER CO | Critical Facilities and Critical Infrastructure
SOUTHERN CALIFORNIA EDISON CO | Critical Facilities and Critical Infrastructure
SOUTHERN CALIFORNIA GAS CO | Critical Facilities and Critical Infrastructure
SOUTHERN PACIFIC CO | Critical Facilities and Critical Infrastructure
SOUTHERN PACIFIC PIPELINES | Critical Facilities and Critical Infrastructure
SPECIAL OLYMPICS SOUTHERN CAL | Critical Facilities and Critical Infrastructure
SPECTRASITE COMMUNICATION INC. | Critical Facilities and Critical Infrastructure
SPRINT COMMUNICATIONS CO LP | Critical Facilities and Critical Infrastructure
SPRINT NEXTEL | Critical Facilities and Critical Infrastructure
SPRINT PCS ASSETS | Critical Facilities and Critical Infrastructure
SPRINT TELEPHONY PCS L.P | Critical Facilities and Critical Infrastructure
SPRINT UTILITIES | Critical Facilities and Critical Infrastructure
SPV WATER CO | Critical Facilities and Critical Infrastructure
ST JAMES CATHOLIC CHURCH | Critical Facilities and Critical Infrastructure
ST JAMES SCHOOL | Critical Facilities and Critical Infrastructure
ST JOHN THE EVANGELIST CHURCH | Critical Facilities and Critical Infrastructure
STALLION SPRINGS C S D | Critical Facilities and Critical Infrastructure
SUGARLOAF MUTUAL WATER | Critical Facilities and Critical Infrastructure
SUGARLOAF VILLAGE MUTUAL | Critical Facilities and Critical Infrastructure
SULPHUR SPRINGS SCHOOL DIST | Critical Facilities and Critical Infrastructure
SUMMIT FARM LLC | Critical Facilities and Critical Infrastructure
SUNE DB APNL, LLC | Critical Facilities and Critical Infrastructure
SUNSHINE GAS PRODUCERS, LLC | Critical Facilities and Critical Infrastructure
T O I D C | Critical Facilities and Critical Infrastructure
TANA HOSPICE CARE | Critical Facilities and Critical Infrastructure
TEHACHAPI CUMMINGS COUNTY WATR | Critical Facilities and Critical Infrastructure
TEHACHAPI UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
TEMECULA, CITY OF | Critical Facilities and Critical Infrastructure
TERESA BESERRA TRUST | Critical Facilities and Critical Infrastructure
TERMO COMPANY, THE | Critical Facilities and Critical Infrastructure
The City of Hemet | Critical Facilities and Critical Infrastructure
THE KNOLLS LEARNING STUDIO, CORP | Critical Facilities and Critical Infrastructure
THERMIC MUT WAT CO | Critical Facilities and Critical Infrastructure
THOMAS AQUINAS COLLEGE | Critical Facilities and Critical Infrastructure
THOMAS CANTERBURY LLC | Critical Facilities and Critical Infrastructure
THOMPSON OIL CO INC | Critical Facilities and Critical Infrastructure
THOUSAND OAKS, CITY OF | Critical Facilities and Critical Infrastructure
TIMBER CANYON MUTUAL WATER | Critical Facilities and Critical Infrastructure
TIME WARNER CABLE | Critical Facilities and Critical Infrastructure
TIVOLI COVE HOA | Critical Facilities and Critical Infrastructure
T-MOBILE US, INC | Critical Facilities and Critical Infrastructure
T-MOBILE USA | Critical Facilities and Critical Infrastructure
T-Mobile USA Inc | Critical Facilities and Critical Infrastructure
TOUCHTEL CORP | Critical Facilities and Critical Infrastructure
TOURNAMENT HILLS COMMUNITY ASSOCIATION | Critical Facilities and Critical Infrastructure
TRABUCO CANYON WATER | Critical Facilities and Critical Infrastructure
TRANS CORRIDOR AGENCY | Critical Facilities and Critical Infrastructure
TRINITY CHRISTIAN CNTR OF SNTA | Critical Facilities and Critical Infrastructure
TULARE, COUNTY OF | Critical Facilities and Critical Infrastructure
TW TELECOM INC | Critical Facilities and Critical Infrastructure
U C SANTA BARBARA | Critical Facilities and Critical Infrastructure
U L B WATER ASSOC | Critical Facilities and Critical Infrastructure
UNION PACIFIC RAILROAD CO | Critical Facilities and Critical Infrastructure
UNITED STATES ARMY CORP OF ENG | Critical Facilities and Critical Infrastructure
UNITED STATES SECRET SERVICE | Critical Facilities and Critical Infrastructure
UNITED WATER CONSERVATION DIST | Critical Facilities and Critical Infrastructure
UNIVISION COMMUNICATIONS INC | Critical Facilities and Critical Infrastructure
UNIVISION RADIO LOS ANGLES,INC | Critical Facilities and Critical Infrastructure
UPLAND, CITY OF | Critical Facilities and Critical Infrastructure
US DEPARTMENT OF THE INTERIOR | Critical Facilities and Critical Infrastructure
VAL VERDE UNIFIED SCHOOL DIST | Critical Facilities and Critical Infrastructure
VALHALLA WTR ASSN | Critical Facilities and Critical Infrastructure
VALLEY OF ENCHANTMENT MUT WTR | Critical Facilities and Critical Infrastructure
VENTURA COUNTY COMM COLL DIST | Critical Facilities and Critical Infrastructure
Ventura Regional Sanitation District | Critical Facilities and Critical Infrastructure
VENTURA REGIONAL SANITATION DT | Critical Facilities and Critical Infrastructure
VENTURA, CITY OF | Critical Facilities and Critical Infrastructure
VERIZON | Critical Facilities and Critical Infrastructure
VERIZON COMMUNICATIONS INC | Critical Facilities and Critical Infrastructure
VERIZON WIRELESS | Critical Facilities and Critical Infrastructure
VIEWPOINT EDUCATION | Critical Facilities and Critical Infrastructure
WAGON TRAIN ROAD LLC | Critical Facilities and Critical Infrastructure
WATERS RD DMSTC USE | Critical Facilities and Critical Infrastructure
WEST VALLEY WATER DIST | Critical Facilities and Critical Infrastructure
WESTCHEM INC | Critical Facilities and Critical Infrastructure
WESTERN MUNICIPAL WATER DIST | Critical Facilities and Critical Infrastructure
WILLIAM S HART UNION H S DIST | Critical Facilities and Critical Infrastructure
WILMON CORPORATION | Critical Facilities and Critical Infrastructure
WOODCREST CHRISTIAN SCHOOL | Critical Facilities and Critical Infrastructure
YAOWARATTANA, DDS, INC. | Critical Facilities and Critical Infrastructure
YERBA BUENA WATER COMPANY | Critical Facilities and Critical Infrastructure
Yucaipa Valley Water District | Critical Facilities and Critical Infrastructure
ZONE MUTUAL WATER | Critical Facilities and Critical Infrastructure

## T12
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 07: Complaints and Claims
Count and Nature of Complaints Received
Nature of Complaints | Number of Complaints
PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS events, Including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 486
Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern | 91
Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, REST/DAM sites (as applicable) | 118
Outreach/Assistance Including, but not limited to complaints regarding community resource centers, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS | 26
General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS event and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 641
Total | 1362

## T13
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 07: Complaints and Claims
Count and Type of Claims Received
Description of Claims | Number of Claims
Food loss only | 112
Property Damage | 9
Food loss and property damage | 1
Evacuation Cost | 0
Business Interruption / Economic Loss | 6
Unspecified | 4
Total | 132

## T14
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 08: Power Restoration Timeline
Circuits Requiring more than 24 hours to restore
Circuit Name | Reason the utility was unable to restore the circuit within 24 hours
ANGUS | Continued high winds and the need for daylight air patrol delayed re-energization
ANTON | Continued high winds and the need for daylight air patrol delayed re-energization
BOOTLEGGER | Continued high winds caused unsafe air patrol conditions resulted in a delay in re-energization
BROADCAST | Continued high winds and the need for daylight air patrol delayed re-energization
CALSTATE | Continued high winds delayed re-energization
CLARINET | Continued high winds, need for daylight air patrol, and Federal Aviation Administration (FAA) Temporary Flight Restrictions (TFR) delayed re-energization
KINSEY | The need for daylight air patrol delayed re-energization
LIMITED | Continued high winds and the need for daylight air patrol delayed re-energization
MAMBA | The need for daylight air patrol delayed re-energization
OBSERVATORY | Continued high winds and the need for daylight air patrol delayed re-energization
RED BOX | Continued high winds and the need for daylight air patrol delayed re-energization
RIM | The need for daylight patrol and access issues delayed re-energization
SAND CANYON | Continued high winds caused unsafe air patrol conditions resulted in a delay in re-energization
TIVO | Continued high winds and the need for daylight air patrol delayed re-energization
JARVIS | Continued high winds and the need for daylight air patrol delayed re-energization

## T15
SCE Post-Event Report Data
January 17, 2025 to January 27, 2025
SECTION 09: Community Resource Centers
Community Resource Center Address
Address | Location Type | Describe the assistance available | Hours of Operations1 (Date / Time) | Number of Visitors
Golden Hills Community Center 21415 Reeves St. Tehachapi, CA 93561 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, blankets, firewood and customer Resiliency Kits. | 1/20/2025 - 1/21/2025 8AM to 10PM Reopened: 1/23/2025 1:30pm to 10PM 1/24/2025 8AM to 2PM | 17
Agua Dulce Women's Club 33201 Agua Dulce Canyon Rd. Agua Dulce, CA 91390 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, blankets, firewood, gallon water bottles and customer Resiliency Kits. | 1/20/2025 - 1/25/2025 8AM to 10PM 1/26/2025 8AM to 7PM | 242
Calabasas Civic Center 200 Civic Way Calabasas, CA 91301 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 8AM to 10PM Staff relocated to Calabasas Community Center | 18
Calabasas Community Center 227040 Malibu Hills Rd. Calabasas, CA 91301 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/21/2025 - 1/24/2025 8AM to 10PM 1/25/2025 8AM to 6PM | 928
Palmdale Oasis Park and Recreation Center 3850 E. Ave. S. Palmdale, CA 93550 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/24/2025 7pm to 10pm 1/25/2025 8AM to 6PM | 13
Residence Inn - Stevenson Ranch 25320 The Old Rd. Stevenson Ranch, CA 91381 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/24/2025 8AM to 10PM 1/25/25 8AM to 6PM | 7
Second Baptist Church of Monrovia 925 S. Shamrock Ave. Monrovia, CA 91016 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, blankets and customer Resiliency Kits. | 1/20/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 2PM Staff relocated to staff Palmdale site | 40
Benton Community Center 58869 CA-120 Benton, CA 93512 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, blankets, firewood and customer Resiliency Kits. | 1/22/2025 - 1/22/2025 8AM to 7PM | 4
Courtyard by Marriott 27492 Portola Pkwy. Foothill Ranch, CA 92610 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, and customer Resiliency Kits. | 1/20/2025 - 1/24/2025 8AM to 10PM 1/25/2025 8AM to 7PM | 7
Cabazon Community Center/James A. Venable Community Center 50390 Carmen Ave. Cabazon, CA 92230 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, and customer Resiliency Kits. | 1/20/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 4PM | 222
City of Perris Senior Center 100 N D St. Perris, CA 92570 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 7:30PM | 84
Elks Lodge #2591 33700 Mission Trail Wildomar, CA 92595 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, blankets and customer Resiliency Kits. | 1/20/2025 - 1/24/2025 8AM to 10PM 1/24/2025 8AM to 7:30PM | 50
Jurupa Valley Resource Center 8300 Limonite Avenue, Suite F Jurupa, CA 92509 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/21/2025 - 1/24/2025 10:30 AM to 10PM 1/23/2025 8AM to 10PM 1/24/2025 8AM to 7:30PM | 108
San Jacinto Community Center 625 S. Pico Ave. San Jacinto, CA 92583 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/21/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 7:30PM | 68
Jessie Turner Health & Fitness Community Center 15556 Summit Ave. Fontana, CA 92336 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/25/2025 8AM to 10PM 1/26/2025 8AM to 2PM | 90
Robert Hootman Senior Community Center 2929 Running Springs School Rd. Running Springs, CA 92391 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms, blankets, firewood and customer Resiliency Kits. | 1/20/2025 - 1/24/2025 8AM to 10PM 1/25/2025 8AM to 5PM Site closed early due to unsafe driving conditions for staff | 411
Yucaipa Community Center 34900 Oak Glen Rd. Yucaipa, CA 92399 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 7:30PM | 1269
Arroyo Vista Recreation Center, Magnolia Room 4550 Tierra Rejada Rd. Moorpark, CA 93021 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 9PM | 27
Fillmore Active Adult and Community Center 533 Santa Clara St. Fillmore, CA 93015 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/22/2025 8AM to 1:10PM Closed due to Hughes fire, safety and high AQI readngs (>169) | 72
Thousand Oaks Inn 75 W Thousand Oaks Blvd. Thousand Oaks, CA 91360 | CRC-Indoor | Small portable device charging (such as a cell phone, laptop, and small medical devices), chairs, seasonal cooling and heating, PSPS information, snacks, water, ice or ice vouchers, ADA compliant restrooms and customer Resiliency Kits. | 1/20/2025 - 1/23/2025 8AM to 10PM 1/24/2025 8AM to 4PM | 74