## Tracking2013 by Month (hidden)
2013 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 5 | 4 | 3 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 4 |  |  | 32 | 32
Amber Goal - Lowest end of range* | 7 | 5 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 4 | 5 |  |  | 42 | 42
Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 3 | 0 |  |  | 31 | 31
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 |  |  | 6 | 6
Actual - HP Distribution Mains | 4 | 1 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 9 | 9
Goal - LP Distribution | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
Actual - LP Distribution | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  |  | 3 | 3
Goal - Distribution Main Total | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 |  |  | 12 | 12
Actual - Distribution Main Total | 4 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 1 | 0 |  |  | 12 | 12
Goal - Distribution Services Total | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 2 |  |  | 12 | 12
Actual - Distribution Services Total | 4 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 1 | 0 |  |  | 12 | 12
Goal - Transmission | 3 | 3 | 2 | 1 | 1 | 2 | 0 | 1 | 2 | 1 | 2 | 2 |  |  | 20 | 20
Actual - Transmission | 4 | 2 | 2 | 2 | 0 | 2 | 0 | 3 | 1 | 1 | 2 | 0 |  |  | 19 | 19
Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 11 | 11
Actual - Large Excursions - HP Distrib | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Actual - Large Excursions - LP Distrib | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  |  | 1 | 1
Actual - Large Excursions - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  |  | 5 | 5
Actual - Total All Large Excursions | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 10 | 10
Goal - All Equipment Failure | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 13 | 13
Actual - All Equipment Failure | 4 | 1 | 0 | 2 | 1 | 2 | 0 | 3 | 0 | 1 | 1 | 0 |  |  | 15 | 15
Goal - All Operator Error | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 14 | 14
Actual - All Operator Error | 3 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | 2 | 0 | 2 | 0 |  |  | 14 | 14
Goal - At Compressor Stn or Storage | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  | 4 | 4
1Q Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
1 - Large Excursions are defined as:
HP Distribution = P ≥ MOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psi
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For November Month-To-Date: 2 transmission events, 1 HP distribution event and 0 LP distribution event (better than month-end goals for HP/LP distribution for month and transmission for month). Preliminary root cause: 2 events were human factor error-related and 1 event was equipment-related. Event details shown below.
OP Team reviewing root causes of overpressure events. Plan additional training to address human-error related OP events. Detail review of equipment-related events to formulate corrective action plan.
| Jan: Total OP Events - Jan to December; Jul: Large Excursion OP Events - Jan to December | Small Excursion OP Events - Jan to December
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 Actuals | 2013 Goal |  | 2011 | 2012 | 2013 | 2014 | 2013 Goal |  | 2011 | 2012 | 2013 | 2014 | 2013 Goal
T&D Total | 774 | 308 | 31 |  | 32 |  | 36 | 8 | 10 |  | 11 |  | 738 | 300 | 21 |  | 21
| 2013 Total OP - 31 Events | [5 empty] | 2013 Large Excursion OP Events - 10 Events
2013 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 774 | 774
2012 Actual - All Events | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 308 | 308
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 3 | 0 |  |  | 31 | 31
2013 Goal OP events | 5 | 4 | 3 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 4 |  |  | 32 | 32
2011 Actual - Total All Large Excursions | 6 | 5 | 3 | 2 | 6 | 4 | 2 | 1 | 4 | 1 | 2 | 0 |  |  | 36 | 36
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 8 | 8
2013 Actual - Total All Large Excursions | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 10 | 10
2013 Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 11 | 11
| Total OP Events |  |  |  |  | Large Excursion OP Events |  |  |  |  | Small Excursion OP Events
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2013 Goals |  | 2011 | 2012 | 2013 Actuals | 2013 Goals |  | 2011 | 2012 | 2013 Actuals | 2013 Goals
HP Dist | 38 | 7 | 9 | 6 |  | 8 | 4 | 4 | 4 |  | 30 | 3 | 5 | 2
LP Dist | 624 | 228 | 3 | 6 |  | 3 | 0 | 1 | 4 |  | 621 | 228 | 2 | 2
Dist Total | 662 | 235 | 12 | 12 |  | 11 | 4 | 5 | 8 |  | 651 | 231 | 7 | 4
Trans | 112 | 73 | 19 | 20 |  | 25 | 4 | 5 | 3 |  | 87 | 69 | 14 | 17
T&D Total | 774 | 308 | 31 | 32 |  | 36 | 8 | 10 | 11 |  | 738 | 300 | 21 | 21
Note on Q11: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on R11: Singer, Kevin D: enter total monthly
Note on Q14: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on R14: Singer, Kevin D: enter total monthly
Note on Q23: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on Q29: Singer, Kevin D: Yr-End Actual = YTD+GOAL (Remaining)
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on R130: Singer, Kevin D: update amber cells from 2011-2013 expanded data

## Tracking2015 by Quarter (hidden)
1Q - 2015 OP Event Performance
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Expected Path: Goal OP events | 6 | 3 | 3 | 4 |  | 16 | 16
Amber Goal - Lowest end of range | 9 | 6 | 6 | 7 |  | 28 | 28
Actual - All Events | 7 | 4 | 9 | 9 |  | 29 | 29
Asset Family OP Metrics
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Goal - HP Distribution | 2 | 0 | 0 | 2 |  | 4 | 4
Actual - HP Distribution | 2 | 4 | 3 | 4 |  | 13 | 13
Goal - LP Distribution | 2 | 1 | 0 | 0 |  | 3 | 3
Actual - LP Distribution | 1 | 0 | 1 | 1 |  | 3 | 3
Goal - Distribution Main Total | 4 | 1 | 0 | 2 |  | 7 | 7
Actual - Distribution Main Total | 3 | 4 | 4 | 5 |  | 16 | 16
Goal - Distribution Services Total | 4 | 1 | 0 | 2 |  | 7 | 7
Actual - Distribution Services Total | 3 | 4 | 4 | 5 |  | 16 | 16
Goal - Transmission | 2 | 2 | 3 | 2 |  | 9 | 9
Actual - Transmission | 4 | 0 | 5 | 4 |  | 13 | 13
Goal - All Large Excursions1 | 2 | 0 | 1 | 1 |  | 2 | 4
Actual - Large Excursions - HP Distrib | 2 | 0 | 1 | 0 |  | 2 | 3
Actual - Large Excursions - LP Distrib | 1 | 0 | 1 | 0 |  | 1 | 0
Actual - Large Excursions - Transmission | 0 | 0 | 2 | 0 |  | 0 | 3
Actual - Total All Large Excursions | 3 | 0 | 4 | 0 |  | 7 | 7
Goal - All Equipment Failure | 3 | 2 | 1 | 3 |  | 9 | 9
Actual - All Equipment Failure | 3 | 2 | 5 | 6 |  | 16 | 16
Goal - All Operator Error | 3 | 1 | 2 | 1 |  | 7 | 7
Actual - All Operator Error | 4 | 2 | 4 | 3 |  | 13 | 13
Goal - At Compressor Stn or Storage | 1 | 1 | 1 | 1 |  | 4 | 4
Actual - At Compressor Stn or Storage | 0 | 0 | 1 | 1 |  | 2 | 2
1 - Large Excursions are defined as:
HP Distribution = P ≥ MAOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psig
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
1st Quarter
Large Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1
HP Distribution | 2 | 2 | 2 | 2 | 2
LP Distribution | 1 | 0 | 0 | 0 | 1
Transmission | 6 | 1 | 2 | 1 | 0
Grand Total | 9 | 3 | 4 | 3 | 3
Small Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1
HP Distribution | 4 | 2 | 3 | 0 | 0
LP Distribution | 172 | 179 | 0 | 1 | 0
Transmission | 35 | 45 | 6 | 2 | 4
Grand Total | 211 | 226 | 9 | 3 | 4
Total OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1
HP Distribution | 6 | 4 | 5 | 2 | 2
LP Distribution | 173 | 179 | 0 | 1 | 1
Transmission | 41 | 46 | 8 | 3 | 4
Grand Total | 220 | 229 | 13 | 6 | 7
Metric Comparison - Prior Years - 1st Quarter
OP Events by Apparent Cause - First Quarter
2015 Total OP - 0 Events as of 3/31/14 | [7 empty] | 2015 Large Excursion OP Events - 0 Events
2nd Quarter
Large Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2
HP Distribution | 5 | 0 | 1 | 0 | 0
LP Distribution | 1 | 0 | 0 | 0 | 0
Transmission | 1 | 1 | 0 | 0 | 0
Grand Total | 7 | 1 | 1 | 0 | 0
Small Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2
HP Distribution | 7 | 0 | 2 | 1 | 4
LP Distribution | 147 | 46 | 1 | 1 | 0
Transmission | 34 | 15 | 4 | 2 | 0
Grand Total | 188 | 61 | 7 | 4 | 4
Total OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2
HP Distribution | 12 | 0 | 3 | 1 | 4
LP Distribution | 148 | 46 | 1 | 1 | 0
Transmission | 35 | 16 | 4 | 2 | 0
Grand Total | 195 | 62 | 8 | 4 | 4
Metric Comparison - Prior Years - 2nd Quarter
OP Events by Apparent Cause - Second Quarter
2015 Total OP- 0 Events as of 7/1/14
3rd Quarter
Large Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3
HP Distribution | 1 | 1 | 1 | 0 | 1
LP Distribution | 0 | 0 | 1 | 0 | 1
Transmission | 1 | 0 | 1 | 2 | 2
Grand Total | 2 | 1 | 3 | 2 | 4
Small Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3
HP Distribution | 10 | 0 | 0 | 1 | 2
LP Distribution | 164 | 46 | 0 | 0 | 0
Transmission | 21 | 15 | 3 | 1 | 3
Grand Total | 195 | 61 | 3 | 2 | 5
Total OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3
HP Distribution | 11 | 1 | 1 | 1 | 3
LP Distribution | 164 | 46 | 1 | 0 | 1
Transmission | 22 | 15 | 4 | 3 | 5
Grand Total | 197 | 62 | 6 | 4 | 9
Metric Comparison - Prior Years - 3rd Quarter
OP Events by Apparent Cause - 4th Quarter
2013 Total OP- 13 Events as of 3/31/13 | [5 empty] | 2013 Large Excursion OP Events - 5 Events
4th Quarter
Large Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4
HP Distribution | 2 | 1 | 0 | 2 | 0
LP Distribution | 1 | 0 | 0 | 0 | 0
Transmission | 0 | 1 | 1 | 0 | 0
Grand Total | 3 | 2 | 1 | 2 | 0
Small Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4
HP Distribution | 8 | 1 | 0 | 0 | 4
LP Distribution | 138 | 3 | 1 | 0 | 1
Transmission | 14 | 6 | 3 | 2 | 5
Grand Total | 160 | 10 | 4 | 2 | 10
Total OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4
HP Distribution | 10 | 2 | 0 | 2 | 4
LP Distribution | 139 | 3 | 1 | 0 | 1
Transmission | 14 | 7 | 4 | 2 | 5
Grand Total | 163 | 12 | 5 | 4 | 10

## Tracking2016 by Quarter (hidden)
Q - 2016 OP Event Performance
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Expected Path: Goal OP events | 5 | 3 | 3 | 5 |  | 11 | 16
Amber Goal - Lowest end of range | 8 | 6 | 6 | 8 |  | 14 | 28
Actual - All Events | 2 | 5 | 4 | 7 |  | 18 | 23 |  |  | Q1 | Q2 | Jul | Aug | Sep | Q4 | YTD | Yr-End
[9 empty] | Expected Path: Goal OP events | 5 | 3 | 1 | 1 | 1 | 5 | 11 | 16
Asset Family OP Metrics | [8 empty] | Actual - All Events | 2 | 5 | 1 | 3 |  | 0 | 11 | 16
| Q1 | Q2 | Q3 | Q4 |  | YTD | Yr-End
Goal - HP Distribution | 2 | 0 | 0 | 2 |  | 2 | 4 |  | Goal - All Large Excursions1 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 4
Actual - HP Distribution | 0 | 2 | 2 | 4 |  | 4 | 6 |  | Actual - Total All Large Excursions | 0 | 4 | 1 | 1 |  | - | 6 | 8
Goal - LP Distribution | 2 | 1 | 0 | 0 |  | 3 | 3
Actual - LP Distribution | 2 | 0 | 0 | 0 |  | 2 | 2
Goal - Distribution Main Total | 4 | 1 | 0 | 2 |  | 5 | 7
Actual - Distribution Main Total | 2 | 2 | 2 | 4 |  | 6 | 8
Goal - Distribution Services Total | 4 | 1 | 0 | 2 |  | 5 | 7
Actual - Distribution Services Total | 2 | 2 | 2 | 4 |  | 6 | 8
Goal - Transmission | 2 | 2 | 3 | 3 |  | 7 | 10
Actual - Transmission | 0 | 3 | 2 | 3 |  | 5 | 8
Goal - All Large Excursions1 | 2 | 0 | 0 | 2 |  | 2 | 4
Actual - Large Excursions - HP Distrib | 0 | 2 | 2 | 2 |  | 6 | 6
Actual - Large Excursions - LP Distrib | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - Large Excursions - Transmission | 0 | 2 | 0 | 2 |  | 4 | 4
Actual - Total All Large Excursions | 0 | 4 | 2 | 4 |  | 10 | 12
Goal - All Equipment Failure | 3 | 2 | 1 | 3 |  | 6 | 9
Actual - All Equipment Failure | 2 | 1 | 2 | 3 |  | 5 | 8
Goal - All Operator Error | 3 | 1 | 2 | 1 |  | 6 | 7
Actual - All Operator Error | 0 | 4 | 2 | 4 |  | 6 | 7
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 1 |  | 0 | 0
1 - Large Excursions are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% |  |  |  | 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig |  |  |  | 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MAOP + 10% or 25 psig
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
1st Quarter
Large Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1 | 2016 Q1 | 2017 Q1
HP Distribution | 2 | 2 | 2 | 2 | 2 | 0 | 1
LP Distribution | 1 | 0 | 0 | 0 | 1 | 0 | 0
Transmission | 6 | 1 | 2 | 1 | 0 | 0 | 0
Grand Total | 9 | 3 | 4 | 3 | 3 | 0 | 1
Small Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1 | 2016 Q1 | 2017 Q1
HP Distribution | 4 | 2 | 3 | 0 | 0 | 0 | 0
LP Distribution | 172 | 179 | 0 | 1 | 0 | 2 | 0
Transmission | 35 | 45 | 6 | 2 | 4 | 0 | 1
Grand Total | 211 | 226 | 9 | 3 | 4 | 2 | 1
Total OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2014 Q1 | 2015 Q1 | 2016 Q1 | 2017 Q1
HP Distribution | 6 | 4 | 5 | 2 | 2 | 0 | 1
LP Distribution | 173 | 179 | 0 | 1 | 1 | 2 | 0
Transmission | 41 | 46 | 8 | 3 | 4 | 0 | 1
Grand Total | 220 | 229 | 13 | 6 | 7 | 2 | 2
Metric Comparison - Prior Years - 1st Quarter
OP Events by Apparent Cause - First Quarter
2015 Total OP - 0 Events as of 3/31/14 | [7 empty] | 2015 Large Excursion OP Events - 0 Events
2nd Quarter
Large Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2 | 2016 Q2
HP Distribution | 5 | 0 | 1 | 0 | 0 | 0
LP Distribution | 1 | 0 | 0 | 0 | 0 | 0
Transmission | 1 | 1 | 0 | 0 | 0 | 0
Grand Total | 7 | 1 | 1 | 0 | 0 | 0
Small Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2 | 2016 Q2
HP Distribution | 7 | 0 | 2 | 1 | 4 | 0
LP Distribution | 147 | 46 | 1 | 1 | 0 | 0
Transmission | 34 | 15 | 4 | 2 | 0 | 0
Grand Total | 188 | 61 | 7 | 4 | 4 | 0
Total OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2014 Q2 | 2015 Q2 | 2016 Q2
HP Distribution | 12 | 0 | 3 | 1 | 4 | 0
LP Distribution | 148 | 46 | 1 | 1 | 0 | 0
Transmission | 35 | 16 | 4 | 2 | 0 | 0
Grand Total | 195 | 62 | 8 | 4 | 4 | 0
Metric Comparison - Prior Years - 2nd Quarter
OP Events by Apparent Cause - Second Quarter
2015 Total OP- 0 Events as of 7/1/14
3rd Quarter
Large Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3 | 2016 Q3
HP Distribution | 1 | 1 | 1 | 0 | 1 | 0
LP Distribution | 0 | 0 | 1 | 0 | 1 | 0
Transmission | 1 | 0 | 1 | 2 | 2 | 0
Grand Total | 2 | 1 | 3 | 2 | 4 | 0
Small Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3 | 2016 Q3
HP Distribution | 10 | 0 | 0 | 1 | 2 | 0
LP Distribution | 164 | 46 | 0 | 0 | 0 | 0
Transmission | 21 | 15 | 3 | 1 | 3 | 0
Grand Total | 195 | 61 | 3 | 2 | 5 | 0
Total OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2014 Q3 | 2015 Q3 | 2016 Q3
HP Distribution | 11 | 1 | 1 | 1 | 3 | 0
LP Distribution | 164 | 46 | 1 | 0 | 1 | 0
Transmission | 22 | 15 | 4 | 3 | 5 | 0
Grand Total | 197 | 62 | 6 | 4 | 9 | 0
Metric Comparison - Prior Years - 3rd Quarter
OP Events by Apparent Cause - 4th Quarter
2013 Total OP- 13 Events as of 3/31/13 | [5 empty] | 2013 Large Excursion OP Events - 5 Events
4th Quarter
Large Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4 | 2016 Q4
HP Distribution | 2 | 1 | 0 | 2 | 0 | 2
LP Distribution | 1 | 0 | 0 | 0 | 0 | 0
Transmission | 0 | 1 | 1 | 0 | 0 | 2
Grand Total | 3 | 2 | 1 | 2 | 0 | 4
Small Excursion OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4 | 2016 Q4
HP Distribution | 8 | 1 | 0 | 0 | 4 | 2
LP Distribution | 138 | 3 | 1 | 0 | 1 | 0
Transmission | 14 | 6 | 3 | 2 | 5 | 1
Grand Total | 160 | 10 | 4 | 2 | 10 | 3
Total OP Events | 2011 Q4 | 2012 Q4 | 2013 Q4 | 2014 Q4 | 2015 Q4 | 2016 Q4
HP Distribution | 10 | 2 | 0 | 2 | 4 | 4
LP Distribution | 139 | 3 | 1 | 0 | 1 | 0
Transmission | 14 | 7 | 4 | 2 | 5 | 3
Grand Total | 163 | 12 | 5 | 4 | 10 | 7

## Tracking2016 by Month (hidden)
2016 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 16 | 16
Amber Goal - Lowest end of range* | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 |  |  | 25 | 28
Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 4 | 4
Actual - HP Distribution Mains | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 8 | 8 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Actual - LP Distribution | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 3 |  |  |  |  | change these colors at End of Month |  |  |  | 0
Goal - Distribution Main Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 7 | 7 | [8 empty] | 1
Actual - Distribution Main Total | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10 |  |  |  |  | change these colors at End of Month |  |  |  | 2
Goal - Distribution Services Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 7 | 7
Actual - Distribution Services Total | 2 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10 |  |  |  |  | change these colors at End of Month |  |  |  | 3
Goal - Transmission | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  |  | 9 | 9
Actual - Transmission | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 1 | 1 |  |  | 8 | 8 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | 3 | 4 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 1 | 1 | 0 |  |  | 6 | 6
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 4 | 4
Actual - Total All Large Excursions | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
Goal - All Equipment Failure | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 2 |  |  | 9 | 9
Actual - All Equipment Failure | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 1 |  |  | 8 | 8
Goal - All Operator Error | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 |  |  | 7 | 7
Actual - All Operator Error | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 2 | 0 | 1 | 2 | 1 |  |  | 10 | 10
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  | 1 | 1
1 - Large Excursions are defined as: | bar: Oct to Dec
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Oct: Large Excursion OP Events | [5 empty] | Small Excursion OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2016 Goal |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2016 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2016 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 16 |  |  | 21 | 7 | 10 | 7 | 7 | 10 | 4 |  | 754 | 302 | 22 | 11 | 22 | 8 | 12
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2016 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 722 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 303 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 16 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2016 Goal OP events | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Excursions | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 18 | 21
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Excursions | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 1 |  |  | 10 | 10
2014 Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Excursions | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2016 Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | 4 | 4
| Jan: Total OP Events; Aug: Large Excursion OP Events | Large |  | Small Excursion OP Events |  |  |  |  | Small
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 |  | 10 | 4 | 4 | 4 | 3 | 6 |  | 29 | 3 | 5 | 2 | 10 | 2
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 |  | 3 | 0 | 1 | 0 | 2 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 |  | 13 | 4 | 5 | 4 | 5 | 6 |  | 650 | 231 | 7 | 4 | 11 | 4
Trans | 112 | 74 | 20 | 10 | 13 | 8 |  | 8 | 4 | 6 | 3 | 2 | 4 |  | 104 | 70 | 14 | 7 | 11 | 4
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 |  | 21 | 8 | 11 | 7 | 7 | 10 |  | 754 | 301 | 21 | 11 | 22 | 8
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on AB59: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P117: Singer, Kevin D: move pre month report
Note on P125: Singer, Kevin D: move per month report
Note on U129: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## Tracking2015 by Month (hidden)
2015 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
Expected Path: Goal OP events* | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | 16 | 16
Amber Goal - Lowest end of range* | 4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  | 28 | 28
Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  | 29 | 29 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 4 | 4
Actual - HP Distribution Mains | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 2 | 2 | 0 | 2 |  | 13 | 13 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 3
Actual - LP Distribution | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 |  | 3 | 3 |  |  |  |  | change these colors at End of Month | 0
Goal - Distribution Main Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 7 | 7 | [5 empty] | 1
Actual - Distribution Main Total | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 2 | 3 | 0 | 2 |  | 16 | 16 |  |  |  |  | change these colors at End of Month | 2
Goal - Distribution Services Total | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 7 | 7
Actual - Distribution Services Total | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 2 | 2 | 3 | 0 | 2 |  | 16 | 16 |  |  |  |  | change these colors at End of Month | 3
Goal - Transmission | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  | 9 | 9
Actual - Transmission | 1 | 2 | 1 | 0 | 0 | 0 | 3 | 1 | 1 | 0 | 2 | 2 |  | 13 | 13 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  | 4 | 4 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 3 | 3
Actual - Large Excursions - LP Dist | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 2 | 2
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 2 | 2
Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  | 7 | 7
Goal - All Equipment Failure | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 2 |  | 9 | 9
Actual - All Equipment Failure | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 |  | 16 | 16
Goal - All Operator Error | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 |  | 7 | 7
Actual - All Operator Error | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 1 | 1 | 0 | 2 |  | 13 | 13
Goal - At Compressor Stn or Storage | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  | 4 | 4
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  | 2 | 2
1 - Large Excursions are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Aug: Large Excursion OP Events |  | Small Excursion OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2015 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2015 Goal | 2011 | 2012 | 2013 | 2014 | 2015 | 2015 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 16 |  | 21 | 7 | 9 | 7 | 7 | 4 | 754 | 302 | 23 | 11 | 22 | 12
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2015 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  | 29 | 29
2015 Goal OP events | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | 12 | 16
2011 Actual - Total All Large Excursions | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  | 21 | 21
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  | 7 | 7
2013 Actual - Total All Large Excursions | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  | 9 | 9
2014 Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  | 7 | 7
2015 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  | 7 | 7
2015 Goal - All Large Excursions1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  | 4 | 4
| Jan: Total OP Events; Aug: Large Excursion OP Events |  | Small Excursion OP Events
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 Actual | 2015 YTD | 2015 Goal |  | 2011 | 2012 | 2013 Actuals | 2014 Actual | 2015 YTD | 2015 Goal | 2011 | 2012 | 2013 Actuals | 2014 Actual | 2015 YTD | 2015 Goal
HP Dist | 39 | 7 | 9 | 6 | 13 | 4 |  | 10 | 4 | 4 | 4 | 3 |  | 29 | 3 | 5 | 2 | 10
LP Dist | 624 | 228 | 3 | 2 | 3 | 3 |  | 3 | 0 | 1 | 0 | 2 |  | 621 | 228 | 2 | 2 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 16 |  | 13 | 4 | 5 | 4 | 5 |  | 650 | 231 | 7 | 4 | 11
Trans | 112 | 74 | 20 | 10 | 13 | 9 |  | 25 | 4 | 6 | 3 | 2 |  | 87 | 70 | 14 | 7 | 11
T&D Total | 775 | 309 | 32 | 18 | 29 | 25 |  | 38 | 8 | 11 | 7 | 7 |  | 737 | 301 | 21 | 11 | 22
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on Y59: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P116: Singer, Kevin D: move pre month report
Note on P123: Singer, Kevin D: move per month report
Note on U127: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## 2019 OP Rag Status (hidden)
Sulfur-gon Filters |  | Contact: Nicolyn Hernandez
Total Stations w/Filters: | 563 | Notes: [9/24] [KDSD] Per JZ. Please note that the total number of Sulfur-gon Installation at Pilot-operated Sites is 380, there were some duplications that were taken out. I do not have any further updates as yet due to the fact that the efforts to get updates from the divisions were put on hold. I just got the go ahead to obtain further updates but, its going be at least a few weeks till I will start receiving updates from the divisions. I will keep you posted. [3/28] [KWB] Per Corine e-mail 3/27, formal count not available, estimated 300+ installs completed
Existing: | 250
2017 Installed: | 75
2018 Installed: | 238
2019 Installed: | 0
Slam Shut Installations (50N) |  | Contact: Sophia Curiel / Ramon Gonzalez
Total | 100 | Notes: [9/26] [KDSD] Updated in September [3/29] [KWB] Per Ramon e-mail 3/29, need clarification. F/U/W Tim on path forward
Completed | 7
2019 Remaining | 93
Mini AT Data into Abnormal Pressure Report |  | Contact: Matt Pace
Total | 343 | Notes: [9/24] [KDSD] Per Sergio, the implementation will initiate this week with 25 sites, 19 complete. [3/28] [KWB] Per Matt pace e-mail 3/28; working with control room to start migration. Not yet started.
2018 Completed | 174
2019 Completed | 169
LVCR Rebuild |  | Contact: Sophia Curiel / Ramon Gonzalez
Total | 16 | Notes: [9/26] [KDSD] Updated in September [9/24] [KDSD] Per Sophia, the group is only researching for data on 96 sites (with the understanding there are ~105) [3/29] [KWB] Per Ramon e-mail 3/29, vendor taking photos to support JUNE desktop condition assessment
2019 Completed | 1
2019 Remaining | 15
Legacy ERX to Control Room |  | Contact: Nishal Gupta
Total Legacy ERX | 135 | Notes: [8/24] [KDSD] Per Nishal, on schedule to complete by EOY [7/1] [KWB] Per Nishal e-mail 7/1, updated.
Completed Legacy ERX | 134
Remaining Legacy ERX | 1
Station Retrofits |  | Contact: Corine Hermann
Total Population | 30 | Notes: [3/29] [KWB] Per Corine, we have not started this effort. [6/26] [KDSD] Met with DIMP team, JANT will prcoess information pending GSP review, and create CAP notification.
Completed | 0
Remaining | 0
updates made for monthly op update
Precent Completion
[10 empty] | Legacy | 99.2593
| last month | [8 empty] | Condition | 7
|  |  | Metrics | 2019 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 6 | 1 | 0 | 1 | kevin
|  | 2 | Small OP Events | 16 | 2 | 2 | 4 | kevin
| 1/16 update | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 563 | 0 | 563 | jz | jmahmood@specservices.com
|  | 4 | Slam Shut Installations by 50N | 100 | 0 | 7 | 7 | jack price
|  | 5 | Slam Shut FCOs | 100 | 0 | 4 | 4 | jack price
|  | 6 | Legacy ERX to Control Room | 135 | 134 | 0 | 134 | nishal
|  | 7 | Mini AT Data into Abnormal Pressure Report | 450 | 174 | 169 | 343 | david
|  | 8 | LVCR Rebuilds | 14 | 0 | 1 | 1 | corine
|  | 9 | Station Retrofits (including secondary OPP) | 30 | 0 | 0 | 0
|  | 10 | LVC Condition Assessment Data Gathering | 379 | 379 | 0 | 379 | sophia
|  | 11 | LVCR Field Assessment | 96 | 96 | 0 | 96 | sophia
|  |  | Metrics | 2018 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 8 | 4 | 1 | 5
|  | 2 | Small OP Events | 16 | 15 | 3 | 18
|  | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 499 | 26 | 525
|  | 4 | Slam Shut Installations by Population | 30 | 5 | 1 | 6
|  | 5 | Legacy ERX to Control Room | 135 | 128 | 6 | 134
|  | 6 | Mini AT Data into Abnormal Pressure Report | 450 | 50 | 131 | 181
|  | 7 | LVCR Rebuilds | 4 | 2 | 2 | 4
|  | 8 | Station Retrofits (including secondary OPP) | 30 | 0
|  | 9 | LVC Condition Assessment Data Gathering | 379 | 301 | 64 | 365
|  | 10 | LVCR Field Assessment | 96 | 84 | 9 | 93

## 2018 OP Rag Status (hidden)
Sulfur-gon Filters (Transmission) |  | Contact: Nicolyn Hernandez
Total Stations w/Filters: | 499 | Notes: [9/24] [KDSD] Per JZ. Please note that the total number of Sulfur-gon Installation at Pilot-operated Sites is 380, there were some duplications that were taken out. I do not have any further updates as yet due to the fact that the efforts to get updates from the divisions were put on hold. I just got the go ahead to obtain further updates but, its going be at least a few weeks till I will start receiving updates from the divisions. I will keep you posted. [3/28] [KWB] Per Corine e-mail 3/27, formal count not available, estimated 300+ installs completed
Existing: | 250
2017 Installed: | 75
2018 Installed: | 174
2018 Remaining: | 0
LVC MSA Condition Assessment |  | Contact: Sophia Curiel / Ramon Gonzalez
Station Total | 379 | Notes: [9/26] [KDSD] Updated in September [3/29] [KWB] Per Ramon e-mail 3/29, need clarification. F/U/W Tim on path forward
Completed | 365
2018 Remaining | 14
Mini AT Data into Abnormal Pressure Report |  | Contact: Matt Pace
Total | 450 | Notes: [9/24] [KDSD] Per Sergio, the implementation will initiate this week with 25 sites, 19 complete. [3/28] [KWB] Per Matt pace e-mail 3/28; working with control room to start migration. Not yet started.
2018 Completed | 181
2018 Remaining | 269
LVCR Field Assessment |  | Contact: Sophia Curiel / Ramon Gonzalez
Station Total (105) | 96 | Notes: [9/26] [KDSD] Updated in September [9/24] [KDSD] Per Sophia, the group is only researching for data on 96 sites (with the understanding there are ~105) [3/29] [KWB] Per Ramon e-mail 3/29, vendor taking photos to support JUNE desktop condition assessment
2018 Completed | 93
2018 Remaining | 3
Legacy ERX to Control Room |  | Contact: Nishal Gupta
Total Legacy ERX | 135 | Notes: [8/24] [KDSD] Per Nishal, on schedule to complete by EOY [7/1] [KWB] Per Nishal e-mail 7/1, updated.
Completed Legacy ERX | 134
Remaining Legacy ERX | 1
MAOP Separation Valves |  | Contact: Corine Hermann
Total Population | 0 | Notes: [3/29] [KWB] Per Corine, we have not started this effort. [6/26] [KDSD] Met with DIMP team, JANT will prcoess information pending GSP review, and create CAP notification.
Mitigated | 0
Remaining | 0
updates made for monthly op update
Precent Completion
[10 empty] | Legacy | 99.2593
| last month | [8 empty] | Condition | 96.3061
|  |  | Metrics | 2019 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 6 | 1 | 0 | 1 | kevin
|  | 2 | Small OP Events | 16 | 2 | 2 | 4 | kevin
| 1/16 update | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 563 | 0 | 563 | jz | jmahmood@specservices.com
|  | 4 | Slam Shut Installations by 50N | 100 | 0 | 7 | 7 | jack price
|  | 5 | Slam Shut FCOs | 100 | 0 | 4 | 4 | nishall
|  | 6 | Legacy ERX to Control Room | 135 | 134 | 0 | 134 | sergio
|  | 7 | Mini AT Data into Abnormal Pressure Report | 450 | 174 | 169 | 343 | corine
|  | 8 | LVCR Rebuilds | 14 | 0 | 1 | 1
|  | 9 | Station Retrofits (including secondary OPP) | 30 | 0 | 0 | 0
|  | 10 | LVC Condition Assessment Data Gathering | 379 | 379 | 0 | 379 | sophia
|  | 11 | LVCR Field Assessment | 96 | 96 | 0 | 96 | sophia
|  |  | Metrics | 2018 Target | Previous | Change | YTD
|  | 1 | Large OP Events (MAOP-S +10%) | 8 | 4 | 1 | 5
|  | 2 | Small OP Events | 16 | 15 | 3 | 18
|  | 3 | Sulfur-gon Installation at Pilot-operated Sites | 800 | 499 | 26 | 525
|  | 4 | Slam Shut Installations by Population | 30 | 5 | 1 | 6
|  | 5 | Legacy ERX to Control Room | 135 | 128 | 6 | 134
|  | 6 | Mini AT Data into Abnormal Pressure Report | 450 | 50 | 131 | 181
|  | 7 | LVCR Rebuilds | 4 | 2 | 2 | 4
|  | 8 | Station Retrofits (including secondary OPP) | 30 | 0
|  | 9 | LVC Condition Assessment Data Gathering | 379 | 301 | 64 | 365
|  | 10 | LVCR Field Assessment | 96 | 84 | 9 | 93

## Tracking2017 by Month (hidden)
2017 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 4 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 16 | 16
Amber Goal - Lowest end of range* | 5 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 22 | 28
Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  |  | 6 | 6
Actual - HP Distribution Mains | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 1 | 0 | 0 |  |  | 6 | 6 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 1 | 1 |  |  |  |  | change these colors at End of Month |  |  |  |  | 0
Goal - Distribution Main Total | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  |  | 6 | 6 | [9 empty] | 1
Actual - Distribution Main Total | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  |  | 7 | 7 |  |  |  |  | change these colors at End of Month |  |  |  |  | 2
Goal - Distribution Services Total | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |  |  | 6 | 6
Actual - Distribution Services Total | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  |  | 7 | 7 |  |  |  |  | change these colors at End of Month |  |  |  |  | 3
Goal - Transmission | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 |  |  | 6 | 6
Actual - Transmission | 0 | 0 | 1 | 2 | 2 | 0 | 0 | 4 | 0 | 4 | 0 | 1 |  |  | 14 | 14 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 |  |  | 4 | 4
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0 |  |  | 7 | 7
Actual - Total All Large OP | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 8
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 |  |  | 7 | 7
Actual - All Equipment Failure | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 1 | 1 | 1 | 0 | 0 |  |  | 12 | 7
Goal - All Operator Error | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 |  |  | 5 | 5
Actual - All Operator Error | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Oct: Large OP Events | [5 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 YTD | 2017 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 YTD | 2017 Forecast |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 YTD | 2017 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 16 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 8 |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 8
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2017 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 1 | 3 | 2 | 2 |  |  | 19 | 19
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2017 Goal OP events | 4 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 5 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 3 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 4 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 4 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 3 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 11 | 11
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2017 Goal - All Large OPs1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4
| Jan: Total OP Events; Oct: Large Excursion OP Events | [5 empty] | Small Excursion OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual |  |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 |  |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 |  |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 |  |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 12 |  |  | 8 | 4 | 6 | 3 | 2 | 4 | 7 |  | 104 | 70 | 14 | 7 | 11 | 4 | 5
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 19 |  |  | 21 | 8 | 11 | 7 | 7 | 10 | 11 |  | 754 | 301 | 21 | 11 | 22 | 8 | 8
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 21
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A60: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on AB65: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P124: Singer, Kevin D: move pre month report
Note on P133: Singer, Kevin D: move per month report
Note on X137: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14
Note on Y137: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## Tracking2018 by Month (hidden)
2018 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 15 | 16
Amber Goal - Lowest end of range* | 4 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 22 | 24
Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 19 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 8 | 8
Actual - HP Distribution Mains | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 2 |  |  | 6 | 6 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 |  |  |  |  | change these colors at End of Month |  |  |  |  | 0
Goal - Distribution Main Total | 4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 8 | 8 | [9 empty] | 1
Actual - Distribution Main Total | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 2 |  |  | 9 | 9 |  |  |  |  | change these colors at End of Month |  |  |  |  | 2
Goal - Distribution Services Total | 4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 8 | 8
Actual - Distribution Services Total | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 2 | 2 |  |  | 9 | 9 |  |  |  |  | change these colors at End of Month |  |  |  |  | 3
Goal - Transmission | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 8 | 8
Actual - Transmission | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 2 | 1 |  |  | 9 | 9 |  |  |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8 | 8 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 2
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 |  |  | 3 | 3
Actual - Total All Large OP | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
Goal - All Equipment Failure | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Actual - All Equipment Failure | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Goal - All Operator Error | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |  |  | 4 | 4
Actual - All Operator Error | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 2 | 2
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 4 | 4 | New for 2018
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - All Safety | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 1
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events; Nov: Large OP Events | [8 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2018 Goal |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 Target |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 YTD | 2018 Goal
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 16 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 6 |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 16
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2017 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 1 | 3 | 2 | 2 |  |  | 19 | 19
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2018 Goal OP events | 8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 1 |  |  | 10 | 10
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 0 | 5
2018 Goal - All Large OPs1 | 4 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8 | 8
| Jan: Total OP Events; Oct: Large Excursion OP Events | [5 empty] | Small Excursion OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 2 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 2 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 |  | 8 | 4 | 6 | 3 | 2 | 4 | 6 | 3 |  | 104 | 70 | 14 | 7 | 11 | 4 | 6 | 6
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 |  | 21 | 8 | 11 | 7 | 7 | 10 | 10 | 5 |  | 754 | 301 | 21 | 11 | 22 | 8 | 9 | 13
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18; 10 ‘17: 21
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10; 10 ‘17: 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A60: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on P125: Singer, Kevin D: move pre month report
Note on P135: Singer, Kevin D: move per month report
Note on Y139: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14
Note on Z139: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## Tracking2014 by Month (hidden)
2014 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Expected Path: Goal OP events* | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 3 |  |  | 24 | 24
Amber Goal - Lowest end of range* | 4 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 4 |  |  | 36 | 36
Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18 |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
Goal - HP Distribution Mains | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 9 | 9
Actual - HP Distribution Mains | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 |  |  | 5 | 5 |  |  | change these colors at End of Month
Goal - LP Distribution | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2
Actual - LP Distribution | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 |  |  | change these colors at End of Month | 0
Goal - Distribution Main Total | 2 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 11 | 11 |  |  |  | 1
Actual - Distribution Main Total | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 |  |  | 7 | 7 |  |  | change these colors at End of Month | 2
Goal - Distribution Services Total | 2 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 11 | 11
Actual - Distribution Services Total | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 |  |  | 7 | 7 |  |  | change these colors at End of Month | 3
Goal - Transmission | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 13 | 13
Actual - Transmission | 1 | 2 | 0 | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 0 | 2 |  |  | 10 | 10 |  |  | change these colors at End of Month
Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 9 | 9 |  |  | change these colors at End of Month
Actual - Large Excursions - HP Distrib | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 3 | 3
Actual - Large Excursions - LP Distrib | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Transmission | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
Goal - All Equipment Failure | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 |  |  | 12 | 12
Actual - All Equipment Failure | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 2 |  |  | 7 | 7
Goal - All Operator Error | [14 empty] | 12 | 12 | bar: Jan to Dec
Actual - All Operator Error | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 2 | 0 | 0 | 0 | 0 |  |  | 8 | 8
Goal - At Compressor Stn or Storage | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  | 4 | 4
Actual - At Compressor Stn or Storage | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 2
1 - Large Excursions are defined as:
HP Distribution = P ≥ MAOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events - Jan to Dec; Jul: Large Excursion OP Events - Jan to Dec | Small Excursion OP Events - Jan to Dec
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 Actuals | 2014 Goal |  | 2011 | 2012 | 2013 | 2014 | 2014 Goal |  | 2011 | 2012 | 2013 | 2014 | 2014 Goal
T&D Total | 774 | 308 | 32 | 18 | 24 |  | 36 | 8 | 10 | 7 | 9 |  | 738 | 300 | 22 | 11 | 15
these tables are auto generated from the Charts tab
Charts tab must be updated monthly
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
2014 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 774 | 774
2012 Actual - All Events | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 308 | 308
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 3 | 1 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2014 Goal OP events | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 3 |  |  | 24 | 24
2011 Actual - Total All Large Excursions | 6 | 5 | 3 | 2 | 6 | 4 | 2 | 1 | 4 | 1 | 2 | 0 |  |  | 36 | 36
2012 Actual - Total All Large Excursions | 2 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 8 | 8
2013 Actual - Total All Large Excursions | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 10 | 10
2014 Actual - Total All Large Excursions | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2014 Goal - All Large Excursions1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 9 | 9
| Jan: Total OP Events; Jul: Large Excursion OP Events | Small Excursion OP Events
| 2011 Actuals | 2012 Actuals | 2013 Actuals | 2014 YTD | 2014 Goals |  | 2011 | 2012 | 2013 Actuals | 2014 YTD | 2014 Goals |  | 2011 | 2012 | 2013 Actuals | 2014 YTD | 2014 Goals
HP Dist | 38 | 7 | 9 | 5 | 9 |  | 8 | 4 | 4 | 3 | 4 |  | 30 | 3 | 5 | 2 | 5
LP Dist | 624 | 228 | 3 | 2 | 2 |  | 3 | 0 | 1 | 0 | 0 |  | 621 | 228 | 2 | 2 | 2
Dist Total | 662 | 235 | 12 | 7 | 11 |  | 11 | 4 | 5 | 3 | 4 |  | 651 | 231 | 7 | 4 | 7
Trans | 112 | 73 | 19 | 10 | 13 |  | 25 | 4 | 5 | 3 | 5 |  | 87 | 69 | 14 | 7 | 8
T&D Total | 774 | 308 | 31 | 17 | 24 |  | 36 | 8 | 10 | 6 | 9 |  | 738 | 300 | 21 | 11 | 15
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A54: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Note on V59: Singer, Kevin D: update topics and year to date totals in concert with the table below
Note on P122: Singer, Kevin D: move pre month report
Note on P128: Singer, Kevin D: move per month report
Note on U132: Singer, Kevin D: if any over pressure events update amber cells from 2011-2014 expanded data - cells should automatically update from this point forward 9/25/14

## CA's Tracking Report (hidden)
CAP ID | CAP Notification Text Title | Point Description/Location | OP/Near Hit | Date of Event | Task No. | Task Code | CAP Task Text Title | Short Description of Corrective Action/Task | Task Processor | Task WrkCtr | Task Status | Task Start Date | Task Due Date | Task Completed By | Task Completion Date | Risk | Notif WrkCenter | Notif Due Date | WT Group | WT Code | Notification Owner | Process | Asset Family | Division/District | Close Call? | Notif Owner Status | Notification System Stat | Extension # | Extension Authorize | Additional Comments
7000006 | Over Pressure - Low Pressure system | not present | OP | not present | 2 | CA | IA Audit - Low Pressure Reg Stn Inspect | All below grade LP Regulator and system relief stations will be inspected. Those that don’t have vents extended above ground will be modified. | MJKQ | GEPDG | TSRL | 2012-04-25 | 2016-12-31 |  |  | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL |  | unknown | ACCP | OSNO OSTS | 0
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | 2013-09-10 12:38 | 4 | CA | Upgrade valve system | Upgrade valve system to prevent valve from being operated beyond the closed position. Per recent audit of the corrective actions for this over pressure event (7005804) it has been determiend that the valve will be replaced during the beginning of December. See Email by Edgardo Ochoa | OXG3 |  | TSRL | 2014-10-31 | 2014-12-31 |  |  | High | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPR NOPT OSTS | 0 |  | Reference Notification 7005804
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | not present | 3 | CA | Upgrade/Replace Existing Gas SCADA |  | RPM4 | GESSO | TSRL | 2013-12-17 | 2016-01-31 |  |  | Medium 3-B | GESSO | 2016-01-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | not present | 4 | CA | Verify and Doc Status of CAs | Verify and Document Status of Corrective Actions Identified in July 2013 Analysis Report: Many of the Corrective Action have been completed. Need to document actions, dates and any status of any outstanding corrective actions. Note that the Corrective Actions identified in July 2013 report were are recommendations and all are not necessarily prudent. | G1CR |  | TSRL | 2014-06-26 | 2014-11-01 |  |  | Medium 3-B | GESSO | 2016-01-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 3 | CA | Evaluate existing maintenance procedure | No additional Description | JLR9 | GEDT | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 4 | CA | Gas Standard H-14 to be looked at | No additional Description | J011 | GACSG | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 5 | CA | Clearances to reflect Mooney Regulation | Clearance committee to address Mooney regulation issues as to low differential lock up in regards to special instructions on clearance | KAS5 | GEST | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 6 | CA | New OPP other than Mooney | New OPP for Mooney regulation other than Mooney to prevent drifting | JLR9 | GEDT | TSRL | 2014-03-06 | 2015-03-20 |  |  | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 5.15.14 Design criteria has been initiated (Stations Group)
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 3 | CA | OPP not installed | OPP added to bypass run D/S of V-3 at Brittan "Y" | M8CN | GEPT | TSRL | 2013-06-17 | 2015-01-15 |  |  | Medium 3-B | GESS | 2015-01-30 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 2 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response.
7000132 | 3628_LT-177A_Over Pressurization | not present | OP | not present | 1 | CA | Tighter regulation controls | Replace the Mooney regulators (one regulation run) at Cummings Creek PLS with another 1/4" turn plug valve with a Becker Controller for better setpoint control on low flow situations on L-177 | MRDN | GAIFP | TSRL | 2013-06-19 | 2015-12-31 |  |  | Medium 3-B | GESS | 2016-01-15 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | HB | unknown | ACCP | OSNO OSTS | 0 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response.
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 2 | CA | Upgrade pipeline capacity | The recommendation is for LT&DP to add additional gas pipeline (gas supply) to the Ripon/Modesto DFM. There is to be additional gas supply added to Ripon/Modesto DFM by 2017. | RLP7 | GESPN | TSRL | 2013-05-16 | 2018-01-04 |  |  | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000784 | Erroneous SCADA alarms upon deployment | not present | Other | N/A | 4 | TA | Implement solution if feasible | There may not be a feasible solution | RPM4 | GESSO | TSRL | 2014-09-10 | 2014-12-20 |  |  | Low 4-B | GESSO | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7000784 | Erroneous SCADA alarms upon deployment | not present | Other | N/A | 3 | TA | Identify possible solutions | No note at this time | RPM4 | GESSO | TSRL | 2014-08-10 | 2014-12-15 |  |  | Low 4-B | GESSO | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7000784 | Erroneous SCADA alarms upon deployment | not present | Other | N/A | 2 | TA | Analyze cause of alarm floods | Settings reviewed and verified correct. Diagnostic code/logiging written and installed, however no alarm flood occurred on 8/27 deployment so no diagnositic info gathered. Analysis extended to 9/10 to caputure next flood | RPM4 | GESSO | TSRL | 2014-07-01 | 2014-11-30 |  |  | Low 4-B | GESSO | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 7 | CA | CA: Replace Station | Lomita Park station will be replaced in 2014… as the other two (Martin and Sullivan) have been replaced in the last two years… this is the final one on the list to be replaced on this system. This order number is 30859799. | SDK2 | GESS | TSRL | 2014-03-05 | 2015-01-30 |  |  | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0 |  | 4.14.14 Station is to be replaced in 2014
7002930 | SCADA Emerg Resp Valve Info Issues | not present | Other | N/A | 2 | CA | Update Area L2&L3 Area Displays |  | C2PP |  | TSRL | 2014-05-19 | 2014-11-01 |  |  | Medium 3-B | GESS | 2014-10-01 | GAWTOPER | WOSC | RPM4 | PRER | TRANSPIPE |  | unknown | ACCP | OSNO OSTS | 0
7003212 | Gas SCADA Change Requests | not present | Other | not present | - | - | Gas SCADA Change Requests | There is no form or process in place for requesting or tracking changes to the gas SCADA system beyond email exchanges with Gas Control Strategy & Support and the requesting party. With all of the rapid changes taking place with the gas system, we need a formal process for requesting display changes and corrections, and it would probably be a good idea to incorporate a formal review of these change requests to be sure they are correct before they are executed. In the past, a TSC form was used for this process, but no longer is being used, and it may not be adequate to the task anyway. http://www/tsconline/forms/ScadaGas/DispChangeOther. aspx | [7 empty] | Low 4-C | GESSO | 2014-12-31 |  |  | RPM4 | PRGS | OTHER
7003563 | Operating Modes of Topock and Hinkley | Topock Compressor Station Topock1 Plant B K Suct Press | OP | 2014-01-10 17:44 | 1 | CA | Operating Modes of Topock and Hinkley | Perform an assessment of Gas Control requested operating modes of Topock and Hinkley compressor stations to determine which requested modes are not documented and/or present significant risk for an operating error. Determine mitigation for risks and implement mitigation. For all other compressor stations around the system, survey the operating supervisors of those stations to determine if some operating modes at those stations create risk and what mitigation may be necessary. | DKM4 | GESS | TSRL | 2014-06-25 | 2017-12-31 |  |  | Medium 3-B | GESS | 2017-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | TP | unknown | REVW | OSNO OSTS | 0 |  | 6/26/2014 - During the Weekly OP Status Meeting on Thursday, Larry mentioned that CA's weren't assigned to a individual. Request for the appropriate task owner
7003563 | Perform PHA to Identify Safegaurds | Topock Compressor Station Topock1 Plant B K Suct Press | OP | 2014-01-10 17:44 | 3 | CA | Perform PHA to Identify Safegaurds | Perform PHA to identify and recommend appropriate safeguards for overpressure hazards for all modes of operation of the Topock compressor stations. Then, driven by the results of the survey, Gas Operations to establish procedures and training content for the most often encountered equipment specific abnormal operating condition | ARDD | GESS | TSRL | 2014-06-25 | 2017-12-31 |  |  | Medium 3-B | GESS | 2017-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | TP | unknown | REVW | OSNO OSTS | 0 |  | 6/26/2014 - During the Weekly OP Status Meeting on Thursday, Larry mentioned that CA's weren't assigned to a individual. Request for the appropriate task owner
7003563 | Reinforce Procedures on Gauging Ops | Topock Compressor Station Topock1 Plant B K Suct Press | OP | 2014-01-10 17:44 | 2 | CA | Reinforce Procedures on Gauging Ops | Reinforce procedures (with messaging to Gas T&D Operations) on gauging valves prior to manual operations, especially when valves are MAOP protection devices and are automatically controlled. | MDFL | GESS | TSRL | 2014-06-25 | 2017-12-31 |  |  | Medium 3-B | GESS | 2017-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | TP | unknown | REVW | OSNO OSTS | 0 |  | 6/26/2014 - During the Weekly OP Status Meeting on Thursday, Larry mentioned that CA's weren't assigned to a individual. Request for the appropriate task owner
7003662 | Gas Operations Technology Records | not present | Other | not present | - | - | Gas Operations Technology Records | Gas Control Strategy and Support does not have a system to create and centrally file records of technology and technology projects and initiatives for the control room. For example, records of the SCADA system, supporting technology and the video wall are not available proactively as part of projects. Sometimes they are created after a project is complete. The lack of records creates a knowledge gap when, for example experts leave the department and when clearances are to be evaluated. The records are a combinatio of inadequate, unavailable and incomplete. | [7 empty] | Low 4-C | GESSI | 2014-12-31 |  |  | GEG4 | PRIT | OTHER | EB
7004145 | M&C Gas JSSA & Tailboard Briefing | Vienna & Avalon SF | OP | 2013-05-06 10:00 | - | - | CA: Add language to inidcate the importance of over pressure event awareness in the Job Site Safety Tailboard | Add language to inidcate the importance of over pressure event awareness in the Job Site Safety Tailboard | [7 empty] | Low 4-C | GASCS | 2016-12-31 | [5 empty] | SF |  | ACCP |  |  |  | GCSS submitted a CAP suggesting JSSA document should have some context associated with bagging process and/or possible risk of OP
7004164 | C-37 Tapping, Bagging, etc - LP Gas Lines | Vienna & Avalon SF | OP | 2013-05-06 10:00 | - | - | CA: Last update was 1989 - update to current technologies or standard to modern time, to address over pressure events | Last update was 1989 - update to current technologies or standard to modern time, to address over pressure events | [7 empty] | Low 4-B | GASCD | 2016-12-31 | [5 empty] | SF |  | ACCP |  |  |  | GCSS submitted a CAP suggesting that Standard C-37 may need to be revised accordingly.
7004175 | Need Console Set up for GLS access | not present | Other | not present | - | - | Need Console Set up for GLS access | Request that gas strategy and support set up consoles that are not operational to have access to all GLS entries. At the present time if you are not logged in to a console you are unable to review GLS entries from alternate locations. 06/13/2014 09:15:55 Felina Lim (FPL3) Phone 925/328-5732 Risk Rationale: No threat to continuity of service 07/11/2014 10:38:02 Robert Mathews (RPM4) Phone 925/244-4573 Due date set at 9/1/14. Work on this has been in progress since Feb 2104 and is still undergoing testing. GDCC has the ability to look at the logs from SF or Brentwood from the log repository. The repository has all logs from all locations and all the operators have access to this shared drive. (Link: \\appgas01\Gas01\OPC\SHARE\GOCS) | [7 empty] | Low 4-B | GESSO | 2014-10-01 |  |  | RPM4 | PRGS | OTHER
7004358 | OP Event L172/169/167 N. of Hershey Sta | not present | OP | not present | 2 | CA | Removal of CROP on L172 | L-172, 167, and 169 are currently under a CROP of 708 psig. The removal of the CROP would potential restores MAOP/MOP of 800 psig that provides additional flexibility in avoiding OP events or near hits. The removal of the CROP on L-172, 167, 169 is to be determine. | K1BY |  | TSRL | 2014-07-09 | 2015-06-25 |  |  | Medium 3-B | GESS | 2015-06-25 |  | WOOP | DKM4 | PRIN | MEASCRTL | SA |  |  | OSNO OSTS
7004510 | Over pressure event -M-01 | not present | OP | not present | 4 | CA | Review Station Configuration | It was recommended by the local supervisor and also other subject matter experts during an OP Elimination Team meeting that Engineering design should review the reg station configuration. 08/14/2014 11:13:33 Jeffrey Cho (JHCQ) Phone 530/889-3191 THE FOLLOWING DOCUMENTATION WAS REQUESTED FROM T&R (G.ROBERTSON & J.GRACE). THIS DOCUMENTATION IS NECESSARY TO PERFORM ENGINEERING REVIEW: 1. Flow data at the time of the excursion, if available. 2. Pressure chart. 3. Did the RV activate? 4. Station configuration diagram (a sketch showing components and distances between them). 5. The CAP item comments (G.Robertson) state that a B-inspection was performed on this station in 2013 due to a similar event. We'll need the details of the event that triggered the B-inspection. | JHCQ |  | TSRL | 2014-07-29 | 2015-07-30 |  |  | Low 4-B | GESS | 2015-07-30 | GAWTOPER | WEER | DKM4 | PRIN | MEASCRTL | SI | unknown | ACCP | OSNO OSTS | 0 |  | Task Owner TBD
7004583 | OP Event Herrmann Station L-21 | not present | OP | not present | 7 | CA | CA: Rebuild Station | Currently there is a design critera to rebuild Herrmann Station, and convert its existing regulation to a dual run station. Rebuild station - there is a current design criteria to assess the rebuild of Herrmann Station. Based on the discussion with the Facilities engineer this will have the due date pushed out to 12/31/15 per past occurrences. the attached document is attached - and has not currently been approved in EDRS, but after this OP event, there will probably be additional push to complete the work. | JBCT |  | TSRL | 2014-07-15 | 2016-06-30 |  |  | Medium 3-B | GESS | 2016-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | NB |  | ACCP | OSNO OSTS
7004583 | OP Event Herrmann Station L-21 | not present | OP | not present | 6 | CA | CA: Update Documentation Consistency | Clarify the discrepancy between the OP diagram (MAOP 397 psig), and 086868 (from Crockett to MP 1.07 - MOP/MAOP 400/473 psig & MP 1.07 to Herrmann Station - MOP/MAOP 400/675 psig) Make the documentation consistent with the design criteria, op diagram, and 086868 | J3FB |  | TSRL | 2014-07-15 | 2016-06-30 |  |  | Medium 3-B | GESS | 2016-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | NB |  | ACCP | OSNO OSTS
7005066 | OP Near Hit Chestnut and Clay DREG | not present | Near Hit | not present | 6 | TA | TA: Engineering Analysis | Examine all stations (in the district) with SCADA and ER to determine if we have an OP risk. Special focus on those stations with common tap and sense lines and parallel runs. | BWW1 |  | TSRL | 2014-09-05 | 2015-11-01 |  |  | Medium 4-A | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | DISTMAINS | FR | true | ACCP | OSNO OSTS | 0
7005066 | OP Near Hit Chestnut and Clay DREG | not present | Near Hit | not present | 5 | CA | CA: Move SCADA tap line | Long term - Move the tap for SCADA to a location on the outlet pipe that is well downstream of the sense lines and outlet valves. | DABQ |  | TSRL | 2014-09-05 | 2015-11-01 |  |  | Medium 4-A | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | DISTMAINS | FR | true | ACCP | OSNO OSTS | 0
7005066 | OP Near Hit Chestnut and Clay DREG | not present | Near Hit | not present | 4 | CA | CA: Field Confirmation Testing | 1. Short term - Ensure that the following procedure is use for checking pressure at this station a. Check running reg and adjust pressure using the standard short line method. b. Switch the running reg and the standby reg by lowering the running reg set point to the standby reg set point. Then raise the standby reg to the normal running set point. c. Check the new running reg and adjust pressure using the short line method. | DABQ |  | TSRL | 2014-09-05 | 2015-11-01 |  |  | Medium 4-A | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | DISTMAINS | FR | true | ACCP | OSNO OSTS | 0
7005140 | DOLAN RD MAOP EXCEEDANCE L-301B V-0.01 | not present | OP | not present | 4 | TA | Review Gas Control Call-Out Process | The Dolan Rd Station Overpressure Event occurred after normal business hours, at approximately 0202. Gas Control did not contact the On-Call pipeline engineer per the current On-Call Schedule and process typically used. Gas Control called the area engineer, his supervisor, and an additional engineer from a nearby area. This delayed the response and could have resulted in further safety impacts. The on-call engineer was never contacted by Gas Control. Pipeline Services to communicate with Gas Control leadership and ensure all operators and coordinators are aware of the On-Call process and how to access the latest On-Call Schedule. | SRFA |  | TSOS | 2014-08-19 | 2014-12-31 |  |  | Medium 3-B | GESS | 2015-07-31 | GAWTOPER | WOGC | DKM4 | PRGS | MEASCRTL | CC | unknown | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | not present | Near Hit | not present | 7 | CA | CA: Sequence of Operations | There have been instances in the recent past at Milpitas Terminal where valve operations by the control room, have led to near hit over pressure events (precautions to OP Events). Upon switching the primary feeds to back up - it would be beneficial for the GSO to review a sequence of operations relating to this terminal specifically. This sequence should be provided to the control room and additionally be reiterated in a tailboard fashion. | AJW2 |  | TSRL | 2014-12-31 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | not present | Near Hit | not present | 6 | CA | CA: Load/Trimmer Control | There was discussion of ways to optimize the load/trimmer valves control. We discussed split range control and modifications to the existing algorithm. We agreed that modifications to the existing algorithm is best; split range control has been implemented at any site and it is best to implement it first at a simpler site. Changing the algorithm will take several steps. Mark Kazimirsky will create the modification and we will bench test it prior to implementation on site. After bench testing, we will implement it with one load/trimmer set on site. We will test it an confirm its operation; this will require district and GSO support. Once its been tested, Mark will modify the remaining load/trimmer sets off site. We'll have a return trip implement the remaining load/trimmer sets This again will require district and GSO support. The estimates time required for this work - 7/5 calendar days, and 12.5 man-days. Project impact - This will provide improved operation of the load trimmer valves. Their control is functional now, but can be improved. | DXH0 |  | TSRL | 2015-03-01 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | not present | Near Hit | not present | 5 | CA | CA: MOP Limits | The MOP at the station are used to limit set point entries. The set point limits are currently based upon an MOP list that does not reflect operational restrictions. These set point limits must be reviewed and perhaps modified. Additionally, the MOP change seasonally, so the program may need to be modified to accommodate seasonal changes. Mark Kazimirsky will provide a list of the current set point limits and the MPs used to create them. Sherkan will review this list, and work with GSO to establish set point limit criteria. Once that is complete, we'll make any changes. Project impact - the programming effort will be small. | DXH0 |  | TSRL | 2014-12-31 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005190 | OP Near Hit Milpitas Terminal | not present | Near Hit | not present | 4 | CA | CA: Set point Ramp Rate | Currently there is a set point ramp rate, which ramps the actual set point to desired (operator entered)set point value, rather than instantly changing I to the desired set point. This means that, following a significant set point change, the actual set point takes up an hour to reach the desired set point. We decided to consider changing this to allow quicker set point changes. Sherkan, Steven and GSO will discuss this to determine whether to: modify the program to allow changes to the ramp rate, change the ramp rate, change the GSO methodology, or leave the system as is. Once they're completed their review, we'll make any changes. There will be no actions taken until that review and recommendation is complete. Project impact - if we move forward with program changes, there will be some impact on the current project. | SXEV |  | TSRL | 2014-12-31 | 2015-06-01 |  |  | Medium 4-A | GESS | 2015-06-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | MH | true | ACCP | OSNO OSTS | 0
7005261 | UDN computer lock-up | not present | Other | not present | - | - | UDN computer lock-up | UDN network computers at GDCC back-up site @ 77 Beale st require administrator access to diable the screen saver feature to keep maps and other needed information on the screen without them locking us out. Screen saver feature needs to be disabled or the time needs to be extended. | [7 empty] | Low 4-C | GESSO | 2014-10-31 |  |  | RPM4 | PRIT | OTHER
7005263 | OP Near Hit 2290 14th Ave ERX, SF | not present | Other | not present | 5 | CA | CA: New ERX Location | Does this ERX require a new location? OR we will be leaving it where it is. Due date moved out to June to give time to provide discussion if this is the right place for the ERX, comments should encompass this upon reaching a solution. | K2BB | GESS | TSRL | 2014-09-03 | 2015-06-12 |  |  | Medium 4-A | GESSC | 2015-06-12 | GAWTEQU | WETE | DKM4 | PRIN | MEASCRTL | SF | true | ACCP | OSNO OSTS | 0 |  | Reference Notification # 7005255
7005524 | OP Near Hit C Street Martinez | C Street, L191 Martinez | Near Hit | 2014-08-20 11:26 | 4 | TA | Update the OP diagram | Task: Update the OP diagram This task is to update the OP diagram with the most recent changes that have occurred since the last revision based on the redlines drawings. Responsible: Lanthy Le Date: 12/1/14 | L1LO |  | TSRL | 2014-10-01 | 2015-12-01 |  |  | Medium | GESS | 2015-12-25 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | DI | unknown | ACCP | OSNO OSTS | 0
7005431 | OP Event Acacia Station | Acacia Station | OP | 2014-08-16 08:50 | 2 | TA | TA: CAP to perform RC under 7005698 | A CAP item has been initiated (7005698) for a RCA to be preformed on this - as there have been 5 events in 2014 This will be assigned to Larry Rochholz | LNR3 | GESS | TSRL | 2014-09-03 | 2015-09-18 |  |  | Medium 3-B | GESS | 2015-09-18 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | ST | unknown | ACCP | OSNO OSTS | 0 |  | Reference Notification # 7005698
7005527 | 445 Wawona St. ERX | not present | Near Hit | not present | 5 | CA | CA: New ERX Location | (SF_SF_S026) Does this ERX require a new location? OR we will be leaving it where it is. | K2BB |  | TSRL | 2014-09-04 | 2015-06-12 |  |  | Medium 4-A | GESS | 2015-08-26 | GAWTEQU | WETE | DKM4 | PRIN | MEASCRTL | SF | true | ACCP | NOPT OSNO OSTS | 0 |  | Reference Notification # 7005255
7005721 | OP Near Hit Kettleman Compressor Station | not present | Near Hit | not present | 5 | TA | Evaluate Station Controlled Configs | Please add a task to evaluate the use of the station configurations that are controlled by the station PLC. See attached. If we do decide to utilize the configurations, testing will need to be performed to verify the configurations work correctly, since they haven't been used since the station was built | RPG8 |  | TSRL | 2014-10-17 | 2015-12-01 |  |  | Medium 4-A | GESS | 2014-12-01 | GAWTOPER | WOGC | DKM4 | PRGS | COMPPROC | KT | true | ACCP | OSNO OSTS | 0
7005804 | Effective Assessment CAPN 7000090 | not present | Near Hit | not present | 1 | TA | Create Effectiveness Evaluation | Upon completion of this CAP item, create a new notification due in 6 to 12 months to evaluate whether the corrective actions implemented to address this issue had the desired effect. The notification should include a plan to review the corrective actions for effectiveness. The effectiveness assessment should consider: a. Any effectiveness measures established in the cause evaluation, b. Whether the corrective actions have been properly integrated into controlling the processes/procedures to ensure the corrective actions are sustained over time, c. That corrective actions did not result in any new performance problems, d. Any potential weaknesses in the corrective actions. | DKM4 | GESS | TSRL | 2014-09-10 | 2015-02-01 |  |  | Non-CAP | GESS | 2015-03-01 | GAWTEVAL | WEOO | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | Reference Notification # 7000090
7006231 | Gas SCADA Telecom Resiliency | not present | Near Hit | not present | 1 | CA | Develop Overall Plan to address |  | D3WN |  | TSOS | 2014-12-01 | 2015-02-01 |  |  | Medium | GESSO | 2015-03-01 | GAWTEQU | WETE | RPM4 | PRGS | MEASCRTL | ZS | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 11 | CA | CA: Update OM&I | 1. The OM&I needs to provide adequate information of how the blow down piping is used and definitely needs to instruct that V-23 be closed prior to a transmission blow down if there is no OPP. The following language was provided by Harpreet Johal: "If V-23 is OPEN, the section of pipe between V-24, V-26, & V-30 should be considered distribution (MAOP 27.5 psig). If V-23 is CLOSED, the section of pipe between V-24, V-26, & V-30 can be considered transmission (MAOP 473 psig)." | TWS4 |  | TSRL | 2014-10-27 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 10 | CA | CA: Tag blow down valves at station | 2. Temporarily (or possibly even long term), it might be a good idea to put a tag on V-24, V-26 and V-30 instructing any operator to ensure V-23 is closed prior to opening these valves. | HSJ3 |  | TSRL | 2014-10-27 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 8 | CA | CA: Design - Plant Engineering | There was a recent over pressure near hit at Herrmann & Crockett Stations caused by some valve sequences - OP diagrams were not updated to show that a blow off stack was shared by distribution, and transmission pressures. Additionally the distribution pressure feed into the stack remained open during the transmission valve throttling without any specific OPP device. Distribution Gas Incident, Notification, and Abnormal Report: 092414 Crocket Overpressure Event Basically, by the OP Diagram at Crockett Station (284254.pdf), V-23 is kept open to maintain pressure in the blow down stack, and V-30 was throttled. The stack pipe is rated for the transmission pressure, in throttling V-30 caused pressure to back into the distribution system almost over pressuring it. OP diagram will be submitted for updating in the near future by the PLE. " Is there any consideration to update the design of the station and installation of an OPP device on the D system if V23 is normally open? o An alternate solution to OPP and create two valve separation between transmission and distribution pressure systems would be to install a valve between the tap valve location of V-23, and where the pipe from V-24 ties into the blow down stack pipe. " Does a situation like V-23 (open valve between GD and GT blowdown piping) occur at any other stations within our gas system? | DTY1 |  | TSRL | 2014-10-15 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006072 | OP Near Hit Crockett Station | Crockett Station | Near Hit | 2014-09-24 12:04 | 6 | CA | CA: Update the Operating Diagram | During the fact finding in this event, you guys mentioned you had made some updates to the operating diagram. I would like to capture, that the OP diagram is being updated - this will be accounted for through a task in CAP. Once the OP diagram has been updated by the mapping group, you can go in and close out the item (or send one of us an email). | TWS4 |  | TSRL | 2014-10-14 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | NOPT OSNO OSTS | 0
7006220 | OP Near Hit Ryer Island, Los Medanos | Los Medanos Ryer Island | Near Hit | 2014-09-26 21:23 | 5 | CA | CA: Controls Engineering | In response to the OP Near Hit (More Details mentioned below), a corrective action has come out of the fact finding session: - Engage Controls Engineering team to evaluate the Ryer Island controls, monitoring points and alarm limits for appropriateness and identification of potential improvements - Since gas is being supplied by a 3rd party do we want to address the pressure alarm limitss and better to the MAOP as opposed to a listed MOP? - Or since the BTU ratio controls that V-716, Hown can we better this situation so more events are not forthcoming? | L1LO |  | TSRL | 2014-10-02 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | LM | unknown | ACCP | NOPT OSNO OSTS | 0
7006220 | OP Near Hit Ryer Island, Los Medanos | Los Medanos Ryer Island | Near Hit | 2014-09-26 21:23 | 4 | CA | CA: Long term corrective actions | The following corrective actions are to be analyzed by the PLE for their use and purpose of updating and maintaing the system. - Currently there is no contract with Vintage about gas delivery specifications (pressure, BTU content) - Potentially install regulation - Update OP diagram/map with current information relating to the owner being Vintage (not Shell/Chevron) | L1LO |  | TSRL | 2014-10-02 | 2015-12-01 |  |  | Medium | GESS | 2015-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | LM | unknown | ACCP | NOPT OSNO OSTS | 0
7006929 | OP Near Hit Atwater ERX, YO | Atwater (ERX) | Near Hit | 2014-11-07 | 2 | TA | AC: Reg did not lock up |  |  |  | TSOS |  |  |  |  | Medium | GESS | 2015-01-15 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | YO | unknown | ACCP | NOPT OSNO OSTS | 0
7006929 | OP Near Hit Atwater ERX, YO | Atwater (ERX) | Near Hit | 2014-11-07 | 1 | TA | EC: Equipment - Sulfur |  |  |  | TSOS |  |  |  |  | Medium | GESS | 2015-01-15 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | YO | unknown | ACCP | NOPT OSNO OSTS | 0
7003740 | Network Outage at San Ramon ODN | not present | Other | N/A | 3 | CA | Corrective Actions for CE report |  | RPM4 | GESSO | TSRL | 2014-11-01 | 2014-12-31 |  |  | Low | GESSO | 2014-12-31 | GAWTEQU | WETE | RPM4 | PRGS | OTHER |  | true | ACCP | OSNO OSTS | 0
7006880 | Potential OP Event-Sunnyvale HP Syst | not present | Other | N/A | - | - | 11/05/2014 10:08:34 Boris Andino (BFA1) Phone 925/244-4505 Lo-Lo Alarm breached at 19 psig on 11/3/14. C16 reg point raised by 1 psig for capacity reasons. Concern that the MAOP of the system could be breached given that the NOP is 27, and MAOP 30 psig. Setting the regulator to 28 psig leaves only 2 psig as buffer potentially creating an OP event if the regulator droop for more than 2 psig. update 11/19/2014 Spoke with Planning Engineer Justin Lau regarding this issue. Alarm limits were originally set too high and have been adjusted down. 19 psig was still low for the system during this time of year and further investigation revealed that the regulator setpoints had drooped from 25 psig. They were reset to 25 psig later in the week. No further action should be needed. |  | - |  | COMP | - | - | MND4 | 2014-12-02 | Medium | GESS | 2014-12-06 | GAWTOPER | WOGC | FWM1 | PRIN | MEASCRTL | SJ | unknown
7003740 | Network Outage at San Ramon ODN | not present | Other | N/A | 1 | CE | psig for capacity reasons. Concern that the MAOP of the system could be | Create a CE report for the incident requested by SCADA Manager for Gas Ops 5/29/2014 | LNR3 | GFSC | TSCO | 2014-10-01 | 2014-11-01 | LNR3 | 2014-08-25 | Low 4-B | GESSO | 2014-12-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER |  | true | ACCP | OSNO OSTS | 0
7003679 | OP Near Hit PLS-6A, 300A | not present | Near Hit | not present | 5 | CA | breached given that the NOP is 27, and MAOP 30 psig. Setting the | Through investigation of the relief valve it was determined that the SCADA transmitter from the relief valve was faulty and malfunctioning. This is what caused the second alarm. It was determined that this should be replaced. | M7CV | GESS | TSCO | 2014-05-14 | 2015-01-31 | AMFQ | 2014-11-18 | Medium 3-B | GESS | 2015-03-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 1 | CA | regulator to 28 psig leaves only 2 psig as buffer potentially creating | Implement better control scheme using "Valve Max" and pressure set point control algorithm similar to PLS 1,2, and 3 RTUs. | GPJ6 | GEDTS | TSCO | 2013-10-11 | 2014-12-01 | GPJ6 | 2014-11-25 | Medium 3-B | GESS | 2015-01-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 1 | JGP1 | Recently reassigned to Geoffrey Jarpe (GJP6) per comments from CAP as a part of personnel changes - email sent 4/24/14
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 2 | CA | an OP event if the regulator droop for more than 2 psig. | Controls Engineering to review potential for similar problem for other PLS stations that do not have the PLS 3 type RU ramp program applied. | GPJ6 | GEDTS | TSCO | 2013-10-11 | 2014-12-01 | GPJ6 | 2014-11-25 | Medium 3-B | GESS | 2015-01-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 1 | JGP1 | Recently reassigned to Geoffrey Jarpe (GJP6) per comments from CAP as a part of personnel changes - email sent 4/24/14
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 3 | CA | Frank,can you please complete in less than 2 weeks if possible. | No additional Description | GPJ6 | GEDTS | TSCO | 2013-10-11 | 2014-12-01 | GPJ6 | 2014-11-25 | Medium 3-B | GESS | 2015-01-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 1 | JGP1 | Recently reassigned to Geoffrey Jarpe (GJP6) per comments from CAP as a part of personnel changes - email sent 4/24/14
7005932 | OP Near Hit Ridgecrest Town, Kern | not present | Near Hit | not present | 4 | CA | Thanks | Transducer is believed to be the issue, a new one has been ordered to replace existing | R2GT |  | TSCO | 2014-09-19 | 2014-12-01 | KDSD | 2014-11-26 | Medium 4-A | GESS | 2015-02-25 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | KE | unknown | ACCP | NOPT OSNO OSTS | 0
7002952 | OP Near Hit Harding & Hunter LP Stockton | Harding & Hunter LP | Near Hit | 2014-04-09 02:25 | 2 | CA | CA: Contact Planning Regarding SetPoints | According to the Abnormal Incident Report, Harding and Hunter HIHI alarm breach was due to the setpoints changed for summer operation. GDCC will let planning know. E-mail has been sent out to GDCC for some follow ups/updates, see attachment list. | TRST |  | TSCO | 2014-04-23 | 2014-12-09 | AMFQ | 2014-10-24 | Medium 3-B | GESS | 2014-12-09 | GAWTOPER | WOOP | DKM4
7004510 | Over pressure event -M-01 | not present | OP | not present | 3 | TA | Notifying Gas Control of OP Events | After the OP event was discovered, the local supervisor submitted a CAP Notification regarding the pressure excursion at Reg Station M-01 (American Rice Dryer) that meet standard TD-4413P-02 Section 3.10: "All over pressurization events must be entered in the CAP database by the responsible department supervisor, manager, or delegate in accordance with Utility Procedure TD-4020P-01, "Gas Operations Corrective Action Program (CAP) Instructions"" However, GDCC wasnt notified of the pressure excursion at Reg Station M-01. Lesson Learned - Upon determining that a potential over pressurization event has occurred, it must be immediately notify to Gas Transmission Control Center or Gas Distribution Control Center. (Per TD-4413P-02 Section 3.3) | BSS2 |  | TSCO | 2014-07-09 | 2014-12-06 | AMFQ | 2014-11-17 | Low 4-B | GESS | 2015-07-30 | GAWTEVAL | WEER | DKM4 | PRIN | MEASCRTL | SI | unknown | ACCP | OSNO OSTS | 0
7005059 | OP Near Hit Alameda SHP ERX | not present | Near Hit | not present | 3 | CA | CA: System Review | Division will review the system, and see if pressure should be lowered on other stations to prevent future alarming. | E1H7 | GESS | TSCO | 2014-09-19 | 2014-11-15 | KDSD | 2014-10-16 | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0
7005059 | OP Near Hit Alameda SHP ERX | not present | Near Hit | not present | 6 | TA | TA: 5MM Bulleting about Settings | 5MM/Bulletin on Winter/Summer operations may need to be distributed |  |  | Unknown |  |  |  |  | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0 |  | Task #6 is not in SAP CAP; this task will be considered remove
7005059 | OP Near Hit Alameda SHP ERX | not present | Near Hit | not present | 5 | TA | TA: Summer and Winter Settings | GDCC notify Divisions of Summer Winter Settings. - What is the process that has been developed? What needs to be done to affirm this gets done? Schedule through SAP as a task annually. (May be through temporary clearances or temporary operational set point changes). Local Engineering - GDCC - I&R |  |  | TSCO |  |  | KDSD | 2014-09-19 | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0
7005059 | OP Near Hit Alameda SHP ERX | not present | Near Hit | not present | 4 | TA | TA: Historical Charts | Is there any additional historical reading throughout the summer that will show the over pressure event is accurate? Or chart? - Request from May 1st moving forward |  |  | TSCO |  |  | KDSD | 2014-09-19 | Medium 4-A | GESS | 2014-11-15 | GAWTOPER | WOGC | DKM4 | PRGS | TRANSPIPE | EB | true | ACCP | OSNO OSTS | 0
7005140 | DOLAN RD MAOP EXCEEDANCE L-301B V-0.01 | not present | OP | not present | 5 | CA | CA: PSRS 28501 - Dolan Rd Stat Rebuild | Option 2 - Expand scope of PSRS 28501 Dolan Rd Station Rebuild project scheduled for 2015 to include strength testing of this section of L-301B. Current scope is limited of valve extensions/gauge tap lines and atmosheric corrosion | SRFA |  | TSCO | 2014-08-26 | 2016-12-31 | KDSD | 2014-11-13 | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOGC | DKM4 | PRGS | MEASCRTL | CC | unknown | ACCP | NOPT OSNO OSTS | 0 |  | Reference Notification # 80001790
7005258 | OP Near Hit Swingle Station | not present | Near Hit | not present | 3 | TA | CA: Mention Hand Throttling in Next 5MM | The apparent cause of this HIHI breach was due to the qiuck hand throttling of L-119A (V-11.07). In Clearance 80000549 it stated "Slowly Open" V-11.07, it appears the crew opened V -11.07 too quickly causing a HIHI at Swingle Station. When re-energizing a line, extra pre-caution should be considered in valve operation. In the next 5MM, valve operation (reopening and/or closing of valves) will be mentioned to remind field crew of potential OP. | AMFQ |  | TSCO | 2014-08-26 | 2015-12-31 | AMFQ | 2014-10-20 | Medium 4-A | GESS | 2015-12-31 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7005489 | East Bay North SCADA Screen - ERRORS | not present | Other | not present | - | - | East Bay North SCADA Screen - ERRORS | There are errors on the East Bay North Citect SCADA screens. This is misleading and unsafe. The screen title is: East Bay - North (Lv3) There are two fields (one pressure and one flow) above the Herrmann field that are incorrect. The Vine Hill flows are also incorrect. Please reach out to me, KBH4, for more clarification. | [7 empty] | Low 4-B | GESSO | 2014-09-21 |  |  | RPM4 | PRGS | MEASCRTL | [6 empty] | Notification with no tasks/CA has been completed
7005556 | ERX HiHI alarm in SF | not present | Near Hit | not present | 3 | CA | CA: Share system pressure data with GDCC | See email attached... Way Ahead Work with Mike Fernande z and the GDCC to obtain approval for alarm set point increase at SCADA sites of higher elevation (IP) 09/16/2014 16:24:31 Michael Fernandez (MSFA) Phone 415/695-3312 Per email sent on 9/15/2014, Hi alarm set to 10"w.c. and Hi-Hi alarm set to 10.5"w.c. (consistent with Melissa Dunlap's email on alarm guidelines); however, the exception will be that if pressures exceed 10.5"w.c., immediate physical response would not be required by I &R. GDCC will notify local planner and I<(>&<)>R supervisor the next business day to coordinate response.These alarm set points can be also applied to the LP SCADA location at Taraval and Wawona as long as it is included as a location with the immediate response exception. | MSFA |  | TSCO | 2014-09-04 | 2014-12-29 | MSFA | 2014-09-16 | Medium 4-A | GESS | 2014-12-29 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | SF | true | ACCP | OSNO OSTS | 0
7005721 | OP Near Hit Kettleman Compressor Station | not present | Near Hit | not present | 4 | CA | CA: Address Training | Supervisor to address training in concerning this operating situation in the future with the GSO o Emphasis to use spill valves during the compression process during times when this operation is required in the future. | AJW2 |  | TSCO | 2014-09-04 | 2015-12-01 | KDSD | 2014-10-20 | Medium 4-A | GESS | 2014-12-01 | GAWTOPER | WOGC | DKM4 | PRGS | COMPPROC | KT | true | ACCP | OSNO OSTS | 0
7001410 | SCADA legacy field equip not reliable | not present | Other | not present | 1 | TA | EB Concentrator resolution plan | In talking with Wayne Fong this plan has been developed. As of 5/20 we are only waiting on Distribution to create orders for funding. | GPJ6 | GEDTS | TSCO | 2014-03-20 | 2014-05-01 | GPJ6 | 2014-05-20 | Medium 3-B | GESSO | 2015-06-01 |  |  | RPM4 | PRGS | MEASCRTL | EB |  | ACCP
7005161 | 1st Relo Exercise to SF Backup CTL CTR | not present | Other | not present | - | - | 1st Relo Exercise to SF Backup CTL CTR | SCADA Console on North desk was not functioning properly. The operator, Ray Cullins, reported that the SCADA Console was not abl to view data at Antioch terminal. Ray also reported all flows were displayed as #com. This issue was only visible on the North Console SCADA terminal. The reason this was a top priority was there was a major pigging operation occurring and it was imperativ that the operator was able to actively monitor pressures and flows. | [5 empty] | RPM4 | 2014-08-24 | Low 4-C | GESSO | 2014-09-07 | 5161 |  | RPM4 | PRGS | OTHER
7000371 | Over Pressure - Transmission - DFM 1024 | not present | OP | not present | 2 | CA | Clearance monitoring on DFM 1024-01 | Monitor system while on clearances. Possible solutions include install permanent or daily pressure check | J5LG | GAIFP | TSCO | 2013-09-30 | 2014-09-30 | KDSD | 2014-09-03 | Medium 3-B | GESS | 2014-09-30 | GAWTEQU | WEIR | DKM4 | PRIN | TRANSPIPE | NV | unknown | ACCP | OSNO OSTS | 0 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response.
7001745 | OP Near Hit Carmel Valley Reg Station | not present | Near Hit | not present | 1 | CA | CA: Confirm On-Call List | Confirm Carmel Valley on-call list has been establish | AMFQ |  | TSCO | 2014-02-18 | 2014-11-01 | AMFQ | 2014-08-27 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | CC | true | ACCP | NOPT OSNO OSTS | 0 |  | 4/24/14 - Emailed corrective action item owner to notify them of closing date is approaching soon 4/25/2014 - Emailed Tom Donabedian who was listed on TRAC's Need Help section for "Data Issues". Tom responsed on the same day that he hasn't been in the TRAC On-Call list loop for a while. He recommends that I contact TSC. A TSC Request Form was submitted and waiting for a response from TSC.
7005061 | OP Event Los Medanos SP3 | not present | Near Hit | not present | 4 | CA | CA: Replace Transducer | During the investigation - it was deteremined that the transducer (I to P) failed, affecting the regulator valve, and causing the station to go on monitor control. It is necessary to replace the transducer | DDT8 |  | TSCO | 2014-07-28 | 2014-12-01 | DDT8 | 2014-08-28 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOGC | DKM4 | PRIN | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7005431 | OP Event Acacia Station | Acacia Station | OP | 2014-08-16 08:50 | 1 | TA | Update PSRS 27086 job to rebuild station | PSRS should track this in the future… See email from WAG8 attached. This task will be closed out | WAG8 |  | TSCO | 2014-08-19 | 2014-09-18 | KDSD | 2014-09-03 | Medium 3-B | GESS | 2015-09-18 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | ST | unknown | ACCP | OSNO OSTS | 0
7000006 | Over Pressure - Low Pressure system | not present | OP | not present | 1 | CA | QA Audit-Revise WP 4540-01 dwnstrm-mon |  | GES6 |  | TSCO TSSC | 2012-04-25 | 2013-12-31 | FPL3 | 2013-10-24 | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL |  | unknown | ACCP | OSNO OSTS | 0
7000006 | Over Pressure - Low Pressure system | not present | OP | not present | 3 | TA | Created in error |  |  |  | TSCO | 2013-10-28 | 2013-10-28 | G1W6 | 2013-10-28 | Medium 3-B | GESS | 2016-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL |  | unknown | ACCP | OSNO OSTS | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 1 | CA | Clearance rights suspended |  | KCC7 |  | TSCO | 2013-05-29 | 2013-05-30 | A3L2 | 2013-08-02 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 10 | CA | QC of Clearance Coordinator work |  | RBQ2 |  | TSCO | 2013-06-10 | 2014-03-30 | FPL3 | 2013-12-23 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 1 | CMPN
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 11 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-11 | 2013-05-29 | RTG6 | 2013-06-11 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 12 | TA | coordinate |  | A3L2 |  | TSCO | 2013-11-12 | 2014-11-12 | A3L2 | 2014-02-25 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 13 | TA | EC: HF/WPE - Field O&M |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-04-01 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 14 | TA | AC: Valves turned past stops |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-04-01 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 2 | CA | Clearance identification points |  | KCC7 |  | TSCO | 2013-06-10 | 2013-06-24 | FPL3 | 2013-06-10 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 3 | CA | JSSA mandates |  | KCC7 |  | TSCO | 2013-06-10 | 2013-06-24 | TSN2 | 2013-06-10 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 4 | CA | Clearance Coordinator responsibilities |  | KAS5 |  | TSCO | 2013-06-10 | 2013-12-31 | FPL3 | 2013-12-24 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 5 | CA | Engineer review of clearances |  | RBQ2 | GEST | TSCO | 2013-06-10 | 2014-03-30 | LNR3 | 2014-03-25 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 1 | CMPN
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 6 | CA | Clearance qualifications |  | D0MN |  | TSCO | 2013-06-10 | 2013-06-17 | A3L2 | 2013-08-01 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 7 | CA | Inattention |  | D0MN |  | TSCO | 2013-06-10 | 2013-06-24 | A3L2 | 2013-08-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 8 | CA | Clearance detail |  | D0MN |  | TSCO | 2013-06-10 | 2013-07-31 | A3L2 | 2013-08-01 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000027 | 3602_385180.g06 - San Pablo OP | not present | Near Hit | not present | 9 | CA | Workload for clearance writing |  | D0MN |  | TSCO | 2013-06-10 | 2013-09-09 | A3L2 | 2013-08-01 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | MEASCRTL | EB | unknown | COMP | ATCO OSNO | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 13 | TA | Develop action plan to address inadequate design validation | The action plan will detail the following, including assignment and due dates: Include confirmation of response to all regulator failure modes in the commissioning process. | JGP1 | GEDTS | TSCO | 2014-04-09 | 2014-12-31 | K1F7 | 2014-07-09 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 3 | JGP1 | • Due date changed from Jan 31st, 2014 to Dec 31st, 2014 by John Phillips • Further Discussion with William Mojica and other Directors
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 1 | CA | Incorporate lesons learned in CAP |  | SEP1 | GFSC | TSCO | 2013-04-09 | 2013-07-31 | TSN2 | 2013-08-07 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 10 | TA | Prepare action plan to address ineffective design verification | The action plan will detail the following (including assignments and due dates): 1. Develop a more formal design review process that requires sign-off by PG&E Engineering Supervision Evaluate current process for review and approval of Design Criteria, Construction Drawings and other engineering/design deliverables. 2. Update process to require sign-off by the appropriate engineering/design supervisor Prepare an Action Plan. | DTY1 | GEDTT | TSCO | 2013-04-09 | 2014-01-31 | K1F7 | 2014-05-01 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Mojica has reviewed and approved. Need to review and obtain approval from issue owner, Dan Menegus- (4/14/14 from Don)
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 11 | TA | Develop an action plan to develop and issue a standard design | The action plan will detail the following (including assignments and due dates): Develop and issue a standard design, including commissioning procedures, for the use of speed controls and DNGPs on regulator and monitor valves a) Prepare a guideline for Regulator Station Design. | DTY1 | GEDTT | TSCO | 2013-04-09 | 2014-01-31 | K1F7 | 2014-05-01 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Close this action after meeting with Dan Menegus
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 12 | TA | Develop an action plan to develop and issue a standard design | The action plan will detail the following including assignments and due dates: Develop and issue a standard design, including commissioning procedures, for the use of speed controls and DNGPs on regulator and monitor valves a) Prepare a guideline for Commissioning Regulator Stations. Needs to consider existing Utility Procedure TD-4550P-07, Gas Transmission Station Commissioning. Require sign-off approval of the Functional Checkout Procedure (FCP) prior to testing, and test acceptance upon completion of the testing, by both Engineering and Operations | JGP1 | GEDTS | TSCO | 2014-04-09 | 2014-12-31 | KDSD | 2014-06-25 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 3 | JGP1 | • Due date changed from Jan 31st, 2014 to Dec 31st, 2014 by John Phillips • Further Discussion with William Mojica and other Directors
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 14 | TA | Develop a weekly OP Event status call |  | SEP1 | GFSC | TSCO | 2013-04-09 | 2013-04-09 | TSN2 | 2013-04-09 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 15 | TA | Determine sourcing lead | Develop a receipt inspection process that assigns clear accountability for inspection of products/material received to assure compliance with what was ordered and is based on approved vendor drawings | DTY1 | GEDTT | TSCO | 2013-04-09 | 2014-01-31 | K1F7 | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14: Recommend opening a new notification and C/A - Follow up with Randy's successor, Ashikur Khan. 05/08/2014 it was closed out.
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 16 | TA | Determine appropriate owner within Gas C |  | SEP1 | GFSC | TSCO | 2013-04-09 | 2013-04-19 | SEP1 | 2013-10-29 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 2 | CA | Legacy Event 4009: Failure 1 Action 3 |  | K2MJ |  | TSCO | 2013-03-27 | 2013-03-27 | FPL3 | 2013-09-03 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 3 | CA | Legacy Event 4009: Failure 1 Action 1 |  | RRMV |  | TSCO | 2013-03-27 | 2013-03-27 | G1W6 | 2013-03-27 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 4 | CA | Legacy Event 4009: Failure 1 Action 2 |  | J1KS |  | TSCO | 2012-12-23 | 2012-12-23 | G1W6 | 2012-12-23 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 5 | CA | Ambiguous procedural requirements |  | DTY1 |  | TSCO | 2013-07-24 | 2013-08-31 | TSN2 | 2013-08-14 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 6 | CA | Ambiguous procedural requirements |  | DTY1 |  | TSCO | 2013-07-24 | 2013-09-30 | FPL3 | 2013-09-04 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 7 | CE | Create CE Report |  | RTG6 | GFSC | TSCO | 2013-03-20 | 2013-03-25 | RTG6 | 2013-03-20 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 8 | CE | Create CE Report |  | JXVB | GFSC | TSCO | 2013-05-28 | 2013-06-02 | RTG6 | 2013-06-11 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | not present | 9 | TA | Prepare action plan to address inadequat |  | MDO1 |  | TSCO | 2013-04-09 | 2013-12-31 | MDO1 | 2013-11-05 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000028 | SR-036 Over Pressure - Trans Creed | not present | OP | 2012-12-23 00:45 | 17 | CA | Research industry regs for press control | "Research industry rules and regulations, industry association guidelines, company standards and other sources of information" regarding the design, maintenance, and operation of pressure regulation stations. Terry White has hired an outside industry expert to perform this assessment. | TGW5 | GAIF | TSCO | 2013-12-16 | 2014-06-30 | TGW5 | 2014-06-06 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0 |  | Further Discussion with William Mojica and other Directors
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | not present | 1 | TA | Coordinate |  | FPL3 | GFSC | TSCO | 2013-12-13 | 2014-12-31 | FPL3 | 2014-02-12 | Medium 3-B | GESS | 2016-01-31 | GAWTOPER | WOSC | DKM4 | PRGS |  |  | unknown | ACCP | OSNO OSTS | 0
7000046 | Network Issues Impacting Gas SCADA Oper | not present | Other | N/A | 2 | CA | Develop Corrective Action | Corrective Actions Identified in Cause Analysis: Analysis completed in July 2013 | RPM4 | GESSO | TSCO | 2013-11-15 | 2014-07-01 | RPM4 | 2013-08-01 | Medium 3-B | GESSO | 2016-01-31 | GAWTOPER | WOSC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 2 | FPL3
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | not present | 1 | CE | Perform Cause Evaluation |  | JXVB | GFSC | TSCO | 2013-10-29 | 2013-11-08 | JXVB | 2013-11-07 | High 2-B | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 4/21/14 Complete/Closed
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | not present | 2 | CA | Non-std locking device | Remove existing chain locking device. Install standard new locking device | OXG3 | GEOTA | TSCO | 2013-11-07 | 2013-12-31 |  | 2014-04-21 | High 2-B | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 4/21/14 Complete/Closed E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7000090 | Over Pressure - Low Pressure system - SJ | not present | OP | not present | 3 | CA | Upgrade valve system | Upgrade valve system to prevent valve from being operated beyond the closed position | OXG3 | GEOTA | TSCO | 2013-11-07 | 2014-12-31 |  | 2014-04-21 | High 2-B | GESS | 2015-01-31 | GAWTOPER | WOOP | DKM4 | PRGS | DISTMAINS | SJ | unknown | ACCP | NOPT OSNO OSTS | 0 |  | 4/21/14 Complete/Closed E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 2 | CA | Update TD-4125P-06 for updates on relief | Standards and procedures to update standard TD-4125P-06 to address gas relief valves specifically | J011 | GACSG | TSCO | 2014-03-06 | 2015-03-20 | J011 | 2014-07-17 | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 0 |  | Jennifer Scroggins "Information in this CAP Notification is being transferred to ECTS document number TD-4125P-06 for further action"
7000101 | Over Pressure - Transmission/Yuba City | not present | OP | not present | 1 | CE | Root Cause evaluation |  | LNR3 | GFSC | TSCO | 2013-10-29 | 2014-03-01 | LNR3 | 2014-03-06 | Medium 3-B | GESS | 2015-04-20 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SI | unknown | ACCP | NOPT OSNO OSTS | 1 | A3L2
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 4 | TA | EC: HF/WPE - Gas Control |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-05-31 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 0
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 5 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-05-31 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 0
7000105 | Close Call - Near Hit,Escaping Gas PLS4B | not present | Near Hit | not present | 6 | TA | AC: Relief valve stuck 'open' position |  | KDSD | GESS | TSCO | 2014-03-06 | 2014-05-31 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-31 |  |  | DKM4 |  | TRANSPIPE | KT | true | ACCP | OSNO OSTS | 0
7000130 | 3669_LT-210C_ | not present | Other | 2013-05-21 14:38 | 5 | CA | Establish two MSAs | Entered on behalf of Roy Green. Establish 2 Master Service Agreements, one with Team Industrial and second with TDW for Gas Hot Tapping and Plugging Services. | RCGP | GECTN | TSRL | 2014-01-14 | 2014-06-30 | Reassigned to Pierre Bigras | Notification Reassigned | Medium 3-C |  | 2014-07-19 |  |  | DKM4 |  |  | NB | unknown | ACCP |  |  |  | 6/19/2014 - a reminder was sent via e-mail to the task owner regarding this item. On 07/09/2014, Larry contacted GCSS that this has been reassigned to any other Notification Owner Pierre Bigras. This line item will be considered others/not associated with GCSS and will not be track at this point.
7000130 | 3669_LT-210C_ | not present | Other | 2013-05-21 14:38 | 2 | TA | Develop Corrective Action Plan | Changed finish date per verbal from Pierre Bigras | JYB9 | GECTN | TSCO | 2013-11-06 | 2014-06-30 | AMFQ | 2014-07-07 | Medium 3-C |  | 2014-07-19 |  |  | DKM4 |  |  | NB | unknown | ACCP |  |  |  | 6/19/2014 - a reminder was sent via e-mail to the task owner regarding this item
7000130 | 3669_LT-210C_ | not present | Other | 2013-05-21 14:38 | 3 | CA | Contractor Vetting | Contractors to have certifications, job skills, and qualifications, checked prior to being awarded contracts. Changed finish date per verbal from Pierre Bigras | J2TA | GFC | TSCO | 2013-11-20 | 2014-06-30 | AMFQ | 7/3/014 | Medium 3-C |  | 2014-07-19 |  |  | DKM4 |  |  | NB | unknown | ACCP |  |  |  | 6/19/2014 - a reminder was sent via e-mail to the task owner regarding this item
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 1 | CA | Communication gap |  | DRWI |  | TSCO | 2013-06-17 | 2013-06-28 | FPL3 | 2013-08-28 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 0
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 2 | CA | OPP not provided |  | DRWI |  | TSCO | 2013-06-17 | 2013-07-31 | FPL3 | 2013-08-28 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 0
7000131 | OP_Britton Ranch Washoe Ave Firebaugh | not present | OP | not present | 4 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-05-02 | 2013-06-27 | RTG6 | 2013-06-19 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | YO | unknown | ACCP | OSNO OSTS | 0
7000132 | 3628_LT-177A_Over Pressurization | not present | OP | not present | 2 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-30 | 2013-07-03 | RTG6 | 2013-06-18 | Medium 3-B | GESS | 2014-09-18 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | HB | unknown | ACCP | OSNO OSTS | 0
7000134 | Reg Stat Maint - Unplanned Outage/Fresno | not present | Other | not present | 1 | CE | Create CE Report |  | SMW7 | GFSC | TSCO | 2013-04-24 | 2013-06-26 | RTG6 | 2013-06-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOUP | DKM4 | PRGS | TRANSPIPE | FR | unknown | ACCP | ATCO OSNO | 0
7000134 | Reg Stat Maint - Unplanned Outage/Fresno | not present | Other | not present | 2 | CE | CE Please use HFACS |  | SMW7 | GFSC | TSCO | 2013-04-24 | 2013-06-26 | RTG6 | 2013-06-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOUP | DKM4 | PRGS | TRANSPIPE | FR | unknown | ACCP | ATCO OSNO | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 1 | CA | Recalibrate |  | EKK4 |  | TSCO | 2013-07-01 | 2013-08-02 | TSN2 | 2013-08-19 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 2 | CA | design / Construct |  | RJWS | GAIFP | TSCO | 2013-07-01 | 2014-03-31 | TGW5 | 2014-03-28 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 3 | CA | Assessment |  | DRJ4 |  | TSCO | 2013-07-02 | 2013-12-31 | KLCP | 2013-12-30 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 4 | CE | Create CE Report |  | JXVB | GFSC | TSCO | 2013-04-08 | 2013-06-20 | RTG6 | 2013-06-20 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0
7000136 | Over Pressure - Transmission Sacramento | not present | OP | not present | 5 | CA | Reduce NOP | No additional Description | TMRO | GEOTC | TSCO | 2013-12-30 | 2014-03-07 |  | 2014-04-18 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | SA | unknown | ACCP | OSNO OSTS | 0 |  | A reminder e-mail was sent out; however, Frank will be contacting Todd Rehrer regarding this overdue CA.
7000240 | Novato Blvd DFM Overpressure | not present | OP | not present | 1 | TA | Coordinate |  | KWD3 |  | TSCO | 2013-12-02 | 2014-12-02 | KWD3 | 2013-12-02 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NB | unknown | ACCP | ATCO NOPT OSNO | 0
7000240 | Novato Blvd DFM Overpressure | not present | OP | not present | 2 | TA | AC: Excessive Sulfur that plugged plilot |  | AMFQ |  | TSCO | 2014-03-12 | 2014-03-12 | AMFQ | 2014-03-12 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NB | unknown | ACCP | ATCO NOPT OSNO | 0
7000240 | Novato Blvd DFM Overpressure | not present | OP | not present | 3 | TA | AC: Low or No-Flow Conditions Mooney |  | AMFQ |  | TSCO | 2014-03-12 | 2014-03-12 | AMFQ | 2014-03-12 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NB | unknown | ACCP | ATCO NOPT OSNO | 0
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 1 | CA | Design Criteria | Require that design criteria consider all regulator failure modes | KMKU | GEDTD | TSCO | 2013-07-12 | 2014-03-31 | KDSD | 2014-05-15 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0 |  | Confirm with Jarpe and Menegus. 5/15/2014 it was closed out.
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 2 | CA | Design Review Process | Develop a more formal design review process that requires sign-off by PG&E Engineering Supervision | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Close this action item after meeting with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 3 | CA | Develop Standard Design (GE/Becker) | Corrective action plan requires discussion to confirm scope of work. Develop and issue a standard design, including commissioning procedures for the GE-Becker DNGPs on regulator and monitor valves\. | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Refer to CAP Notification 7000728 description for discussion of changing from pressure control to flow control and impact on operatio of the regulator
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 4 | CA | Functional Checkout Procedure (FCP) |  | JGP1 |  | TSCO | 2013-07-12 | 2013-07-15 | FPL3 | 2013-09-06 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 5 | CA | Corrective Action Program |  | SEP1 | GFSC | TSCO | 2013-07-12 | 2013-07-15 | TSN2 | 2013-08-07 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 6 | CA | Power Gas Controls Configuration | Corrective action plan requires discussion to confirm scope of work. Develop and implement a process to verify power gas controls are configured correctly for all similar actuator configurations. | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 1 | FPL3 | 5/6/14: closed out: Confirm with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 7 | CA | Validation | Corrective action plan requires discussion to confirm scope of work. The action plan will detail the following: 1. Verification of response to all regulator failure modes 2. Verification of response in all environmental conditions 3. Continue RCA of GE-Becker actuator system | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-05-08 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 1 | FPL3 | 5/8/14 closed out: Close this action item after meeting with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 8 | CA | Validation | Corrective action plan requires discussion to confirm scope of work. The action plan will detail the following: 1. Determine if new regulation is required at Creed Station if TD-4430-B rev. 1 cannot be implemented on L-210. 2. Continue to investigation as to origin of unanticipated system upset | DTY1 | GEDTT | TSCO | 2013-07-12 | 2014-01-31 | KDSD | 2014-04-28 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 2 | FPL3 | 5/8/14 closed out: Close this action item after meeting with Dan Menegus
7000278 | Over Pressure - Transmission - Creed | not present | OP | not present | 9 | CE | Create CE Report |  | JXVB | GFSC | TSCO | 2013-06-04 | 2013-06-09 | RTG6 | 2013-06-19 | Medium 3-B | GESS | 2014-07-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | RV | unknown | ACCP | OSNO OSTS | 0
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 1 | CA | Gauging inadequate |  | JGJ4 |  | TSCO | 2013-05-16 | 2013-05-29 | FPL3 | 2013-08-02 | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 3 | CA | Supervisory observation |  | JGJ4 |  | TSCO | 2013-05-16 | 2013-07-17 | FPL3 | 2013-09-01 | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000279 | Over Pressure - Transmission - Modesto | not present | OP | not present | 4 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-11 | 2013-06-28 | RTG6 | 2013-05-16 | Medium 3-B | GESS | 2018-02-04 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | TR | unknown | ACCP | OSNO OSTS | 0
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 1 | CA | CA: Replacing RTU at the location | The existing RTU at 34th and Telegraph, Oakland is to be replaced with a new RTU | LXPM | GECDE | TSCO | 2013-04-29 | 2014-05-16 | M4S6 | 2014-03-31 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 1 | AMFQ | 4/24/14 - JO number 30988380 was provided on 4/3/14 - check back if comepleted at the beginning of May. SAP does not show this is completed as of 4/24/14 4/30/14 - E-mailed Tasha Capen to obtain an update on the RTU replacement at 34th and Telegraph 5/21/14 - Closed out by Matt Sanders and suggest a new task for Michael Graham (MRG2) should be created to follow up on bringing the RTU back online.
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 2 | CE | Create CE Report |  | LNR3 | GFSC | TSCO | 2013-04-11 | 2013-05-03 | RTG6 | 2013-04-29 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 0
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 3 | TA | AC: Comm Failure |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 0
7000330 | Over Pressure - Low Pressure system | not present | Near Hit | not present | 4 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-05-31 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | EB | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 1 | CA | Communication |  | AJW2 |  | TSCO | 2012-12-13 | 2012-12-13 | FPL3 | 2013-07-29 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 2 | CA | Communication/Change settings |  | AJW2 |  | TSCO | 2012-12-13 | 2012-12-13 | FPL3 | 2013-07-29 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 3 | CA | Implement 5/20 plan | Implement 5/20 rule for SP3 to potentially prevent future over pressure events | GJG3 | GESPB | TSCO | 2012-12-13 | 2014-03-31 |  | 2014-04-01 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000333 | Over Pressure - Transmission - Antioch | not present | OP | not present | 4 | CE | Complete Causal evaluation |  | LNR3 | GFSC | TSCO | 2012-12-13 | 2013-01-18 | LNR3 | 2012-12-13 | Medium 3-B | GESS | 2014-03-31 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | LM | unknown | ACCP | OSNO OSTS | 0
7000371 | Over Pressure - Transmission - DFM 1024 | not present | OP | not present | 1 | CA | Adjust Regs to meet manufacturers specs | Establish a regulation and safety system that ensures operational load meets manufacturer's spec. Possible solutions include: 1. Replace regulators with recommended manufacturer's spec (correct size) 2. Uprate L-177B and DFM 1024-01 with L-177A MAOP at 819 psig and eliminate Grape Way Reg Station | J5LG | GAIFP | TSCO | 2013-09-30 | 2014-09-30 | KDSD | 2014-06-19 | Medium 3-B | GESS | 2014-09-30 | GAWTEQU | WEIR | DKM4 | PRIN | TRANSPIPE | NV | unknown | ACCP | OSNO OSTS | 0 |  | 6/19/14 - Email reminder sent out to responsible party - awaiting response. 6/19/2014 - Completed
7000723 | Gas Control/Gas Dispatch Phone Issues | N/A | Other | N/A | 2 | TA | Develop Corrective Action Plan |  | NXF5 | GESSO | TSCO | 2013-12-16 | 2014-07-01 | FPL3 | 2014-06-25 | Medium 4-A | GESSO | 2014-08-01 | GAWTOPER | WOGC | RPM4 | PRGS | OTHER | MI | unknown | ACCP | OSNO OSTS | 2 | RPM4
7001195 | OP Near Hit Station # R-H02 Richmond | not present | Near Hit | not present | 1 | TA | Coordinate Corrective Actions |  | LNR3 |  | TSCO | 2014-01-09 | 2014-03-01 | LNR3 | 2014-02-28 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | EB | true | ACCP | ATCO OSNO | 0
7001195 | OP Near Hit Station # R-H02 Richmond | not present | Near Hit | not present | 2 | TA | AC: Work Procedure |  | KDSD | GESS | TSCO | 2014-03-12 | 2014-03-12 | KDSD | 2014-03-12 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | EB | true | ACCP | ATCO OSNO | 0
7001195 | OP Near Hit Station # R-H02 Richmond | not present | Near Hit | not present | 3 | CA | CA: Training Tailboard |  | KDSD |  | TSCO | 2014-03-12 | 2014-12-02 | AMFQ | 2014-03-24 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | EB | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | not present | Near Hit | not present | 1 | TA | Coordinate |  | JXVB |  | TSCO | 2014-01-07 | 2014-12-31 | JXVB | 2014-01-07 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | not present | Near Hit | not present | 2 | CA | CA: Update MOP on Op Diagram |  | TXPS | GESS | TSCO | 2014-01-07 | 2014-06-30 | TXPS | 2014-03-20 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | not present | Near Hit | not present | 3 | TA | AC: Leaking Valve |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | not present | Near Hit | not present | 4 | TA | EC: Equpiment - Other |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001210 | OP near hit - Paramount Farm D/S of V-18 | not present | Near Hit | not present | 5 | TA | EC: HF/WPE - Other |  | AMFQ |  | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | YO | true | ACCP | ATCO OSNO | 0
7001256 | OPE Concord Mtr Station D/S of V-12 & 13 | not present | OP | not present | 1 | TA | Coordinate |  | LNR3 |  | TSCO | 2014-01-10 | 2015-01-10 | LNR3 | 2014-03-14 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | unknown | ACCP | ATCO OSNO | 0
7001315 | Topock Suction Pipe OP 2 Events-1/10/14 | not present | OP | not present | 1 | TA | Coordinator for OP at Topock |  | LNR3 |  | TSCO | 2014-01-15 | 2014-03-01 | LNR3 | 2014-02-27 | Medium 3-B | GESS |  | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC | TP | unknown | ACCP | ATCO OSNO | 0
7001315 | Topock Suction Pipe OP 2 Events-1/10/14 | not present | OP | not present | 2 | CE | Coordinate interviews. |  | LNR3 |  | TSCO | 2014-01-17 | 2014-03-16 | LNR3 | 2014-03-07 | Medium 3-B | GESS |  | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC | TP | unknown | ACCP | ATCO OSNO | 1 | LNR3
7001340 | OP Eureka LP System | not present | OP | not present | 1 | TA | Gas OP on LP system in Eureka |  | LNR3 |  | TSCO | 2014-01-16 | 2014-03-01 | LNR3 | 2014-02-27 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001340 | OP Eureka LP System | not present | OP | not present | 2 | TA | AC: Reg & Monitor set point too close |  | AMFQ |  | TSCO | 2014-03-11 | 2014-03-11 | AMFQ | 2014-03-11 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001340 | OP Eureka LP System | not present | OP | not present | 3 | CA | CA: Reg Set Point Lowered to 8" WC |  | WDBA |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001340 | OP Eureka LP System | not present | OP | not present | 4 | CA | CA: Increase MAOP to 14" WC |  |  |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | DISTMAINS | HB | unknown | COMP | ATCO NOPT OSNO | 0
7001390 | Overpressure Event 4022- El Dorado Hills | not present | OP | not present | 1 | CA | Ensure facilities comply w/ Gas Std H-14 | Develop program to bring Mooney Regs max 350psig differential in compliance with GS H-80.3 | TGW5 |  | TSCO | 2014-04-01 | 2014-05-01 |  | 2014-04-22 | Medium 3-B | GESS | 2014-05-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SI | unknown | ACCP | NOPR OSTS | 0
7001442 | Swingle Station "Overpressure" 1-29-14 | not present | Near Hit | not present | 1 | TA | AC: Hand Throttle Valve |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GAIFP |  | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SA | unknown | REVW | OSNO OSTS | 0
7001442 | Swingle Station "Overpressure" 1-29-14 | not present | Near Hit | not present | 2 | TA | EC: HF/WPE - Field O&M |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GAIFP |  | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SA | unknown | REVW | OSNO OSTS | 0
7001442 | Swingle Station "Overpressure" 1-29-14 | not present | Near Hit | not present | 3 | CA | CA: Tailboard Prior to the Clearance |  | OXM1 |  | TSCO | 2014-03-05 | 2014-03-31 |  | 2014-04-02 | Medium 3-B | GAIFP |  | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE | SA | unknown | REVW | OSNO OSTS | 0
7001532 | OP Event Center St. DFM Press | not present | OP | not present | 1 | TA | AC: 8" Mooney Reg Optimum Range 10-80% |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | EB | unknown | ACCP | ATCO NOPT OSNO | 0
7001532 | OP Event Center St. DFM Press | not present | OP | not present | 2 | CA | CA: Lowered Reg Down |  | DMRU |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | EB | unknown | ACCP | ATCO NOPT OSNO | 0
7001546 | OP Near Hit Brentwood Terminal | not present | Near Hit | not present | 2 | TA | AC: Leaking Valve |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0
7001546 | OP Near Hit Brentwood Terminal | not present | Near Hit | not present | 3 | TA | EC: Equipment - Other |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0
7001546 | OP Near Hit Brentwood Terminal | not present | Near Hit | not present | 1 | CA | CA: Validate & Update MAOP Doc | Validate the MAOP D/S of V-65 in Brentwood Terminal to be 867 psig in accordance with PG&E standards and work with Mapping in updating operating diagram | SXEV |  | TSCO | 2014-02-19 | 2014-06-30 | SXEV | 2014-06-26 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0 |  | 4/25/2014 - Sherkan has contacted the lead Map Tech and waiting for a response from the Map Tech. More follow up from Sherkan is anticipated regarding this CA. 5/30/2014 - Will be completed within the next couple of weeks from an email sent by the task owner
7001745 | OP Near Hit Carmel Valley Reg Station | not present | Near Hit | not present | 2 | TA | AC: Gauge Accuracy |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | CC | true | ACCP | NOPT OSNO OSTS | 0
7001745 | OP Near Hit Carmel Valley Reg Station | not present | Near Hit | not present | 3 | TA | EC: Equipment - Other |  | AMFQ | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | CC | true | ACCP | NOPT OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 1 | TA | AC: Mon. and Reg. set points too close |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 2 | TA | AC: Monitor set incorrectly: clearance? |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 3 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 4 | TA | EC: HF/WPE - Field O&M |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 5 | TA | EC: Set Point to close to MOP |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7001977 | Lomita Park OP Event of 145 psig system | not present | OP | not present | 6 | CA | CA: Immediate Response |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | LNR3 | 2014-03-05 | Medium 3-B | GESS | 2015-02-01 | GAWTOPER | WOOP | DKM4 |  | MEASCRTL | MH | unknown | ACCP | OSNO OSTS | 0
7002021 | OP Near Hit at West Capital & 5th in Sac | not present | Near Hit | not present | 1 | CA | CA: Repair Phone Line |  | TMRO | GESS | TSCO | 2014-02-25 | 2014-08-31 |  | 2014-04-18 | Low 4-D | GESS | 2014-12-01 | GAWTOPER | WOSC | DKM4 | PRIN | MEASCRTL | SA | unknown | ACCP | OSNO OSTS | 0 |  | A reminder e-mail was sent out; however, Frank will be contacting Todd Rehrer regarding this overdue CA.
7002021 | OP Near Hit at West Capital & 5th in Sac | not present | Near Hit | not present | 2 | TA | AC: Phone Line Failure |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-D | GESS | 2014-12-01 | GAWTOPER | WOSC | DKM4 | PRIN | MEASCRTL | SA | unknown | ACCP | OSNO OSTS | 0
7002021 | OP Near Hit at West Capital & 5th in Sac | not present | Near Hit | not present | 3 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Low 4-D | GESS | 2014-12-01 | GAWTOPER | WOSC | DKM4 | PRIN | MEASCRTL | SA | unknown | ACCP | OSNO OSTS | 0
7002166 | OP Near Hit Los Banos #4 | not present | Near Hit | not present | 1 | TA | AC: Calibration Issues |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-07-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | YO | true | ACCP | OSNO OSTS | 0
7002166 | OP Near Hit Los Banos #4 | not present | Near Hit | not present | 2 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-05 | 2014-03-05 | KDSD | 2014-03-05 | Medium 3-B | GESS | 2014-07-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | YO | true | ACCP | OSNO OSTS | 0
7002166 | OP Near Hit Los Banos #4 | not present | Near Hit | not present | 3 | CA | CA: Replace transducer at reg station | Transducer is to be replaced | JNL4 | GESS | TSCO | 2014-03-05 | 2014-06-01 |  | 2014-04-24 | Medium 3-B | GESS | 2014-07-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | YO | true | ACCP | OSNO OSTS | 0 |  | 4/24/14 - JO number 42078493 was provided on 3/6/14 - check back if comepleted at the beginning of May. Construction complete 4/8/14 - task not yet closed in SAP, CAP will close this out based on the information provided
7002167 | OP Near Hit 22nd and 24th Dist, SAC | not present | Near Hit | not present | 1 | TA | EC: Equipment - Other |  | KDSD | GESS | TSCO | 2014-03-07 | 2014-06-06 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRGS | MEASCRTL | SA | true | COMP | ATCO NOPR | 0
7002167 | OP Near Hit 22nd and 24th Dist, SAC | not present | Near Hit | not present | 2 | TA | AC: Gauge Accuracy/Calibration |  | KDSD | GESS | TSCO | 2014-03-07 | 2014-06-07 | KDSD | 2014-03-11 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRGS | MEASCRTL | SA | true | COMP | ATCO NOPR | 0
7002167 | OP Near Hit 22nd and 24th Dist, SAC | not present | Near Hit | not present | 3 | CA | CA: Replace Transducer |  | TMRO | GESS | TSCO | 2014-03-07 | 2014-03-07 | AMFQ | 2014-03-07 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRGS | MEASCRTL | SA | true | COMP | ATCO NOPR | 0
7002300 | OP Near Hit Los Medanos Ryer Island | not present | Near Hit | not present | 1 | TA | AC: Typical Operation |  | AMFQ |  | TSCO | 2014-03-19 | 2014-04-01 |  | 2014-04-01 | Medium 3-B | GESS |  | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | DI | true | ACCP | OSNO OSTS | 0
7002301 | OP Near Hit Aborn & White L100 San Jose | not present | Near Hit | not present | 1 | TA | AC: Low or No-Flow Conditions |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-25 | AMFQ | 2014-03-25 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | ATCO OSNO | 0
7002301 | OP Near Hit Aborn & White L100 San Jose | not present | Near Hit | not present | 2 | CA | CA: Lowered Mixer Press Milpitas Term |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-19 | AMFQ | 2014-03-19 | Medium 3-B | GESS | 2014-04-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | ATCO OSNO | 0
7002401 | Over pressure event Rocklin 3-12-14 | not present | OP | not present | 1 | TA | AC: Low or No-Flow Conditions |  | AMFQ |  | TSCO | 2014-03-19 | 2014-03-19 |  | 2014-04-01 | Medium 3-B | GESS | 2014-12-01 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SI | unknown | REVW | NOPT OSNO OSTS | 0
7002454 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 1 | TA | AC: SP Too Close to MOP/HiHi |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-12-31 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-12-31 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002454 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 2 | TA | EC: Within SCADA Accuracy |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-12-31 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-12-31 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002454 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 3 | CA | CA: Maintenance Required | Maintenance to establish 0-100% calibration | OXG3 | GESS | TSCO | 2014-03-21 | 2014-12-31 |  | 2014-04-21 | Medium 3-B | GESS | 2014-12-31 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7002455 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 1 | TA | AC: SP Too Close to MOP/HiHi |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-04-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002455 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 2 | TA | EC: SP Too Close to MOP |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-04-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002455 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 3 | TA | AC: Within SCADA Accuracy |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-04-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002455 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 4 | CA | CA: Maintenance Required | Maintenance to establish 0-100% calibration | OXG3 |  | TSCO | 2014-03-24 | 2014-04-21 |  | 2014-04-21 | Medium 3-B | GESS | 2014-04-21 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7002457 | OP Near Hit Redding Tap L-402 | not present | Near Hit | not present | 1 | TA | EC: Design Issue - Other |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-30 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE |  | true | REVW | ATCO OSNO | 0
7002457 | OP Near Hit Redding Tap L-402 | not present | Near Hit | not present | 2 | TA | AC: Low flow or no flow conditions |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-30 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE |  | true | REVW | ATCO OSNO | 0
7002457 | OP Near Hit Redding Tap L-402 | not present | Near Hit | not present | 3 | TA | AC: Typical Operations |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-30 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | TRANSPIPE |  | true | REVW | ATCO OSNO | 0
7002458 | OP Near Hit Ryer Island - Los Medanos St | not present | Near Hit | not present | 1 | TA | EC: Design Issue - Other |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC |  | unknown | REVW | ATCO OSNO | 0
7002458 | OP Near Hit Ryer Island - Los Medanos St | not present | Near Hit | not present | 2 | TA | AC: Typical Operations |  | KDSD | GESS | TSCO | 2014-03-21 | 2014-06-21 | KDSD | 2014-03-21 | Medium 3-B | GESS | 2014-06-30 | GAWTOPER | WOOP | DKM4 | PRGS | COMPPROC |  | unknown | REVW | ATCO OSNO | 0
7002461 | OP Near Hit Felton Reg Station D/S Press | not present | Near Hit | not present | 1 | TA | AC: Within SCADA Accuracy |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-04-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002461 | OP Near Hit Felton Reg Station D/S Press | not present | Near Hit | not present | 2 | CA | CA: Reg Set Point Lowered to 46 psig |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-01 | Medium 3-B | GESS | 2014-04-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002464 | OP Near Hit Almaden & Redmond | not present | Near Hit | not present | 1 | TA | AC: Within SCADA Accuracy |  |  |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002464 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 2 | TA | Contacted T&R Sup and Planner | Contacted the local T&R Supervisor on 03/12/2014 to determine Almaden & Redmond reg and monitor set point. The reg was set at 51 psig and monitor was set at 56 psig.. After contacting the T&R Supervisor, an e-mail was sent out to the local planner for further discussion on CA's. | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-03 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out
7002464 | OP Near Hit Almaden & Redmond San Jose | not present | Near Hit | not present | 3 | CA | CA: Maintenance Required | Maintenance to establish 0-100% calibration | OXG3 |  | TSCO | 2014-03-24 | 2014-03-24 |  | 2014-04-21 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SJ | true | ACCP | OSNO OSTS | 0 |  | 4/21/14 - according the Cathlene Bennett - complete/closed out E-mails has been sent out several time regarding this Corrective Action. It has been escalated to Manger. Frank will be contacting Kelly Ball regarding this overdue CA.
7002465 | OP Near Hit Clarksburg Prim | not present | Near Hit | not present | 1 | TA | AC: Operating Close to MOP/HIHI |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002465 | OP Near Hit Clarksburg Prim | not present | Near Hit | not present | 2 | TA | Contacted T&R Sup |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-01 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | SA | true | ACCP | OSNO OSTS | 0
7002466 | OP Near Hit Brentwood Terminal | not present | Near Hit | not present | 1 | TA | AC: Hand Throttle Valve |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 | AMFQ | 2014-03-18 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | LM | true | ACCP | OSNO OSTS | 0
7002466 | OP Near Hit Brentwood Terminal | not present | Near Hit | not present | 2 | CA | CA: Checked Valve Positions & Close V-42 |  | AMFQ |  | TSCO | 2014-03-18 | 2014-03-18 |  | 2014-04-01 | Medium 3-B | GESS | 2014-05-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | LM | true | ACCP | OSNO OSTS | 0
7002795 | Alarm inadvertently generated in GDCC | not present | Other | not present | 2 | TA | Complete Separation of Dev and Prod | Complete separation of Development and Production to the extend feasible with existing system | RPM4 |  | TSCO | 2014-04-11 | 2014-08-01 | RPM4 | 2014-07-29 | Low 4-C | GESSO | 2014-08-01 | GAWTOPER | WOSC | RPM4 | PRTR | OTHER | MI | unknown | ACCP | OSNO OSTS
7002795 | Alarm inadvertently generated in GDCC | not present | Other | N/A | 1 | TA | Training Issues with SCADA | Ensure training modules do not affect SCADA information or screens | RPM4 | GESSO | TSCO | 2014-04-11 | 2014-06-29 | RPM4 | 2014-06-01 | Low 4-C | GESSO | 2014-08-01 | GAWTOPER | WOSC | RPM4 | PRTR | OTHER | MI | unknown | ACCP | OSNO OSTS | 1 | LNR3 |  | JO15 | 2014-08-12 | GASCAPCPIC | LNR3 | 2014-08-20
7002930 | SCADA Emerg Resp Valve Info Issues | not present | Other | N/A | 1 | CA | Upgrade SCADA Screens |  | MWH7 |  | TSCO | 2014-04-08 | 2014-08-01 | RPM4 | 2014-07-29 | Medium 3-B | GESS | 2014-08-01 | GAWTOPER | WOSC | RPM4 | PRER | TRANSPIPE |  | unknown | ACCP | OSNO OSTS | 0 |  | Work reassigned to Carlos Penner. Task 1 work performed by Mike Henscey considered completed.
7002936 | OP Near Hit Congo & Flood SF | Congo & Flood | Near Hit | 2014-04-08 23:52 | 2 | CA | CA: Check SF Load Center Set Points | San Francisco Gas OM&C Supervisor has requested the Milpitas District that maintain SF Load Center to come up and check the station. | JGJ4 |  | TSCO | 2014-04-23 | 2014-08-25 |  |  | Medium 3-B | GESS | 2014-08-25 | GAWTOPER | WOOP | DKM4 |  | DISTSERVS | [6 empty] | 6/19/14 - Email reminder sent out to responsible party - awaiting response. 6/26/2014 - Upon review, all CA's have been completed and is ready for trending
7003089 | OP Near Hit French Camp, Stockton | not present | Near Hit | not present | 3 | CA | CA: Immediate Response | Immediate actions were done during the HIHI breach which included: GTCC contacted the Field Supervisor regarding the HI alarm and asked to have Vernalis Regulations to be checked, Supervisor contacted the Tech, and Tech checked the regulations at Vernalis | KDSD | GESS | TSCO | 2014-04-17 | 2014-04-17 | KDSD | 2014-04-17 | Medium 3-B | GESS | 2014-12-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | ST | true | ACCP | OSNO OSTS
7003181 | OP Near Hit Skyline & Rischell, EB | not present | Near Hit | not present | 2 | CA | CA: Immediate Actions Followed | Immediate actions were done during the HIHI breach. At this point, no further actions are required. |  |  | TSCO | 2014-05-06 | 2014-12-01 | AMFQ | 2014-12-01 | Medium 3-B | GESS | 2014-12-01 | GAWTEQU | WEOT | DKM4 | PRIN | MEASCRTL | PN | true | ACCP | OSNO OSTS
7003420 | Inefficient new Dist SCADA system | not present | Other | not present | 1 | TA | Response to D SCADA Cost Effectiveness | Response on CAP Item 7003420 - Questions about D SCADA Cost Effectiveness The Gas Distribution Control Center (GDCC) Project is intended to provide significant benefits to PG&E and its customers by improving Company operations, reliability, and emergency response. The deployment of Supervisory Control and Data Acquisition (SCADA) and control center processes provides improved visibility into the status and state of the system and allows quicker and more informed decision making when events occur on the system. PG&E's gas distribution SCADA system is focused on monitoring key pipeline pressures (e.g. low pressure points) and monitoring and control applications at gas pressure regulator stations.... | AMFQ |  | TSCO | 2014-08-25 | 2014-09-06 | AMFQ | 2014-08-25 | Low 4-C | GESSO | 2014-09-06 | GAWTOPER | WOGC | FWM1 | PRGS | MEASCRTL | NB |  | ACCP |  |  |  | On Friday Aug 22nd, Frank sent the response for this CAP to Me (Alvin Flores). A CAP task was created and the response has been uploaded into CAP.
7003538 | OP Near Hit Redding Tap L-402 | not present | Near Hit | not present | 3 | CA | CA: Immediate Actions Followed | Immediate actions were taken during the incident that included the following: GTCC conacted the on call supervisor, a tech was sent out to the location, and the tech reducded the pressure set point to 585 psig | AMFQ | GESS | TSCO | 5/27/214 | 2014-05-27 | AMFQ |  | Medium 3-B | GESS | 2015-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | NV | [5 empty] | 5/27/2014 - the CA was closed out
7003638 | BR Bldg Y IGCC SCADA Workstation Failure | not present | Other | N/A | 1 | CA | Manually Update all 4 workstations (TIG | 1) Manually Update all 4 workstations (TIGCC1,TIGCC2,DIGCC1,DIGCC2) | JUHM |  | TSCO | 2014-05-19 | 2014-05-19 | JUHM | 5/19/014 | Low 4-C | GESSO | 2014-07-01 | GAWTOPER | WOSC | RPM4 |  | OTHER |  | unknown | ACCP | OSNO OSTS | 0
7003730 | OP Near Hit Sacramento GLC | not present | Near Hit | not present | 3 | CA | CA: Immediate Response | Immediate Response: Local Supervisor sent out a Tech to the location first thing in the morning and the Tech completed a Sulfagon Filters installation at Sac GLC. | KDSD | GESS | TSCO | 5/14/014 | 2014-05-14 | KDSD |  | Medium 3-B | GESS | 2014-05-19 | GAWTOPER | WOOP | DKM4 | PRIN | MEASCRTL | SA | [5 empty] | 5/14/2014 - it was closed out
7004203 | ERX Testing | not present | Other | not present | - | - | ERX Testing | ERX testing alarms coming out of SCADA lad at Bishop Ranch are going into live SCADA system. There needs to be a sand box for thes alarms coming out of the test lab during the testing phase of new equipment. Please assign to Bob Matthews | [5 empty] | RPM4 | 2014-08-01 | Low 4-B | GESSO | 2014-07-19 |  |  | RPM4 | PRIT | OTHER
7004755 | OP Near Hit Irvington Station | not present | Near Hit | not present | 2 | TA | AC: Valve Operation |  | KDSD | GESS | TSCO | 2014-07-29 | 2014-07-29 | LNR3 | 2014-07-29 | Medium 4-A | GESS | 2015-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | MI | true | SUBM | OSNO OSTS
7004755 | OP Near Hit Irvington Station | not present | Near Hit | not present | 1 | TA | EC: HF/WPE-Manual Operations |  | KDSD | GESS | TSCO | 2014-07-29 | 2014-07-29 | LNR3 | 2014-07-29 | Medium 4-A | GESS | 2015-12-31 | GAWTOPER | WOOP | DKM4 | PRIN | TRANSPIPE | MI | true | SUBM | OSNO OSTS
| Today | 2024-08-28 |  | not present
7005868 | OP Near Hit at Enrico Station, L-105 | not present | Near Hit | not present | 2 | CA | CA: Remove TROP on L105N | L105N has an MOP/MAOP of 150/198 psig respectively. It is currently being held down by a crop to have an MOP of 121psig. By the comments on the latest version of 086868 it describes the TROP as being caused by unscheduled crane movement along L105A. "A TROP was issued due to unscheduled crane movement along L105A on Hollis St between Powell St and 59th. Engineering requested a 10% reduction until further review can be made." This does not seem to actually affect pipe specifications (just increased wheel loading forces on the surface). Removing this TROP will return the MOP back to 150 psig. | TWS4 |  | TSCO | 2014-09-22 | 2015-02-01 | KDSD | 2014-10-17 | Medium 4-A | GESS | 2015-09-16 | GAWTOPER | WOGC | DKM4 | PRIN | MEASCRTL | EB | unknown | ACCP | OSNO OSTS | 0
Some CAP notes:
2014-07-16

## Checklist (hidden)
Count | Engineer | Event Location/Title | Notification to Dan | OP/Near Hit | 48-hour report complete | Update Master | CAP Number | Quick Hit | Weekly CAP Meeting | Apparent/Root Cause | OP Elimination meeting | CA enter to CAP | Final Report/Root Cause/CA communication | 5 MM | CA Complete
1 | K1D7 | Corning | 2014-01-07 | OP | 2014-01-07 | 2014-01-07 | 7001252 | [5 empty] | k1d7 | Liquids
2 | K1D7 AMFQ | Topock | 2014-01-10 | OP | 2014-01-14 | 2014-01-14 | 7001315 7003563 | [5 empty] | CAP |  | CAP 7003563
3 | K1D7 | Corning | 2014-01-13 | OP | 2014-01-13 | 2014-01-13 | 7001312 | [5 empty] | k1d7 | Liquids
4 | P5B7 | 9th and I | 2014-01-15 | OP | 2014-01-16 | 2014-01-16 | 7001340 | [5 empty] | kdsd
5 | MND4 | Center St | 2014-02-02 | OP | 2014-02-04 | 2014-02-04 | 7001532 | [5 empty] | kdsd
6 | KDSD | Lomita Park | 2014-02-24 | OP | 2014-02-24 | 2014-02-24 | 7001977 | [5 empty] | kdsd |  | 7001977
7 | AMFQ | Avalon & Vienna | 2014-05-08 | OP | 2014-05-20 | 2014-05-16 | 7003511 | [7 empty] | CAP 7004145 CAP 7004164
8 | AMFQ | L172 North at Hershey Station | 2014-06-23 | OP |  | 2014-06-25 | 7004358
9 | KDSD | Herrmann Station | 2014-06-30 | OP | 2014-07-01 | 2014-06-30 | 7004583 | [5 empty] | kdsd |  | 7004583
10 | AMFQ | American Rice Dryer | 2014-06-16 | OP | 2014-07-03 | 2014-07-03 | 7004510
11 | AMFQ | L134A Herdon Junction | 2014-07-18 | NH | 2014-07-21 | 2014-07-21 | 7004896
12 | AMFQ | Monolith Cement | 2014-07-18 | NH | 2014-07-21 | 2014-07-21 | 7004934
13 | KDSD | Los Medanos | 2014-07-21 | OP | 2014-07-22 | 2014-07-22 | 7004884 | [7 empty] | 7004884
| KDSD | Alameda SHP | 2014-07-30 | OP | 2014-07-30 | 2014-07-30 | 7005059
14 | KDSD | Dolan Rd | 2014-08-04 | OP | 2014-08-05 | 2014-08-04 | 7005140 | [7 empty] | 7005431
15 | AMFQ | Acacia Station | 2014-08-16 | OP | 2014-08-16 | 2014-08-16 | 7005431 | 2014-08-27 |  | 8/26/14 CAP
16 | AMFQ | Enrico | 2014-09-13 | NH | 2014-09-25 | 2014-09-23 | 7005868 |  | 2014-09-18 | 09/22/14 CAP
17 | AMFQ | Cemex | 2014-09-11 | NH |  | 2014-09-13 | 70006071
18 | AMFQ | Swingle Station | 2014-08-12 | NH | 2014-08-11 | 2014-08-14 | 7005258 | [6 empty] | Mention Hand Throttle Valve in the next theme 5MM. This event will be noted and CA will be closed out
19
20
21 | [15 empty] | Formal Communication Checklist
22 | [15 empty] | 1 | 48-hour report
23 | [15 empty] | 2 | Final 48-hour Report (with Root Cause and CAs)
[16 empty] | 3 | EOM meetings with Dan to deliver closed out Notifications, and the CAs related to the notifications
|  | no action needed | [13 empty] | Steps to follow with the checklist in mind
incomplete
|  | pending | [14 empty] | Engineer writes the report and notifies Dan for next 7 am meeting
|  | complete | [14 empty] | 48 hour report is completed
Update the 2011-2014 master excursion spreadsheet
Establish the report has a CAP number, add this to the report
At the Thursday meetings with CAP team to discuss
If not resolved establish root cause
and corrective actions for the event
These two should be sepecified into the CAP tool and 48-hour report
This should finalize the 48-hour report, and mass communication can be delivered
The OP event will be discussed at the next OP Elimination meeting
Track CA to completion
Note on J1: Flores, Alvin: Clarification: CAP Meeting means Thursday Meeting?

## Pivots (hidden)
# of OP events by Division
Year | (Multiple Items)
Gas Log Event | (All)
Count of Percent over MOP | Month
Division | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 | Grand Total
Central Coast | [7 empty] | 1 |  |  | 1 |  |  |  | Central Coast
Diablo | [9 empty] | 1 | 1 |  |  |  | Diablo
East Bay |  |  | 1 | [7 empty] | 1 |  |  |  | East Bay
Fresno | 1 |  |  |  |  | 1 |  |  |  | 2 | 4 |  |  |  | Fresno
Kern | 1 |  |  | 1 | [6 empty] | 2 |  |  |  | Kern
Mission |  | 1 | [8 empty] | 1 |  |  |  | Mission
North Bay | [5 empty] | 2 |  |  | 1 |  | 3 |  |  |  | North Bay
North Coast |  |  |  | 1 | [6 empty] | 1 |  |  |  | North Coast
North Valley | 2 | [5 empty] | 2 |  |  |  | 4 |  |  |  | North Valley
Peninsula |  | 1 | [8 empty] | 1 |  |  |  | Peninsula
Sacramento | 3 |  | 1 | 1 |  | 1 | 1 |  |  |  | 7 |  |  |  | Sacramento
San Francisco |  |  |  |  | 2 | [5 empty] | 2 |  |  |  | San Francisco
San Jose | [7 empty] | 1 |  |  | 1 |  |  |  | San Jose
Sierra |  |  |  |  | 1 | 1 | 1 |  |  |  | 3 |  |  |  | Sierra
Stockton | 1 | 2 | [8 empty] | 3 |  |  |  | Stockton
Yosemite |  | 1 |  | 1 | [6 empty] | 2 |  |  |  | Yosemite
(blank) | [14 empty] | Year
Hollister | 1 | [9 empty] | 1 |  |  |  | Gas Log Event
Year | (Multiple Items) | [13 empty] | 0
Gas Log Event | (Multiple Items) | [13 empty] | Count of Percent over MOP
Specific OP Metric Group
Count of Percent over MOP | Group | [13 empty] | Design
Specific OP Metric Group | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total | [10 empty] | Equipment Failure
Design |  | 1 |  | 1 | [10 empty] | Operator Error
Equipment Failure | 5 | 2 | 3 | 10
Operator Error | 8 | 7 | 7 | 22
SP too close to MOP | 2 | 1 |  | 3
Grand Total | 15 | 11 | 10 | 36
Gas Log Event
Year | (Multiple Items)
Gas Log Event | (Multiple Items)
Count of Percent over MOP | Trans/Dist
Specific OP Metric Group | HP Distribution | LP Distribution | Transmission | Grand Total
Design |  |  | 1 | 1
Equipment Failure | 6 |  | 4 | 10
Operator Error | 3 | 3 | 16 | 22
SP too close to MOP | 1 | 1 | 1 | 3
Grand Total | 10 | 4 | 22 | 36
# of OP Events by System
Year | (Multiple Items)
Count of Percent over MOP | Study Group
Trans/Dist |  | Trans P > MOP+10 | HP Distribution > MOP+10% | LP > 16 | Grand Total
HP Distribution | 5 |  | 6 |  | 11
LP Distribution | 3 |  |  | 1 | 4
Transmission | 16 | 6 |  |  | 22
Grand Total | 24 | 6 | 6 | 1 | 37
# of OP Events by System
Year | (Multiple Items)
Count of Percent over MOP | Study Group
Trans/Dist |  | Trans P > MOP+10 | HP Distribution > MOP+10% | LP > 16 | Grand Total
HP Distribution | 5 |  | 6 |  | 11
LP Distribution | 3 |  |  | 1 | 4
Transmission | 16 | 6 |  |  | 22
Grand Total | 24 | 6 | 6 | 1 | 37
# of OP Events by System | [12 empty] | # of OP Events by System by Quarter | [30 empty] | # of OP Events by System by Month
Year | (Multiple Items)
Count of Percent over MOP | Study Group | [11 empty] | Count of Percent over MOP | Year | Quarter | [28 empty] | Count of Percent over MOP | Year | Month
Trans/Dist |  | Trans P > MOP+10 | HP Distribution > MOP+10% | LP > 16 | Grand Total | [8 empty] | 2011 |  |  |  | 2011 Total | 2012 |  |  |  | 2012 Total | 2013 |  |  |  | 2013 Total | 2014 |  | 2014 Total | [13 empty] | 2011 | [11 empty] | 2011 Total | 2012 | [11 empty] | 2012 Total | 2013 | [9 empty] | 2013 Total | 2014 |  |  |  | 2014 Total
HP Distribution | 5 |  | 6 |  | 11 | [7 empty] | Trans/Dist | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | [13 empty] | Trans/Dist | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 |  | 1 | 2 | 5 | 6
LP Distribution | 3 |  |  | 1 | 4 | [7 empty] | HP Distribution | 5 | 12 | 11 | 10 | 38 | 4 |  | 1 | 2 | 7 | 5 | 3 | 1 |  | 9 | 2 |  | 2 | [12 empty] | HP Distribution |  | 3 | 2 | 1 | 7 | 4 | 3 | 2 | 6 | 1 | 5 | 4 | 38 | 3 | 1 | [6 empty] | 1 |  |  | 2 | 7 | 4 | 1 |  | 2 | 1 |  | 1 |  |  |  | 9 | 2 |  |  | 1 | 3
Transmission | 16 | 6 |  |  | 22 | [7 empty] | LP Distribution | 173 | 148 | 164 | 139 | 624 | 179 | 46 |  | 3 | 228 |  | 1 | 1 | 1 | 3 | 1 |  | 1 | [12 empty] | LP Distribution | 53 | 45 | 75 | 37 | 56 | 55 | 67 | 43 | 54 | 70 | 28 | 41 | 624 | 53 | 60 | 66 | 37 | 9 | [6 empty] | 3 | 228 |  |  |  |  | 1 |  |  | 1 |  | 1 | 3 | 1 |  |  |  | 1
Grand Total | 24 | 6 | 6 | 1 | 37 | [7 empty] | Transmission | 41 | 35 | 22 | 14 | 112 | 45 | 16 | 5 | 7 | 73 | 8 | 4 | 4 | 3 | 19 | 3 | 2 | 5 | [12 empty] | Transmission | 13 | 17 | 11 | 13 | 10 | 12 | 13 | 7 | 2 | 4 | 2 | 8 | 112 | 12 | 7 | 26 | 10 | 4 | 2 | 2 | 2 | 1 | 5 | 1 | 1 | 73 | 4 | 2 | 2 | 2 |  | 2 | 3 | 1 | 1 | 2 | 19 | 1 | 2 |  | 2 | 5
[13 empty] | LP Distribution | [16 empty] | 1 | 1 | [12 empty] | LP Distribution | [39 empty] | 1 |  | 1
[13 empty] | Grand Total | 219 | 195 | 197 | 163 | 774 | 228 | 62 | 6 | 12 | 308 | 13 | 8 | 6 | 4 | 31 | 6 | 3 | 9 | [12 empty] | Grand Total | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 | 774 | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 | 308 | 8 | 3 | 2 | 4 | 2 | 2 | 4 | 2 | 1 | 3 | 31 | 4 | 2 | 1 | 3 | 10
Small/Large Excursions OP Events | [12 empty] | Large Excursions OP Events by Quarter | [14 empty] | Small Excursions OP Events by Quarter | [15 empty] | Large Excursions OP Events by Quarter
Year | 2014 | [42 empty] | Large Excursion/Small Excursion | 2011 1: Small Excursion
Count of Percent over MOP |  | Month | [10 empty] | Count of # over MOP |  | Year | Quarter | [11 empty] | Count of # over MOP |  | Year | Quarter | [12 empty] | Count of # over MOP | 2011 2: Month
Large Excursion/Small Excursion | Trans/Dist | 1 | 2 | Grand Total | [10 empty] | 2011 |  |  |  | 2012 |  |  |  | 2013 |  |  |  | 2014 |  |  | 2011 |  |  |  | 2011 Total | 2012 |  |  |  | 2012 Total | 2013 |  |  |  | Year | Trans/Dist | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total
Large Excursion | HP Distribution | 2 |  | 2 | [8 empty] | Large Excursion/Small Excursion | Trans/Dist | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Large Excursion/Small Excursion | Trans/Dist | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 | 2011 | HP Distribution |  | 2 | 2 | 1 | 3 | 3 | 3 | 2 | 6 |  | 5 | 3 | 30
| Transmission | 1 |  | 1 | [8 empty] | Large Excursion | HP Distribution | 1 | 5 |  | 2 | 2 |  | 1 | 1 | 2 | 1 | 1 |  | 2 | Small Excursion | HP Distribution | 4 | 7 | 11 | 8 | 30 | 2 |  |  | 1 | 3 | 3 | 2 |  |  |  | LP Distribution | 53 | 45 | 74 | 37 | 55 | 55 | 67 | 43 | 54 | 69 | 28 | 41 | 621
Small Excursion | LP Distribution | 1 |  | 1 | [9 empty] | LP Distribution | [14 empty] | LP Distribution | 172 | 147 | 164 | 138 | 621 | 179 | 46 |  | 3 | 228 |  | 1 |  | 1 |  | Transmission | 7 | 13 | 9 | 11 | 9 | 9 | 11 | 6 | 2 | 2 | 1 | 7 | 87 | bar: Q1 to Q1
| Transmission |  | 2 | 2 | [9 empty] | Transmission | 12 | 6 | 3 | 4 | 1 | 2 |  | 1 | 3 |  | 1 | 1 | 1 |  | Transmission | 29 | 29 | 19 | 10 | 87 | 44 | 14 | 5 | 6 | 69 | 5 | 4 | 3 | 2 | 2011 Total |  | 60 | 60 | 85 | 49 | 67 | 67 | 81 | 51 | 62 | 71 | 34 | 51 | 738
Grand Total |  | 4 | 2 | 6 | [8 empty] | Small Excursion | HP Distribution | 4 | 7 | 11 | 8 | 2 |  |  | 1 | 3 | 2 |  |  |  |  | LP Distribution | [14 empty] | 2012 | HP Distribution | 1 | 1 | [9 empty] | 1 | 3
[14 empty] | LP Distribution | 172 | 147 | 164 | 138 | 179 | 46 |  | 3 |  | 1 |  | 1 | 1 | Grand Total |  | 205 | 183 | 194 | 156 | 738 | 225 | 60 | 5 | 10 | 300 | 8 | 7 | 3 | 3 |  | LP Distribution | 53 | 60 | 66 | 37 | 9 | [6 empty] | 3 | 228
[14 empty] | Transmission | 29 | 29 | 19 | 10 | 44 | 14 | 5 | 6 | 5 | 4 | 3 | 2 | 2 | [17 empty] | Transmission | 12 | 7 | 25 | 10 | 2 | 2 | 2 | 2 | 1 | 5 | 1 |  | 69
[14 empty] | LP Distribution | [29 empty] | 2012 Total |  | 66 | 68 | 91 | 47 | 11 | 2 | 2 | 2 | 1 | 5 | 1 | 4 | 300
[13 empty] | Grand Total |  | 219 | 195 | 197 | 163 | 228 | 62 | 6 | 12 | 13 | 8 | 6 | 4 | 6 | [16 empty] | 2013 | HP Distribution | 2 | 1 |  | 1 | 1 | [7 empty] | 5
OP Events by Apparent Cause | [44 empty] | LP Distribution |  |  |  |  | 1 | [5 empty] | 1 |  | 2
Year | 2014 | [43 empty] | Transmission | 3 | 1 | 1 | 2 |  | 2 |  | 2 | 1 | 1 | 1 |  | 14
[44 empty] | 2013 Total |  | 5 | 2 | 1 | 3 | 2 | 2 |  | 2 | 1 | 1 | 2 |  | 21
Count of Percent over MOP | Month | [11 empty] | Count of Percent over MOP | Year | Q1: Quarter | [16 empty] | 2014 | HP Distribution | [5 empty] | 1 | [6 empty] | 1
Specific OP Metric Group | 1 | 2 | Grand Total | [10 empty] | 2011 | Q4: 2011 Total; Q1: 2012; Q1: 2012 Total; Q2: 2013 | 2013 Total | 2014 |  |  | 2014 Total | Grand Total | [11 empty] | LP Distribution | 1 | [11 empty] | 1
Design | 1 |  | 1 | [9 empty] | Specific OP Metric Group | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | Q3 | Q4 |  | Q1 | Q2 | (blank) | [13 empty] | Transmission |  | 2 |  |  |  | 2 | [6 empty] | 4
Equipment Failure | 2 | 2 | 4 | [9 empty] | Design | 13 | 4 | 6 | 4 | 27 | 1 |  |  | 2 | 3 |  |  |  | 1 | 1 |  |  |  |  | 31 | [11 empty] | LP Distribution |  |  |  |  | 1 | [7 empty] | 1
Operator Error | 1 |  | 1 | [9 empty] | Equipment Failure | 12 | 14 | 7 | 2 | 35 | 13 | 2 | 3 | 8 | 26 | 3 | 4 | 2 |  | 9 | 2 |  |  | 2 | 72 | [10 empty] | 2014 Total |  | 1 | 2 |  |  | 1 | 3 | [6 empty] | 7
Grand Total | 4 | 2 | 6 | [9 empty] | Operator Error | 14 | 21 | 10 | 7 | 52 | 12 | 13 | 2 | 2 | 29 | 8 | 4 | 4 | 3 | 19 | 3 | 3 |  | 6 | 106 | [10 empty] | Grand Total |  | 132 | 132 | 177 | 99 | 81 | 74 | 83 | 55 | 64 | 77 | 37 | 55 | 1066
[13 empty] | SP too close to MOP |  | 1 |  | 5 | 6 | 26 | 6 | 1 |  | 33 | 2 |  |  |  | 2 | 1 |  | 1 | 2 | 43
[13 empty] | Unknown/ Not Reported | 180 | Q1: 155; Q2: 174; Q3: 145; Q4: 654; Q1: 176; Q2: 41; Q1: 217 | [5 empty] | 871
[13 empty] | Grand Total | 219 | 195 | 197 | 163 | 774 | 228 | 62 | 6 | 12 | 308 | 13 | 8 | 6 | 4 | 31 | 6 | 3 | 1 | 10 | 1123
OP Events by Apparent Cause by large/small excursion
Year | 2014
Count of Percent over MOP | Large Excursion/Small Excursion | [11 empty] | Count of Percent over MOP |  | Q1: Year; Q2: Quarter
Specific OP Metric Group | Large Excursion | Small Excursion | Grand Total | [11 empty] | Q1: 2014; Q2: 2014 Total; Q3: Grand Total
Design |  | 1 | 1 | [9 empty] | Large Excursion/Small Excursion | Specific OP Metric Group | Q1: (blank)
Equipment Failure | 2 | 2 | 4 | [9 empty] | Small Excursion | SP too close to MOP | bar: Q1 to Q3
Operator Error | 1 |  | 1 | [9 empty] | Grand Total | bar: Q1 to Q3
Grand Total | 3 | 3 | 6
# of OP Events by At Storage or Compr Station | [12 empty] | # of OP Events by At Storage or Compr Station
Count of Percent over MOP |  | Month | [10 empty] | Count of Percent over MOP | Year | Q1: quarter
Year | At Compr Stn or Storage | 1 | [11 empty] | 2011 | Q1: 2011 Total; Q2: 2012; Q3: 2012 Total; Q4: 2014; Q1: 2014 Total
2014 | yes | 1 | [10 empty] | At Compr Stn or Storage | Q1 | bar: Q2; Q4
2014 Total |  | 1 | [10 empty] | yes | 11 | Q1: 11; Q2: 1; Q3: 1; Q4: 1; Q1: 1
Grand Total |  | 1 | [10 empty] | Grand Total | 11 | Q1: 11; Q2: 1; Q3: 1; Q4: 1; Q1: 1
Small/Large Excursions OP Events
Count of Percent over MOP |  | Year | Month
|  | 2011 | [11 empty] | 2011 Total | Q1: 2012; Q1: 2012 Total | 2013 | [9 empty] | 2013 Total | 2014 |  | 2014 Total | (blank) | Grand Total
Large Excursion/Small Excursion | Trans/Dist | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 |  | 1 | 2
Large Excursion | HP Distribution | 2011 2: 1; 2011 5: 4; 2011 6: 1; 2011 10: 1; 2011 12: 1 | 8 | 2 | [7 empty] | 1 |  |  | 1 | 4 | 2 |  |  | 1 |  |  | 1 |  |  |  | 4 | 2 |  | 2 |  | 18
| LP Distribution | [12 empty] | 3 | [20 empty] | 1 |  |  | 1 |  |  |  |  | 4 | bar: 2011 3; 2011 5; 2011 10
| Transmission | 6 | 4 | 2 | 2 | 1 | 3 | 2 | 1 |  | 2 | 1 | 1 | 25 |  |  | 1 |  | 2 | [6 empty] | 1 | 4 | 1 | 1 | 1 |  |  |  | 1 |  |  | 1 | 5 | 1 |  | 1 |  | 35
Small Excursion | HP Distribution |  | 2 | 2 | 1 | 3 | 3 | 3 | 2 | 6 |  | 5 | 3 | 30 | 1 | 1 | [9 empty] | 1 | 3 | 2 | 1 |  | 1 | 1 | [5 empty] | 5 |  |  |  |  | 38
| LP Distribution | 53 | 45 | 74 | 37 | 55 | 55 | 67 | 43 | 54 | 69 | 28 | 41 | 621 | 53 | 60 | 66 | 37 | 9 | [6 empty] | 3 | 228 |  |  |  |  | 1 |  |  |  |  | 1 | 2 | 1 |  | 1 |  | 852
| Transmission | 7 | 13 | 9 | 11 | 9 | 9 | 11 | 6 | 2 | 2 | 1 | 7 | 87 | 12 | 7 | 25 | 10 | 2 | 2 | 2 | 2 | 1 | 5 | 1 |  | 69 | 3 | 1 | 1 | 2 |  | 2 | 2 | 1 | 1 | 1 | 14 |  | 2 | 2 |  | 172
(blank) | (blank)
Grand Total |  | 66 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 | 774 | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 | 308 | 8 | 3 | 2 | 4 | 2 | 2 | 4 | 2 | 1 | 3 | 31 | 4 | 2 | 6 |  | 1119

## Charts (hidden)
2015 | [15 empty] | fill key:
|  | UPDATE THE TABLES BELOW | [14 empty] | autofill
2015 OP Events for entire year | [16 empty] | manual
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design
Equipment Failure |  |  | 6
Operator Error |  |  | 8
SP too close to MOP |  |  | 3
Unknown/ Not Reported
Grand Total
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP - 17 Events
Operator Error - HP/WPE (Field, Manual Operations, Eng Review)
[7 empty] | 2015 Total OP - 17 Events |  |  |  |  | 2015 Large Excursion OP Events - 0 Events
2015 OP Events for quarter - First Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0
2014 Total OP Events - 17 Events
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP - 0 Events as of 3/31/14
2015 OP Events for quarter - Second Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0 |  |  | 2015 Total OP- 0 Events as of 7/1/14 | [6 empty] | 2014 Total OP Events - 17 Events
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP- 0 Events as of 7/1/14 | [8 empty] | 0
2015 OP Events for quarter - Third Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2013 Total OP- 0 Events as of 9/30/14
2015 OP Events for quarter - Fourth Quarter
Reason | Large Excursions | Small Excursions | Grand Total | Key
Design |  |  | 0
Equipment Failure |  |  | 0
Operator Error |  |  | 0
SP too close to MOP |  |  | 0
Unknown/ Not Reported |  |  | 0
Grand Total | 0 | 0 | 0
| 2015 Large Excursion OP Events - 0 Events | 2015 Small Excursion OP Events - 0 Events | 2015 Total OP- 0 Events as of 9/30/14
2011/2012 OP Events on LP Distribution
Trans/Dist | LP Distribution
Count of Percent over MOP | Year
Month | 2011 | 2012
Jan | 53 | 53
Feb | 45 | 60
Mar | 75 | 66
Apr | 37 | 37
May | 56 | 9
Jun | 55 | 0
Jul | 67 | 0
Aug | 43 | 0
Sep | 54 | 0
Oct | 70 | 0
Nov | 28 | 0
Dec | 41 | 3
Grand Total | 624 | 228
2012 OP Events - Gas Log
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 3 | 3
Equipment Failure | 7 | 6 | 7 | 20
Operator Error | 12 | 9 | 3 | 24
SP too close to MOP | 7 | 0 | 0 | 7
Unknown/ Not Reported | 9 | 2 | 2 | 13
Grand Total | 35 | 17 | 15 | 67
| 35 2012 OP Events | 17 2012 OP Events | 15 2012 OP Events | 67 2012 Total OP Events
[7 empty] | 35 2012 OP Events | [6 empty] | 17 2012 OP Events | 15 2012 OP Events
67 2012 Total OP Events
[7 empty] | 67 2012 Total OP Events | [5 empty] | MOP Excursions greater than 10%
15 2012 OP Events
2013 OP Events (not updated)
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 0 | 0
Equipment Failure | 5 | 1 | 1 | 7
Operator Error | 3 | 2 | 4 | 9
SP too close to MOP | 1 | 0 | 0 | 1
Unknown/ Not Reported | 0 | 0 | 0 | 0
Grand Total | 9 | 3 | 5 | 17
| 9 2013 OP Events | 3 2013 OP Events | 5 2013 OP Events | 17 2013 Total OP Events
[7 empty] | 9 2013 OP Events | [6 empty] | 3 2013 OP Events | 5 2013 OP Events
17 2013 Total OP Events
2012 OP Events for entire year
Reason | Large Excursions | Small Excursions | Grand Total
Design | 3 | 0 | 3
Equipment Failure | 3 | 23 | 26
Operator Error | 2 | 27 | 29
SP too close to MOP | 0 | 32 | 32
Unknown/ Not Reported | 0 | 218 | 218
Grand Total | 8 | 300 | 308
| 2012 Large Excursion OP Events - 8 Events | 2012 Small Excursion OP Events - 300 Events | 2012 Total OP - 308 Events
[7 empty] | 2012 Total OP - 308 Events | [5 empty] | 2012 Large Excursion OP Events - 8 Events
2013 OP Events for entire year
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 1 | 1
Equipment Failure | 4 | 11 | 15
Operator Error | 6 | 8 | 14
SP too close to MOP | 0 | 1 | 1
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 10 | 21 | 31
| 2013 Large Excursion OP Events - 10 Events | 2013 Small Excursion OP Events - 21 Events | 2013 Total OP - 31 Events
[7 empty] | 2013 Total OP - 31 Events | [5 empty] | 2013 Large Excursion OP Events - 10 Events
2013 OP Events for quarter - First Quarter
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 0 | 0
Equipment Failure | 0 | 5 | 5
Operator Error | 5 | 2 | 7
SP too close to MOP | 0 | 1 | 1
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 5 | 8 | 13
| 2013 Large Excursion OP Events - 5 Events | 2013 Small Excursion OP Events - 8 Events | 2013 Total OP- 13 Events as of 3/31/13
2013 OP Events for quarter - Second Quarter
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 0 | 0
Equipment Failure | 1 | 4 | 5
Operator Error | 0 | 3 | 3
SP too close to MOP | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 1 | 7 | 8
| 2013 Large Excursion OP Events - 1 Events | 2013 Small Excursion OP Events - 7 Events | 2013 Total OP- 8 Events as of 7/2/13
2013 OP Events for quarter - Third Quarter
Reason | Large Excursions | Small Excursions | Grand Total |  |  |  | 2013 Total OP- 13 Events as of 3/31/13 | [5 empty] | 2013 Large Excursion OP Events - 5 Events
Design | 0 | 1 | 1
Equipment Failure | 1 | 1 | 2
Operator Error | 1 | 1 | 2
SP too close to MOP | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 2 | 3 | 5
| 2013 Large Excursion OP Events - 2 Events | 2013 Small Excursion OP Events - 3 Events | 2013 Total OP- 5 Events as of 9/30/13
2013 OP Events for quarter - Fourth Quarter
Reason | Large Excursions | Small Excursions | Grand Total
Design | 0 | 0 | 0
Equipment Failure | 1 | 1 | 2
Operator Error | 0 | 2 | 2
SP too close to MOP | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0
Grand Total | 1 | 3 | 4
| 2013 Large Excursion OP Events - 1 Events | 2013 Small Excursion OP Events - 3 Events | 2013 Total OP- 4 Events as of 9/30/13
2012 OP Events - LP Distribution
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 0 | 0
Equipment Failure | 0 | 1 | 4 | 5
Operator Error | 0 | 1 | 5 | 6
SP too close to MOP | 4 | 0 | 0 | 4
Unknown/ Not Reported | 142 | 61 | 10 | 213
Grand Total | 146 | 63 | 19 | 228
| 146 2012 LP OP Events | 63 2012 LP OP Events | 19 2012 LP OP Events | 228 2012 Total LP OP Events
[7 empty] | 146 2012 LP OP Events | [6 empty] | 63 2012 LP OP Events | 19 2012 LP OP Events
228 2012 Total LP OP Events
Design |  |  | 2
Equipment Failure | 1 | 2 | 2
2012 OP Events - HP Distribution
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 2 | 2
Equipment Failure | 1 | 2 | 2 | 5
Operator Error | 0 | 0 | 0 | 0
SP too close to MOP | 0 | 0 | 0 | 0
Unknown/ Not Reported | 0 | 0 | 0 | 0
Grand Total | 1 | 2 | 4 | 7
| 1 2012 HP OP Events | 2 2012 HP OP Events | 4 2012 HP OP Events | 7 2012 Total HP OP Events
[7 empty] | 1 2012 HP OP Events | [6 empty] | 2 2012 HP OP Events | 4 2012 HP OP Events
7 2012 Total HP OP Events
Design |  |  | 1
Equipment Failure | 12 | 3 | 1
Operator Error | 15 | 8
Setpt too close to MOP | 28
Unknown/Not Reported | 5
2012 OP Events - Transmission
Reason | MOP Excursions less than 2% | MOP Excursions from 2% to less than 10% | MOP Excursions greater than 10% | Grand Total
Design | 0 | 0 | 1 | 1
Equipment Failure | 12 | 3 | 1 | 16
Operator Error | 15 | 8 | 0 | 23
SP too close to MOP | 28 | 0 | 0 | 28
Unknown/ Not Reported | 5 | 0 | 0 | 5
Grand Total | 60 | 11 | 2 | 73
| 60 2012 Transmission OP Events | 11 2012 Transmission OP Events | 2 2012 Transmission OP Events | 73 2012 Total Transmission OP Events
[7 empty] | 60 2012 Transmission OP Events | [6 empty] | 11 2012 Transmission OP Events | 2 2012 Transmission OP Events
73 2012 Total Transmission OP Events
SCADA vs Non-SCADA | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01
Non-SCADA | 2012-01-01: 2; 2012-02-01: 1; 2012-05-01: 1; 2012-09-01: 1; 2012-10-01: 1; 2012-11-01: 1; 2012-12-01: 3 | 10
SCADA | 66 | 67 | 92 | 47 | 12 | 2 | 2 | 2 | 1 | 4 |  | 3 | 298
Grand Total | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 | 308
Equipment Failure | 2012-03-01: 4
Operator Error | 2012-03-01: 4
Unknown/ Not Reported | 2012-01-01: 376; 2012-02-01: 197; 2012-03-01: 43
2011 OP Events - LP Distribution
Reason | 2012-01-01: MOP Excursions less than 2%; 2012-02-01: MOP Excursions from 2% to less than 10%; 2012-03-01: MOP Excursions greater than 10%; 2012-04-01: Grand Total
Design | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 0; 2012-04-01: 0
Equipment Failure | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 4; 2012-04-01: 4
Operator Error | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 4; 2012-04-01: 4
SP too close to MOP | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 0; 2012-04-01: 0
Unknown/ Not Reported | 2012-01-01: 376; 2012-02-01: 197; 2012-03-01: 43; 2012-04-01: 616
Grand Total | 2012-01-01: 376; 2012-02-01: 197; 2012-03-01: 51; 2012-04-01: 624
| 376 2011 LP OP Events | 197 2011 LP OP Events | 51 2011 LP OP Events | 624 2011 Total LP OP Events
| 2012-07-01: 376 2011 LP OP Events |  | 197 2011 LP OP Events | 51 2011 LP OP Events
624 2011 Total LP OP Events
2011 OP Events - HP Distribution
Reason | 2012-01-01: MOP Excursions less than 2%; 2012-02-01: MOP Excursions from 2% to less than 10%; 2012-03-01: MOP Excursions greater than 10%; 2012-04-01: Grand Total
Design | 2012-01-01: 0; 2012-02-01: 0; 2012-03-01: 1; 2012-04-01: 1
Equipment Failure | 2012-01-01: 9; 2012-02-01: 3; 2012-03-01: 1; 2012-04-01: 13
Operator Error | 2012-01-01: 5; 2012-02-01: 3; 2012-03-01: 4; 2012-04-01: 12
SP too close to MOP | 2012-01-01: 5; 2012-02-01: 0; 2012-03-01: 0; 2012-04-01: 5
Unknown/ Not Reported | 2012-01-01: 4; 2012-02-01: 0; 2012-03-01: 3; 2012-04-01: 7
Grand Total | 2012-01-01: 23; 2012-02-01: 6; 2012-03-01: 9; 2012-04-01: 38
| 23 2011 HP OP Events | 6 2011 HP OP Events | 9 2011 HP OP Events | 38 2011 Total HP OP Events
| 2012-07-01: 23 2011 HP OP Events |  | 6 2011 HP OP Events | 9 2011 HP OP Events
38 2011 Total HP OP Events
2011 OP Events - Transmission
Reason | 2012-01-01: MOP Excursions less than 2%; 2012-02-01: MOP Excursions from 2% to less than 10%; 2012-03-01: MOP Excursions greater than 10%; 2012-04-01: Grand Total
Design | 2012-01-01: 21; 2012-02-01: 3; 2012-03-01: 2; 2012-04-01: 26
Equipment Failure | 2012-01-01: 11; 2012-02-01: 6; 2012-03-01: 1; 2012-04-01: 18
Operator Error | 2012-01-01: 23; 2012-02-01: 12; 2012-03-01: 1; 2012-04-01: 36
SP too close to MOP | 2012-01-01: 0; 2012-02-01: 1; 2012-03-01: 0; 2012-04-01: 1
Unknown/ Not Reported | 2012-01-01: 23; 2012-02-01: 8; 2012-03-01: 0; 2012-04-01: 31
Grand Total | 2012-01-01: 78; 2012-02-01: 30; 2012-03-01: 4; 2012-04-01: 112
| 78 2011 Transmission OP Events | 30 2011 Transmission OP Events | 4 2011 Transmission OP Events | 112 2011 Total Transmission OP Events
| 2012-07-01: 78 2011 Transmission OP Events |  | 30 2011 Transmission OP Events | 4 2011 Transmission OP Events
112 2011 Total Transmission OP Events

## MonthlyReportDetail (hidden)
Location | Date/Time | Max Pressure Reached | MOP | % over MOP | Cause Code | Description | Preliminary Root Causes (Root Cause Evaluation not completed)
Corning-Reg Distribution | North Valley | 2014-01-07 10:32 | 66.9871 | 60 |  | Called Patrick Harding about hihi and mop alarm for Corning Reg. he's currently investigating the situation, he will call back once he finds something out NOTED HIHI, MOP ALARM FOR CORNING REG. THANK YOU spoke with Patrick Harding again, he's sending someone out to check on it now appx eta is 1 hour | • Immediately switched runs and lowered the set pressure to 55 PSIG. • Initial diagnosis appears to be failed regulator and monitor - Performed 'B' type inspection • Equipment was saturated with large amounts of pipeline liquid - so the liquids were removed. • The filters and sense lines to the pilot were also coated and were dripping upon disassembly. • More information to come as the investigation continues.
Topock Compressor Station Topock1 Plant B K Suct Press | Kern | 2014-01-10 17:44 | 699 | 660 |  | The governor on K-8 was malfunctioning (wasn’t able to speed up… only could get 220 rpms out of it) we decided to put K-7 on line and take K-8 offline (K-9 was also on line) before I could take K-8 off, K-7 came on line and pulled the suction pressure down when it automatically loaded. (K-9 valves failed to operate during shutdown, noticed high pressure on L300B suction at the time (698 psig) we isolated the units and opened the stack valve on K-8 to blowdown the pressure to 635 psig) the station was set up with AB-1, AB-3 and TW-6 closed while on line at the time... After L300B equalized we opened AB-3, AB-1 and TW-6 to equalize the plant suction pressures. We then closed the PIV valve to TW-1 and slowly opened TW-1 shutdown OP to reset at this time and have called out techs and a mech … | • Review possible relief valve installation between the suction side and Transwestern Gas in accordance to standards • Check the current status of the MAOP uprate for Topock suction piping • Further discussion on the procedures for abnormal operating conditions at Topock Compressor Station with a split suction • Perform a CAP investigation to further comprehend the root cause of the OP event
Corning-Reg Distribution | North Valley | 2014-01-13 07:52 | 89 | 60 |  | mop breach at corning reg at 0752 hrs. called t&r supervisor Patrick Harding and he stated he will be sending a tech out to corning reg Kelly; mark bailey called gdcc to advise that he is currently at corning reg and that as far as he can tell, this pipeline liquids event is identical to the issue that occurred last week. He has been going out to this station every day to celar out the liquid that's been coming through. he said the standby side of reg is fully activated, and he will be speaking with his dept to get a plan together to get this issue resolved. he will call back when more information is available and keep gdcc apprised of all updates kelly | • Repeat B inspection • and repairs on affected equipment • Leak Survey on system
9th and I St. | Eureka | 2014-01-15 05:50 | 11.3 | 10.5 |  | Description: Cause determined to be regulator and monitor set points were to close together and frequent oscillations of regulated pressure combined with high-flow conditions due to cold morning temperatures caused near-hit event. The condition location is actually the SCADA 'end of line' location 11 blocks away that did not reflect the excursion | • Immediate action was lowering regulator set-point to 8 in-WC. • Daily monitoring of chart will take place during cold weather, high gas demand conditions. Notifications were made as required. • Increase MAOP to 14 in

## Tracking2012 (hidden)
2012 OP Events - Thru Dec 26, 2012 | [7 empty] | 2011 OP Events
| Gas Log # of OP Events | Gas Log event criteria | Approach 1 # of OP Events | Approach 1 event criteria | Approach 2 # of OP Events | Approach 2 event criteria |  |  | Gas Log # of OP Events | Gas Log event criteria | Approach 1 # of OP Events | Approach 1 event criteria | Approach 2 # of OP Events | Approach 2 event criteria
HP Distribution | 7 | MAOP | 7 | MAOP | 7 | MAOP |  | HP Distr | 19 | MAOP | 38 | MAOP | 38 | MAOP
LP Distribution | 26 | some 12" HiHi, some 10.5" Hi | 13 | 12 in WC | 228 | 10.5 in WC |  | LP Distr | 6 | some 12" HiHi, some 10.5" Hi | 35 | 12 in WC | 624 | 10.5 in WC
Transmission | 34 | MOP+3, some MOP | 19 | MOP+3 | 73 | MOP |  | Trans | 51 | MOP+3, some MOP | 87 | MOP+3 | 129 | MOP
Total | 67 |  | 39 |  | 308 |  |  | Total | 76 |  | 160 |  | 791
| 33 |  |  |  | 235 |  |  |  | adjusted 3 events after review of root cause to not OP |  |  |  | 662
Over Pressure Event Frequency Metric Tracking - 2012 |  |  |  |  | Green |  | Amber |  | Red
[5 empty] | <=42 |  | >42 and <=49 |  | >49
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
Expected Path: Goal OP events | 6 | 6 | 5 | 5 | 4 | 4 | 3 | 3 | 2 | 2 | 1 | 1 |  | 42 | 42
Actual OP events - Reported | 7 | 1 | 10 | 23 | 6 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 67 | 67
Actual OP Events - Approach 1 | 7 | 1 | 12 | 3 | 4 | 2 | 2 | 0 | 1 | 1 | 1 | 5 |  | 39 | 39
Actual OP Events - All OP events | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 308 | 308
Cumulative
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Expected Path: Goal OP events | 6 | 12 | 17 | 22 | 26 | 30 | 33 | 36 | 38 | 40 | 41 | 42
Actual OP events - Reported | 7 | 8 | 18 | 41 | 47 | 49 | 51 | 53 | 55 | 60 | 61 | 67
Actual OP Events - Approach 1 | 7 | 8 | 20 | 23 | 27 | 29 | 31 | 31 | 32 | 33 | 34 | 39
Actual OP Events - All OP events | 68 | 136 | 228 | 275 | 288 | 290 | 292 | 294 | 296 | 301 | 302 | 308
Breakdown of Actual OP Events - All OP Events
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
HP Distribution | Jan: 3; Feb: 1; Sep: 1; Dec: 2 |  | 7
LP Distribution | Jan: 53; Feb: 60; Mar: 66; Apr: 37; May: 9; Dec: 3 |  | 228
Transmission | 12 | 7 | 26 | 10 | 4 | 2 | 2 | 2 | 1 | 5 | 1 | 1 |  | 73
Total | 68 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 308 | 308
[8 empty] | forecast | forecast | forecast | forecast | forecast
2012 OP Events
Comments
OP Events by Month | Jul: OP Events by Quarter
Month | Distribution – MP/HP | Distribution - Low Pressure | Transmission | Grand Total | cumul total | 2013 proposed | Quarter | Distribution – MP/HP | Distribution - Low Pressure | Transmission | Grand Total | cumul total
1 | 3 | 2 | 2 | 7 | 7 | 4 | Qrtr 1 | 4 | 4 | 10 | 18 | 18
2 | 1 | 0 | 0 | 1 | 8 | 3 | Qrtr 2 | 0 | 19 | 12 | 31 | 49
3 | 0 | 2 | 8 | 10 | 18 | 3 | Qrtr 3 | 1 | 0 | 5 | 6 | 55
4 | 0 | 17 | 6 | 23 | 41 | 2 | Qrtr 4 | 2 | 3 | 7 | 12 | 67
5 | 0 | 2 | 4 | 6 | 47 | 1 | Grand Total | 7 | 26 | 34 | 67
6 | Jan: 0; Feb: 0; Mar: 2; Apr: 2; May: 49; Jun: 1
7 | Jan: 0; Feb: 0; Mar: 2; Apr: 2; May: 51; Jun: 1
8 | Jan: 0; Feb: 0; Mar: 2; Apr: 2; May: 53; Jun: 1
9 | Jan: 1; Feb: 0; Mar: 1; Apr: 2; May: 55; Jun: 1
10 | Jan: 0; Feb: 0; Mar: 5; Apr: 5; May: 60; Jun: 2
11 | Jan: 0; Feb: 0; Mar: 1; Apr: 1; May: 61; Jun: 2
12 | Jan: 2; Feb: 3; Mar: 1; Apr: 6; May: 67; Jun: 3
Grand Total | Jan: 7; Feb: 26; Mar: 34; Apr: 67; Jun: 24
Dasboard Variance Comments:
For December had 1 transmission event, 1 HP distribution event and 3 LP distribution event (more than expected). Preliminary root cause: LP distribution OP events were flooding related, both transmiission and HP distribution events were design related.
Team formed to address root causes of overpressure events. Backbone pressure reductions completed - 180 HP distribution pressure reductions completed in October and November. Distribution team lowered all LP reg pressures. Planning evaluating impact completed of proposed pressure reductions on local transmission systems and distribution systems. Planning completed evaluation of winter impacts of lowering LP regulator pressures. Initiated MOP alarm in Citect for all process gas pressure points to improve visibility of OP events. De-watering program for vaults likely to flood was instituted.
Will not return to green for the remainder of the year

## LP SubSystems (hidden)
SCADA Points LP Pressure
SCADA Point Name | SCADA Point Description | Division | LP System Name
OC1_PT0041 | Alameda Broadwy/Linc Dist Pres | East Bay | Alameda LP
OC1_PT0047 | Alameda Grand/Alameda Dist Pres | East Bay | Alameda LP
OC1_PT0048 | Alameda Grand/Pacific Dist Pres | East Bay | Alameda LP
OC2_PT0043 | Alameda Pacifc/6Th Dist Pres | East Bay | Alameda LP
OC1_PT0045 | Berkeley Fairvw/Adeln Dist Pres | East Bay | Oakland N LP
OC2_PT2109 | 34Th/Telegph Lp Pres | East Bay | Oakland N LP
OC1_PT0049 | Oakland Cooldg/Brookdl Dist Pres | East Bay | Oakland S LP
OC2_PT2105 | Foothl/Rosdl Lp Pres | East Bay | Oakland S LP
OC2_PT2108 | 19Th/E-26Th Lp Pres | East Bay | Oakland S LP
OC2_PT2111 | E-12Th/21St Lp Pres | East Bay | Oakland S LP
OC2_PT2106 | Bancrt/Havct Lp Pres | East Bay | Oakland SII LP
OC2_PT2107 | Flora/67Th Lp Pres | East Bay | Oakland SII LP
OC1_PT0031 | Oakland Center/8Th Dist Pres | East Bay | Oakland W LP
OC1_PT0046 | Richmond Penn/9Th Dist Pres | East Bay | Richmond N LP
OC2_PT0102 | Richmond 16Th/Bisl Lp Pres | East Bay | Richmond S LP
FFN_PT0033 | Fresno Fowler Lp Pres | Fresno | Fowler LP
FFN_PT0035 | Fresno Fresno-High Lp Pres | Fresno | Fresno High LP
FFN_PT0031 | Fresno Selma Lp Pres | Fresno | Selma LP
FFN_PT0041 | Fresno Tulare Alley Lp Pres | Fresno | West Side LP
K09_PT0031 | Bakersfield Beale Alley Dist Pr | Kern | Bakersfield LP
REU_PT0001 | Eureka 9Th/I Lp Pres | North Coast | Eureka LP System
STF_PT0002 | Chico Lo Press | North Valley | Chico LP (R-L03, R-L04, R-L05, R-L09, R-L12, R-L14)
SRD_PT0001 | Red-Bluff-Dist Low Press | North Valley | Red Bluff LP (R-106, R-105)
SSA_PT0101 | 19Th/C Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0102 | 24Th/Brdwy Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0103 | 38Th/H Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0106 | 3Rd/I Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0111 | 12Th/S Lo Press | Sacramento | Sacramento Large LP - 10.5" WC MAOP
SSA_PT0131 | Sacramento 14Th/52Nd Lp Pres | Sacramento | Sacramento Small LP - 10.5" WC MAOP
SWO_PT0002 | Wdlnd-Twn Lp Dist Press | Sacramento | Woodland - LP 10.5" WC MAOP
NSF_PT0018 | Amazn/Missn Lp Pres | San Francisco | Alemany 10.5"w.c.
NSF_PT0014 | Silvr/Hlyok Lp Pres | San Francisco | Bayview 10.5"w.c.
NSF_PT0012 | Tarvl/Wwona Lp Pres | San Francisco | Mount Davidson 10.5"w.c.
NSF_PT0020 | Irving/20Th Lp Pres | San Francisco | Sunset 10.5"w.c.
NSF_PT0016 | Presdio/Gry Lp Pres | San Francisco | Western Addition 10.5"w.c.
JSJ_PT0041 | Sn-Jose Gilroy Dist Pres | San Jose | MH-GILROY_Gilroy LP system DR H-98 (6th & Railroad)
JSJ_PT0044 | Sn-Jose 15Th & St John Dist Pr | San Jose | SANTA_CLARA_VALLEY_15th and St. John LP system DR F-63
JSJ_PT0039 | Sn-Jose Shortrg/30Th Dist Pres | San Jose | SANTA_CLARA_VALLEY_30th and Shortridge LP system DR F-53
JSJ_PT0037 | Sn-Jose Bird/Fuller Dist Pres | San Jose | SANTA_CLARA_VALLEY_Bird and Fuller LP system DR F-83
JSJ_PT0035 | Sn-Jose Emory/Chestnt Dist Pres | San Jose | SANTA_CLARA_VALLEY_Emory and Chestnut LP system DR F-55
JLF_PT0002 | Lfyt-Cvc Lo Press | San Jose | SANTA_CLARA_VALLEY_Park and Newhall LP system DR F-25
JSJ_PT0031 | Sn-Jose 12Th/Margaret Dist Pres | San Jose | SANTA_CLARA_VALLEY_Santa Clara and Margaret LP system DR F-77
JSJ_PT0033 | Sn-Jose Humboldt/Vine Dist Pres | San Jose | SANTA_CLARA_VALLEY_Vine and Humboldt LP system DR G-09
SMY_PT0031 | Mary-Glc Willow Alley/12Th Lp Pres | Sierra | MRY; Marysville Low Pressure
FEH_PT0003 | Elm & Hutch Lodi Lp Dist Press | Stockton | Lodi LP
FST_PT0043 | Stockton GLC Worth/Bieghle Lp Pres | Stockton | Stockton LP ST-LP-01-C (Worth & Biehle)
FST_PT0041 | Stockton GLC 5Th/Monroe Lp Pres | Stockton | Stockton LP ST-LP-02-C (5th & Monroe)
FST_PT0037 | Stockton GLC Carltn/Mtdiab Lp Pres | Stockton | Stockton LP ST-LP-03-C (Carlton & Mt Diablo)
FST_PT0039 | Stockton GLC Church/Snjose Lp Pres | Stockton | Stockton LP ST-LP-04-C (Church & San Jose)
FSN_PT0004 | Airport-Way & Sonora Lp Press | Stockton | Stockton LP ST-LP-05A-C (Airport & Sonora)
FST_PT0033 | Stockton GLC Sunset/Chrkee Lp Pres | Stockton | Stockton LP ST-LP-06-C (Sunset & Cherokee)
FST_PT0035 | Stockton GLC Harding/Huntr Lp Pres | Stockton | Stockton LP ST-LP-07-C (Harding & Hunter)
FST_PT0031 | Stockton GLC Filbert/Hardg Lp Pres | Stockton | Stockton LP ST-LP-08-C (Filbert & Harding)
FFN_PT0053 | Yosemite Madera Lp Pres | Yosemite | Madera LP
FME_PT0032 | Mrcd-V60 Yosemite Merced Lp Pres | Yosemite | Merced LP
FCT_PT0008 | Cffe-Clta G Street Pressure | Yosemite | Modesto LP MOLP-3,15, & 16
FST_PT0051 | Stockton GLC Yosemite Modesto Lp Pres | Yosemite | Modesto LP MOLP-5,7,10, & 12
F1J_PT0030 | Yosemite Oakdale Lp Press | Yosemite | Oakdale LP
FST_PT0061 | Stockton GLC Harding/Funston Lp Pres | Yosemite | Stockton LP ST-LP-05B-C (Harding & Funston)
FWA_PT0030 | West Ave Reg Yosemite Turlock LP Pres | Yosemite | Turlock LP
None |  | Fresno | Fresno Downtown LP (Modeled with F-C-S)
N9M_PT0002 | Ninth and Market Lo Press | San Francisco | 9th St and Market St 10.5"w.c.

## Regulation Sta. (hidden)
Note: Each row represents a single pressure control device. Filter by the HIS Name column to see all the equipments for an individual HIS.
Note: The source equipment shown is for normal operating conditiions, in some circumstances the pipeline flow will change.
Note: The equipment is listed by Pressure Control Device therefore in a parallel run station with Reg/Mon there will be two line items listed, one for each run.
HIS_ID | Plng Engr | Planning Model | HIS Name | HIS Description | Result | PCE | Type | Location | Area | Station Description | Additional Station information | Device Type | Valve | MOP | MAOP | District/Div | Comments
1 | MJA3 | TP_NORTH_BAY | Benica_175 | Benicia DFM | C4-V1 | PCE341 | Station | Vallejo | NGO | L-21 to Benicia DFM | Glenn Cove & Benicia Rd Reg OD 800103 V-3, 4, 5, 6; Vallejo Station OD 086452 V-33, 34, 35, 36 | Monitor | 34 | 175 | 175 | North Bay
1 | MJA3 | TP_NORTH_BAY | Benica_175 | Benicia DFM | C4-V1 | PCE340 | Station | Vallejo | NGO | L-21 to Benicia DFM | Glenn Cove & Benicia Rd Reg OD 800103 V-3, 4, 5, 6; Vallejo Station OD 086452 V-33, 34, 35, 37 | Monitor | 33 | 175 | 175 | North Bay
2 | MJA3 | TP_NORTH_BAY | Benicia_Ind_Park_175 | Benicia Industrial Park | C4-V1 | MJA3PCE800 | Reg Station | East 2nd St & Reservoir Rd, Benicia |  | V35, East 2nd St & Reservoir Rd Reg Station, Benicia | E. 2nd St & Resvr Rd OD0800104 V-3, 4, 5, 6
3 | MJA3 | TP_NORTH_BAY | Calistoga_150 | Calistoga DFM serving Calistoga & Angwin | C3-V1 | MJA3PCE801 | Reg Station | Pratt Ave & Main St, St Helena |  | R108, York Creek Reg Station, St Helena | York Creek Reg OD0800390 V-3, 4, 5, 6
4 | MJA3 | TP_NORTH_BAY | Calistoga_250 | Calistoga 250# DFM | C2-V1 | MJA3PCE802 | Reg Station | Hwy 29 & Zinfandel Ln, St Helena |  | R68, Hwy 29 & Zinfandel Ln Reg Station, St Helena | Hwy 29 & Zinfandel OD0800126, V-3, 4, 5, 6
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | C4-V3 | PCE365 | Regulator Station | U.S. 101 & Old Rdwd Hwy | NGO | L-21 to Cotati DFM | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 5 | Monitor | 20 | 150 | 150 | North Coast
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | C4-V3 | PCE364 | Regulator Station | U.S. 101 & Old Rdwd Hwy | NGO | L-21 to Cotati DFM | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 6 | Monitor | 19 | 150 | 150 | North Coast
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | C4-V3 | MJA3PCE803 | Reg Station | West Sierra Ave & Old Redwood Hwy, Cotati |  | R375, Cotati Reg Pit, Cotati | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 7
6 | MJA3 | TP_NORTH_BAY | Fairfield_230 | Fairfield DFM to Tabor & Dover | C2-V1 | MJA3PCE804 | Reg Station | Union Ave & Ohio St, Fairfield |  | R07, Suisun-Fairfield Reg Station, Fairfield | Suisun-Fairfield Reg OD081528 V-56, 57, 58, 59
7 | MJA3 | TP_NORTH_BAY | Fulton_150 | Fulton & Grant Rd DFM to Wikiup and Healdsburg | C4-V1 | MJA3PCE807 | Reg Station | Hart Ln & Fulton Rd, Santa Rosa |  | R124, Hart Ln & Fulton Rd Reg Station, Santa Rosa | Grant School Rd Reg OD082460 V-8, 9, 10, 11 ; Fulton Reg OD0800190 V-13, 14, 15, 16
7 | MJA3 | TP_NORTH_BAY | Fulton_150 | Fulton & Grant Rd DFM to Wikiup and Healdsburg | C4-V1 | MJA3PCE808 | Reg Station | Grant School Rd & Old Redwood Highway, Healdsburg |  | R69, Grant School Rd Reg Station, Healdsburg | Grant School Rd Reg OD082460 V-8, 9, 10, 11 ; Fulton Reg OD0800190 V-13, 14, 15, 17
8 | MJA3 | TP_NORTH_BAY | Fairfield_400 | Fairfield DFM to Travis AFB and Vacaville Prison | C1-V1 | MJA3PCE806 | Reg Station | Petersen Rd, Fairfield |  | R09, Vacaville Reg Station, Fairfield | Vacaville Regulator Station OD081527 V-R1, R2, R3, R4
9 | MJA3 | TP_NORTH_BAY | Fairfield_275 | Fairfield DFM to Rancho Solano | C1-V3 | MJA3PCE805 | Reg Station | Cordelia & Chadbourne Rd, Fairfield |  | R03, Cordelia & Chadbourne Rd Reg Station, Fairfield | Cordelia & Chadbourne Reg OD0800494 V-4, 5, 8, 9
10 | MJA3 | TP_NORTH_BAY | Hiddenbrook_175 | Hiddenbrook DFM to Sky Valley | C1-V1 | MJA3PCE809 | Reg Station | Sky Valley Rd, Vallejo |  | V54, Sky Valley Reg Station, Vallejo | Sky Valley OD0800479 V-3, 4, 5, 6
11 | MJA3 | TP_NORTH_BAY | Mare_Island_100 | Mare Island DFM | C4-V1 | MJA3PCE810 | Reg Station | Pine & Woodrow Ave, Vallejo |  | V13, Pine & Woodrow Ave Reg Station, Vallejo | Pine & Woodrow Ave OD0800157 V-5, 6, 7, 8
12 | MJA3 | TP_NORTH_BAY | Marin_175 | Marin DFM | C3-V1 | PCE339 | Holder | San Rafael | NGO | L-21 to DFM 12-0402-01 | San Rafael Meter & Reg OD183804 V-6, 7, 8, 9, 15, 16, 17, 18 | Monitor | 52 | 175 | 175 | North Bay
12 | MJA3 | TP_NORTH_BAY | Marin_175 | Marin DFM | C3-V1 | PCE338 | Holder | San Rafael | NGO | L-21 to DFM 12-0401-01 | San Rafael Meter & Reg OD183804 V-6, 7, 8, 9, 15, 16, 17, 19 | Monitor | 50 | 175 | 175 | North Bay
13 | MJA3 | TP_NORTH_BAY | Marine_World_125 | Marine World DFM | C3-V2B | MJA3PCE811 | Reg Station | Hwy 80 & Coach Lane, Vallejo |  | V32, Hwy 80 & Coach Lane Reg Station, Vallejo | Hwy 80 & Coach Lane 0800102 V-1
14 | MJA3 | TP_NORTH_BAY | Napa_Valley_150 | Napa Valley 150# DFM | C3-V2B | MJA3PCE812 | Reg Station | Redwood Rd & Solano Ave, Napa |  | R51, Solano Ave Reg Station, Napa | Solano Ave Reg OD0800130 V-3, 4, 5, 6
15 | MJA3 | TP_NORTH_BAY | North_Bay_450 | North Bay 450, Napa Y to Calistoga, Marin, and Santa Rosa | C4-V1 | PCE333 | Meter Station | Napa "Y' | NGO | L-210 to L-21 | Napa Y OD385170 V-5, 11, 25.98, 60 | Monitor | 25.98 | 450 | 450 | North Bay
15 | MJA3 | TP_NORTH_BAY | North_Bay_450 | North Bay 450, Napa Y to Calistoga, Marin, and Santa Rosa | C4-V1 | PCE334 | Meter Station | Napa "Y' | NGO | L-210 to L-21 | Napa Y OD385170 V-5, 11, 25.98, 61 | Monitor | 5 | 450 | 450 | North Bay
16 | MJA3 | TP_NORTH_BAY | North_Bay_610 | North Bay 610, Santa Rosa Compressor to Willits | C2-V1 | PCE354 | Compressor Station | Santa Rosa | NGO | Discharge Pressure Control (K-1) | Santa Rosa Compressor OD082485 | PLC | N/A | 610 | 720 | North Coast
16 | MJA3 | TP_NORTH_BAY | North_Bay_610 | North Bay 610, Santa Rosa Compressor to Willits | C2-V1 | PCE355 | Compressor Station | Santa Rosa | NGO | Discharge Pressure Control (K-2) | Santa Rosa Compressor OD082486 | PLC | N/A | 610 | 720 | North Coast
17 | MJA3 | TP_NORTH_BAY | North_Bay_650 | North Bay 650, Creed to Napa "Y" and Herrmann Station | C2-V1 | PCE58 | Station | Creed | NGO | L-210 W from L400/L401 | Creed Station OD182416 V-7, 8, 10, 14, 16, 17 | Monitor | 16 | 650 | 650 | Rio Vista
17 | MJA3 | TP_NORTH_BAY | North_Bay_650 | North Bay 650, Creed to Napa "Y" and Herrmann Station | C2-V1 | PCE57 | Station | Creed | NGO | L-210 W from L400/L401 | Creed Station OD182416 V-7, 8, 10, 14, 16, 18 | Monitor | 14 | 650 | 650 | Rio Vista
18 | MJA3 | TP_NORTH_BAY | Novato_150 | Novato DFM, Novato Blvd and Diabl to Novato Blvd & Reservoir Rd | C2-V3 | MJA3PCE813 | Reg Station | Diablo Ave & S. Novato Blvd, Novato |  | RA04, Diablo Ave & S. Novato Blvd Reg Station, Novato | Diablo Ave & S. Novato Blvd OD0800128 V-5, 6, 7, 8
19 | MJA3 | TP_NORTH_BAY | Pine_St_150 | Pine St 150# DFM, Pine St Napa Meter Station to Browns Valley | C2-V3 | MJA3PCE814 | Reg Station | Pine St and Highway 29, Napa |  | R38, Pine St Reg Station, Napa | Pine St Reg OD081513 V-13, 24, E
20 | MJA3 | TP_NORTH_BAY | Schellville_150 | Schellville DFM, Schellville Reg Station to 5th St West & MacArthur | C2-V1 | MJA3PCE815 | Reg Station | Highway 121 & Fremont Rd, Sonoma |  | R543, Schellville Reg Station, Sonoma | Shellville Reg 081514 V-10, 11, 12, 13
21 | MJA3 | TP_NORTH_BAY | Sebastopol_150 | Sebastopol 150# DFM, Stone Station Reg to Graton | C4-V1 | MJA3PCE816 | Reg Station | Stone Station Rd, Sebastopol |  | R446, Stone Station Rd Reg Station, Sebastopol | Stone Reg Station OD0800563 V-4, 5, 6, 7
22 | MJA3 | TP_NORTH_BAY | Sebastopol_275 | Sebastopol 275# DFM, Madrone Station to Stone Station | C2-V1 | MJA3PCE817 | Reg Station | Stony Pt Rd & Madrone Ave, Cotati |  | R384, Madrone Ave Reg Station, w/o Cotati | Madrone Ave Reg OD082329 V-23, 24, 27, 28
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | C4-V1 | PCE367 | Regulator Station | Monroe | 7 | L-21C to DFM (1304-01, 1305-01) | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 7 | Monitor | 21 | 200 | 200 | North Coast
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | C4-V1 | PCE366 | Regulator Station | Monroe | 7 | L-21C to DFM (1304-01, 1305-01) | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 8 | Monitor | 20 | 200 | 200 | North Coast
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | C4-V1 | MJA3PCE818 | Reg Station | Fifth St West & Macarthur, Sonoma |  | R591, Fifth St West & Macarthur Reg Station, Sonoma | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 9
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | C2-V1 | MJA3PCE819 | Reg Station | Kaiser Rd, Napa |  | R48, Kaiser Rd Reg Station, Napa | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 6
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | C2-V1 | PCE336 | Meter Station | Napa "Y' | NGO | L-210 to Napa DFM | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 7 | Monitor | 71 | 150 | 150 | North Bay
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | C2-V1 | PCE337 | Meter Station | Napa "Y" | NGO | L-210 to Napa DFM | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 8 | Monitor | 79 | 150 | 150 | North Bay
25 | MJA3 | TP_NORTH_BAY | Trancas_250 | Trancas DFM, Napa | C2-V1 | MJA3PCE820 | Reg Station | Coffield Ave Cul de Sac, Napa |  | R41, Coffield Ave Cul de Sac Reg Station, Napa | Coffield Reg OD0800210 V-3, 4, 5, 6
26 | MJA3 | TP_NORTH_BAY | Vallejo_250 | Vallejo DFM, Herrmann Station to Napa "Y" | C2-V1 | PCE335 | Meter Station | Napa "Y' | NGO | L-210 to L-21 | Napa Y OD385170 V-9, 10; Hermann Station 082454 V-2, 9 | Monitor | 9 | 250 | 275 | North Bay
26 | MJA3 | TP_NORTH_BAY | Vallejo_250 | Vallejo DFM, Herrmann Station to Napa "Y" | C2-V1 | PCE332 | Station | Herrmann | NGO | L-210 to 16" L-21 | Napa Y OD385170 V-9, 10; Hermann Station 082454 V-2, 10 | Monitor | 2 | 250 | 375 | North Bay
27 | MJA3 | TP_VACAVILLE | Vacaville_400 | Vacaville 400 DFM supplied from Hawkins & Lewis Primary Reg Station | C2-V1 | MJA3PCE821 | Reg Station | Hawkins & Lewis Rd, Vacaville |  | R48, Hawkins & Lewis Primary Reg Station, Vacaville | Hawkins & Lewis Primary Reg Station OD0800154 V-R1, R2, R3, R4
28 | MJA3 | TP_VACAVILLE | Vacaville_450 | Vacaville 450 DFM supplied from Vaca Dixon Primary Reg Station | C1-V1 | MJA3PCE822 | Reg Station | Meridian Rd w/o I-80 @ Vaca Dixon Substation, Vacaville |  | R21, Vaca Dixon Primary Reg Station, Vacaville | Vaca Dixon Primary Reg OD0800153 V- 4, 5, 8, 9
29 | NAH1 | TP_PENINSULA | RAYCHEM DFM | DCUST 5760, EQ000032, 1M1559 to RINGB84 | C2-V3 | nah1PCE800 | Station | DCUST 5760 |  | Feeds from L101 into Raychem DFM, 175# MOP | Van Buren Dr & Ringwood Ave Station, B-84
30 | NAH1 | TP_PENINSULA | MIDDLEFIELD RINGWOOD DFM | EQ000027, SRIEXT to SREGDN | C2-V2B | nah1PCE801 | Station | Downstream of Raychem DFM |  | Feeds from Raychem DFM into Middlefield/Ringwood DFM, 120# MOP | Middlefield & Ringwood Reg Station, B-83
31 | NAH1 | TP_PENINSULA | HEALY TO MARTIN | SEGMENT OF LINE NEAR CRESSMAN THAT IS OPERATING AT 200 PSIG | C1-V1 | nah1PCE802 | Station | Near Cressman between Healy/Martin |  | Feeds Healy towards Martin at 200# set pressure | Healy Reg Station
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE171 | Regulator Station | Martin Station | CNTL | L- 132 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 12 | 145 | 145 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE168 | Meter Station | Lomita Park | CNTL | L-101 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 33.68 | 145 | 275 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE169 | Meter Station | Lomita Park | CNTL | L-101 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 24 | 145 | 275 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE170 | Regulator Station | Martin Station | CNTL | L- 132 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 46.59 | 145 | 145 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE191 | Regulator Station | Sullivan Avenue | CNTL | L-109 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 2 | 145 | 150 | Milpitas
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | C4-V1 | PCE192 | Regulator Station | Sullivan Avenue | CNTL | L-109 | Sullivan Station, C-97; Martin Station, Lomita Park Station | Monitor | 13 | 145 | 150 | Milpitas
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | C4-V1 | PCE183 | Terminal | Milpitas | CNTL | L-109 | Milpitas Terminal L132, L109 | Monitor | 39 | 300 | 375 | Milpitas
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | C4-V1 | nah1PCE816 | Station | L132 |  | Feeds into L132 at Milpitas | Milpitas Terminal L132, L110
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | C4-V1 | PCE182 | Terminal | Milpitas | CNTL | L-109 | Milpitas Terminal L132, L111 | Monitor | 37 | 300 | 375 | Milpitas
35 | NAH1 | TP_PENINSULA | L101 | Milpitas to Lomita | C4-V1 | nah1PCE817 | Station | L101 |  | Feeds into L101 at Milpitas | Milpitas Terminal L101
36 | NAH1 | TP_PENINSULA | FOSTER CITY DFM | 0214-01 aka Poinsettia DFM | C2-V2B | nah1PCE803 | Station | Route 0214-01 |  | Feeds Foster City DFM 170# MOP | Pointsettia Ave. Reg Station, A-74
37 | NAH1 | TP_PENINSULA | EL MONTE DFM | Fed at Sierra Vista into recently uprated 201 MOP system | C2-V3 | nah1PCE804 | Station | At Sierra Vista |  | Feeds El Monte DFM 201# MOP | Sierra Vista Ave Reg Station, B-28
38 | NAH1 | TP_PENINSULA | TODO EL MUNDO DFM | 0207-01 | C3-V3 | nah1PCE805 | Station | Route 0207-01 |  | Feeds Todo El Mundo DFM 125# MOP | Woodside and L109 Reg Station, C-10
39 | NAH1 | TP_PENINSULA | RALSTON POLHEMUS DFM | 0208-02 Ralston 0209-01 Polhemus both fed from common reg station, with Ralston endpoint as design control | C4-V3 | nah1PCE811 | Station | Routes 0208-02, 0209-01 |  | Feeds Ralston Polhemus DFM 150# MOP | Ralston Ave. Reg Station, B-03
40 | NAH1 | TP_PENINSULA | PACIFICA DFM | 0213-02, floats off L109 to San Pedro Reg at MP 0.91; Beyond 0.91 the MOP is 90# | C4-V3 | nah1PCE806 | Station | Route 0213-02 |  | Feeds Pacifica DFM 90# MOP | San Pedro Valley Reg Station, C-50
41 | NAH1 | TP_PENINSULA | NORTH FIRST ST DFM | 0806-01 San Jose | C4-V2B | nah1PCE807 | Station | Route 0806-01 |  | Feeds N 1st Street DFM 200# MOP | N. First St & Tasman Dr Reg Station, E-05
42 | NAH1 | TP_PENINSULA | GRANT STEVENS CREEK LAWRENCE DFM | 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from 2 regs Lawrence and Whisman | C4-V2B | nah1PCE809 | Station | Routes 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from Whisman reg |  | Feeds Grant Stevens Creek Lawrence DFM 180# MOP - Whisman | Whisman & Middlefield Reg Station, B-34 ; Lawrence & Lakehaven Dr. Reg Station, C-20
42 | NAH1 | TP_PENINSULA | GRANT STEVENS CREEK LAWRENCE DFM | 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from 2 regs Lawrence and Whisman | C4-V2B | nah1PCE808 | Station | Routes 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from Lawrence reg |  | Feeds Grant Stevens Creek Lawrence DFM 180# MOP - Lawrence | Whisman & Middlefield Reg Station, B-34 ; Lawrence & Lakehaven Dr. Reg Station, C-21
43 | NAH1 | TP_PENINSULA | LAFAYETTE DFM | 0804-03, Santa Clara | C4-V2B | nah1PCE810 | Station | Route 0804-03, Santa Clara |  | Feeds Lafayette DFM 180# MOP | Lafayette & Hogan Reg Station, E-07
44 | JTRc | TP_PENINSULA | SUNNYVALE DFM | aka Britton Ave, GCUST 5813 | C1-V3 | nah1PCE812 | Station | GCUST 5813 |  | Feeds Sunnyvale, Britton Ave DFM 400# MOP | Reg Station C-18
45 | NAH1 | TP_PENINSULA | ALPINE DFM | 0204-01 | C4-V3 | nah1PCE813 | Station | Route 0204-01 |  | Feeds Alpine DFM 170# MOP | Alpine Rd & Piers Ln Reg Station, C-37
46 | NAH1 | TP_PENINSULA | WALSH DFM | 0205-01 | C4-V3 | nah1PCE814 | Station | Route 0205-01 |  | Feeds Walsh Rd DFM 230# MOP | Walsh Rd Reg Station, C-21
47 | NAH1 | TP_PENINSULA | HACIENDAS DFM | 0206-01 | C4-V3 | nah1PCE815 | Station | Route 0206-01 |  | Feeds Haciendas Drive DFM 110# MOP | Woodside Rd Reg Station, C-13
48 | BHH2 | TP_CENTRAL_COAST | L306_839 | L306 - 20" transmission from Kettleman to Estrella River PLS. The Town of Avenal has small DFM's off L306 but these DFM's were modeled at 630 PSIG. | C1-V1 | PCE209 | Compressor Station | Kettleman | SGO | High Discharge Press. Shutdown | Kettleman to Milpitas Lines 100, 190 & 300 382704 Sht 1 | PLC | N/A | 839 | 840 | Kettleman
48 | BHH2 | TP_CENTRAL_COAST | L306_839 | L306 - 20" transmission from Kettleman to Estrella River PLS. The Town of Avenal has small DFM's off L306 but these DFM's were modeled at 630 PSIG. | C1-V1 | PCE208 | Compressor Station | Kettleman | SGO | Discharge Pressure Control | Kettleman to Milpitas Lines 100, 190 & 300 382704 Sht 2 | PLC | N/A | 839 | 840 | Kettleman
49 | BHH2 | TP_CENTRAL_COAST | L306_636 | L306 - 20" transmission from Estralla PLS to Morro Bay Power Plant 275 PSIG primary. SoCal gas company has a tap for emergency supply to their customers. | C1-V1 | PCE225 | Pressure Limiting Station | Estrella River | SGO | L-306 | Estrella River PLS 089659 | Monitor | 4 | 636 | 650 | Kettleman
49 | BHH2 | TP_CENTRAL_COAST | L306_636 | L306 - 20" transmission from Estralla PLS to Morro Bay Power Plant 275 PSIG primary. SoCal gas company has a tap for emergency supply to their customers. | C1-V1 | PCE226 | Pressure Limiting Station | Estrella River | SGO | L-306 to L-306 | Estrella River PLS 089660 | Monitor | 8 | 636 | 650 | Kettleman
50 | BHH2 | TP_CENTRAL_COAST | L306_275 | L306 - Primary to Morro Bay Power Plant. Short piping to the plant from the primary. Min Flow is 450 MSCF, Maximum flow is 7,000 MSCF | C1-V1 | BHH2PCE800 | Regulator Station | Morro Bay PP Pri Reg Station |  | GCUST5912_102_306_70.0200 - 082657 | Morro Bay PP Pri Reg Sta 083657
51 | BHH2 | TP_CENTRAL_COAST | L310_840 | L310 - Tres Pinos to Metz. This line feeds Calpine Cogen and Calpines peaker unit. The feed comes from Tres Pinos off L300A and B. The maximum inlet pressures over the years has been no more than 750 PSIG from L300. Loads 1500 MMCF + 300 MMCF | C1-V1 | BHH2PCE801 | Regulator Station | Tres Pinos Station |  | Tres Pinos Station - 089179 | Tres Pinos Station 089179
52 | BHH2 | TP_CENTRAL_COAST | L301A_396 | Line 301A - Old MOP 396 PSIG, CROP 394 PSIG (2011). This line is exclusive to Moss PP units 6&7. Max capacity of this line is 7,000 mcfh. Units 6&7 peak at 13,800 mcfh and the additional load will come from L301G. This line is currently operating at 3 | C1-V1 | PCE204 | Meter Station | Hollister | CNTL | L-301A from L-300A | Hollister Meter Station 282255 | Monitor | 35 | 315 | 396 | Hollister
52 | BHH2 | TP_CENTRAL_COAST | L301A_396 | Line 301A - Old MOP 396 PSIG, CROP 394 PSIG (2011). This line is exclusive to Moss PP units 6&7. Max capacity of this line is 7,000 mcfh. Units 6&7 peak at 13,800 mcfh and the additional load will come from L301G. This line is currently operating at 3 | C1-V1 | PCE207 | Meter Station | Hollister | CNTL | L-301A from L-300A | Hollister Meter Station 282256 | Monitor | 28 | 315 | 396 | Hollister
53 | BHH2 | TP_CENTRAL_COAST | CARMEL_125 | Carmel DFM - 125 PSIG MOP. This system comes off the Monterey system tied to L301B. Aguaito cuts the pressure into Carmel at 125 PSIG. | C4-V1 | BHH2PCE802 | Regulator Station | Aguajito Road Reg Station |  | Aguajito Road Reg Station - 086445 | Aguajito Road Reg Sta 086445
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE427 | Regulator Station | Metz Road | SGO | L-310 to KC DFM (1st stage) | King City Primary Regulator Station 0800096, and Metz Road Station 183721 | Monitor | 10 | 320 | 320 | Central Coast
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE429 | Regulator Station | Metz Road | SGO | L-310 to KC DFM (2nd stage) | King City Primary Regulator Station 0800096, and Metz Road Station 183722 | Monitor | 21 | 130 | 130 | Central Coast
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE426 | Primary Regulator Station | King City | SGO | L-187 to King City DFM | King City Primary Regulator Station 0800096, and Metz Road Station 183723 | Monitor | 3 | 130 | 130 | Central Coast
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | C2-V1 | PCE428 | Regulator Station | Metz Road | SGO | L-310 to KC DFM (1st stage) | King City Primary Regulator Station 0800096, and Metz Road Station 183724 | Monitor | 11 | 320 | 320 | Central Coast
55 | BHH2 | TP_CENTRAL_COAST | L301BCEF_408 | L301BCEF - 408 MOP CROP 344 MOP regulators set at 324 PSIG at Dolan. This system feeds primarily the Ford Ord, Monterey and Carmel areas. Secondary feed is to Harkins which feeds L187, but is now secondary to L187 and L103 is the primary | C1-V3 | PCE203 | Meter Station | Dolan Road | CNTL | L-301B from L-301G | Dolan Road Meter Sta 083812 | Monitor | 20 | 408 | 408 | Hollister
55 | BHH2 | TP_CENTRAL_COAST | L301BCEF_408 | L301BCEF - 408 MOP CROP 344 MOP regulators set at 324 PSIG at Dolan. This system feeds primarily the Ford Ord, Monterey and Carmel areas. Secondary feed is to Harkins which feeds L187, but is now secondary to L187 and L103 is the primary | C1-V3 | PCE202 | Meter Station | Dolan Road | CNTL | L-301B from L-301G | Dolan Road Meter Sta 083813 | Monitor | 19 | 408 | 408 | Hollister
56 | BHH2 | TP_CENTRAL_COAST | L103_350 | L103 - 350 MOP system. Bolsa set at 330 PSIG to California Street Regulator station | C2-V1 | PCE201 | Meter Station | Bolsa | CNTL | L-301 A&G to L-103 | Bolsa Meter Station 089655 | Monitor | 8 | 350 | 350 | Hollister
56 | BHH2 | TP_CENTRAL_COAST | L103_350 | L103 - 350 MOP system. Bolsa set at 330 PSIG to California Street Regulator station | C2-V1 | PCE200 | Meter Station | Bolsa | CNTL | L-301 A&G to L-103 | Bolsa Meter Station 089656 | Monitor | 7 | 350 | 350 | Hollister
57 | BHH2 | TP_CENTRAL_COAST | L301G_500 | L301G - 500 MOP is the main transmission line that feeds the Central Coast area. This line directly feeds Moss power plant units 1&2 and extra capacity for units 6&7. There is a back feed regulator set at the end of L301G at 260 PSIG to allow pressure t | C2-V3 | PCE206 | Meter Station | Hollister | CNTL | L-301G from L-300A | Hollister Meter Station 282255 | Monitor | 27 | 500 | 500 | Hollister
57 | BHH2 | TP_CENTRAL_COAST | L301G_500 | L301G - 500 MOP is the main transmission line that feeds the Central Coast area. This line directly feeds Moss power plant units 1&2 and extra capacity for units 6&7. There is a back feed regulator set at the end of L301G at 260 PSIG to allow pressure t | C2-V3 | PCE205 | Meter Station | Hollister | CNTL | L-301G from L-300A | Hollister Meter Station 282256 | Monitor | 26 | 500 | 500 | Hollister
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE430 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 1 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE431 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 2 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE432 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 4 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE433 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | 5 | 135 | 275 | Central Coast
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | C1-V1 | PCE434 | Primary Regulator Station | Moss Landing PP | SGO | Power Plant | Moss LandingPower Plant Primary Reg Sta 083811 | Monitor | M | 135 | 275 | Central Coast
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | C2-V3 | PCE424 | Primary Regulator Station | Harkins Rd. | SGO | L-301C to L-187 | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082856 | Monitor | 7 | 313 | 313 | Central Coast
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | C2-V3 | PCE425 | Regulator Station | Harkins Rd. | SGO | L-301C to L-187 | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082857 | Monitor | 6 | 313 | 313 | Central Coast
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | C2-V3 | PCE423 | Regulator Station | California St. | SGO | L-103 to L-103 | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082858 | Monitor | 2 | 313 | 313 | Central Coast
60 | BHH2 | TP_CENTRAL_COAST | MTY1_2_313 | 1813, 1815 Monterey - 313 MOP system. Two stations feed the Fort Ord, Monterey area. 1st & 8th and Davis - Reservation | C2-V1 | BHH2PCE804 | Regulator Station | Davis - Reservation Roads Reg Stat |  | Davis Reservation Reg Station - 089572 | 8th St and 1st Ave Regulator Station 087211 and Davis-Reservation Roads Regulator Station 089572
60 | BHH2 | TP_CENTRAL_COAST | MTY1_2_313 | 1813, 1815 Monterey - 313 MOP system. Two stations feed the Fort Ord, Monterey area. 1st & 8th and Davis - Reservation | C2-V1 | BHH2PCE803 | Regulator Station | 8th St and 1st Ave Reg Station |  | 8th street & 1st Ave - 08721 | 9th St and 1st Ave Regulator Station 087211 and Davis-Reservation Roads Regulator Station 089572
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE438 | Regulator Station | San Juan Rd. | SGO | L-181A to L-181A | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087212 | Monitor | 17 | 242 | 303 | Central Coast
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE436 | Pressure Limiting Station | Rob Roy Junction | SGO | DMF -2 to DFM -1 | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087213 | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080393 | PCE435, PCE436 | Monitor | 15 | 303 | 303 | Central Coast
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE435 | Pressure Limiting Station | Rob Roy Junction | SGO | DFM -2 to DFM -1 | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087214 | Cole Road Reg Sta 089666 and San Juan 0800062 | BHH2PCE808, BHH2PCE809 | Monitor | 14 | 303 | 303 | Central Coast
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | C4-V3 | PCE437 | Regulator Station | San Juan Rd. | SGO | L-181A to L-181A | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087215 | Santa Cruz Underground Holder 080393 | PCE439, PCE440 | Monitor | 12 | 242 | 303 | Central Coast
62 | BHH2 | TP_CENTRAL_COAST | DFM1_2_3_303 | 1816 and 1818 DFM (Felton and Davenport DFM's, Santa Cruz holder). Systems past Rob Roy | C4-V1 | PCE436 | Pressure Limiting Station | Rob Roy Junction | SGO | DMF -2 to DFM -1 | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080392 | Monitor | 15 | 303 | 303 | Central Coast
62 | BHH2 | TP_CENTRAL_COAST | DFM1_2_3_303 | 1816 and 1818 DFM (Felton and Davenport DFM's, Santa Cruz holder). Systems past Rob Roy | C4-V1 | PCE435 | Pressure Limiting Station | Rob Roy Junction | SGO | DFM -2 to DFM -1 | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080392 | Monitor | 14 | 303 | 303 | Central Coast
63 | BHH2 | TP_CENTRAL_COAST | L181B_DFM2_400 | 1817 - 400 MOP system starting at Cole Road Regulator Station and endind at Rob Roy. Cole is the primary feed, and San Juan is the secondary feed | C4-V1 | BHH2PCE808 | Regulator Station | Cole Road Regulator Station |  | Cole Road Regulator Station - 089666 | Cole Road Reg Sta 089666 and San Juan 0800061
63 | BHH2 | TP_CENTRAL_COAST | L181B_DFM2_400 | 1817 - 400 MOP system starting at Cole Road Regulator Station and endind at Rob Roy. Cole is the primary feed, and San Juan is the secondary feed | C4-V1 | BHH2PCE809 | Regulator Station | San Juan Regulator Station |  | San Juan Regulator Station - 0800062 | Cole Road Reg Sta 089666 and San Juan 0800061
64 | BHH2 | TP_CENTRAL_COAST | SANTA_CRUZ_HOLDER | The underground holder is used during winter months to make up capacity to serve the Felton area. It is manually filled each time it is used during a cold event. There is no permanent connection to the transmission system that could over pressure it. | C4-V1 | PCE440 | Underground Holder | Santa Cruz | SGO | Holder Relief | Santa Cruz Underground Holder 080393 | Relief | C | 618 | 618 | Central Coast
64 | BHH2 | TP_CENTRAL_COAST | SANTA_CRUZ_HOLDER | The underground holder is used during winter months to make up capacity to serve the Felton area. It is manually filled each time it is used during a cold event. There is no permanent connection to the transmission system that could over pressure it. | C4-V1 | PCE439 | Underground Holder | Santa Cruz | SGO | Holder Relief | Santa Cruz Underground Holder 080393 | Relief | B | 618 | 618 | Central Coast
65 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Tap | L138A, L138B | C1-V1 | RLP7PCE811 | Regulator Station | Oper. Drw - 081818 |  | Helm tap L138 | Helm Tap Sta. Op Dia. 081818
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC | C4-V1 | RLP7PCE800 | Regulator Station | Oper. Drw - 080421 |  | Tarpey Reg Station | Tarpey Reg Sta. Op Dia. 080421
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC | C4-V1 | PCE449 | Gas Load Center | Fresno | SGO | Header to Belt Main | Oper. Drw - 382885 | Monitor | 19 | 163 | 163 | Fresno
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC | C4-V1 | PCE443 | Regulator Station | Chestnut & Clay | SGO | L-138 to Belt Main | Oper. Drw - 082423 | Monitor | 10 | 163 | 163 | Fresno
67 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Tap | Vernalis Tap to Vernalis Field Valve Lot | C1-V1 | PCE154 | Meter Station | Vernalis | CNTL | L-108 | Oper. Drw - 089654 | Monitor | 6 | 720 | 720 | Tracy
68 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Vernalis Valve Lot | Vernalis Field Valve Lot to Ripon Reg Station | C2-V1 | RLP7PCE809 | Regulator Station | Oper. Drw - 082994 |  | Vernalis Mixing Sta. L112 to L108 | Op Dia. 082994
69 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L215 | Oak Flat to West Ave Reg. | C1-V1 | RLP7PCE808 | Regulator Station | Oper. Drw - 082544 |  | Oak Flat Rd. Mt. Sta. L215 | Op Dia. 082544
70 | RLP7 | TP_SAN_JOAQUIN_VALLEY | 7224-19 | Stanislaus DFM | C4-V2B | RLP7PCE806 | Regulator Station | Oper. Drw - 0800480 |  | Oregan and Santa Anna | Op Dia. 0800480
71 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Oakdale | Oakdale, Escalon, Riverbank | C2-V1 | PCE465 | Regulator Station | Coffee and Claratina | SGO | 408 System to 180 System | Coffee & Claratina Reg Sta Op Dia. 082435 | Monitor | 26 | 180 | 180 | Yosemite
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | PCE464 | Regulator Station | Coffee and Claratina | SGO | 408 System to 260 System | Coffee & Claratina Reg Sta Op Dia. 082435 | Monitor | 29 | 260 | 260 | Yosemite
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | PCE463 | Regulator Station | Coffee and Claratina | SGO | 408 System to 260 System | Coffee & Claratina Reg Sta Op Dia. 082435 | Monitor | 28 | 260 | 260 | Yosemite
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | RLP7PCE817 | Regulator Station | Oper. Drw - 082545 |  | West Ave. Reg. Sta | Op Dia. 082545
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. | C2-V3 | RLP7PCE816 | Regulator Station | Oper. Drw - 0800499 |  | Morgan Ave. and Morgan Rd. | Op Dia. 0800499
73 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Modesto | 408 psig system. | C4-V1 | RLP7PCE802 | Regulator Station | Oper. Drw - 086444 |  | Ripon Modesto Mt. Sta. | Op Dia. 0800719
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) | C4-V1 | PCE450 | Junction | Fresno | SGO | L- 118 from L-111S | Oper. Drw - 081524 | Monitor | 4 | 400 | 400 | Fresno
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) | C4-V1 | RLP7PCE804 | Regulator Station | Oper. Drw - 081543 |  | Herndon Junction L134 to L118 | Op Dia. 081543
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) | C4-V1 | RLP7PCE803 | Regulator Station | Oper. Drw - 082548 |  | Bradbury Rd. Sta. L118 | Op Dia. 082548
75 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Eight Mile Road DFM | Eight Mile Road DFM fed from L108. | C1-V3 | RLP7PCE822 | Regulator Station | Oper. Drw - 0802402 |  | Eight Mile Rd. PLS L108 | Op Dia. 0802402
76 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L148 | McMullin Ranch to Morgan/Whitmore | C4-V1 | RLP7PCE801 | Regulator Station | Oper. Drw - 081792 |  | McMullin Sta.L108 to L148 | Op Dia. 081792
77 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Hammertown | Hammertown and Tom 'O' Shanter | C1-V3 | RLP7PCE823 | Regulator Station | Oper. Drw - 9892403 |  | West Lane and Hammertown Rd. L108 | Op Dia. 0802403
79 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Zephyr Road DFM | Fed from L108 1606 at Carpenter Rd | C1-V3 | RLP7PCE821 | Regulator Station | Oper. Drw - 089442 |  | Carpenter Rd. Sta. | Op Dia. 0800484
80 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Alpine DFM | 1621-01, DREG 4939. Fed from L108. | C4-V3 | RLP7PCE805 | Regulator Station | Oper. Drw - 0800489 |  | Stadium and San Rafael Reg. Sta. L108 | Op Dia. 0800489
81 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Manteca DFM | 1602-01. MP 0.7 - MP 2.66 | C3-V3 | RLP7PCE807 | Regulator Station | Oper. Drw - 081534 |  | Manteca Reg. Sta. | Op Dia. 081534
83 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Stockton L108 | Ripon-Modesto Meter Station to Eight Mile Road. | C4-V1 | RLP7PCE825 | Regulator Station | Oper. Drw - 086444 |  | Ripon Modesto Mt. Sta. L108 | Op Dia. 086444
84 | RLP7 | OTHER | Patterson DFM | Served from L-2. | C2-V3 | PCE149 | Station | Patterson | CNTL | Patterson from L-2 | Oper. Drw - 085517 | Monitor | 14 | 250 | 395 | Tracy
85 | RLP7 | OTHER | Los Banos DFM | Served from L-2. | C2-V1 | RLP7PCE810 | Regulator Station | Oper. Drw - 183301 |  | Los Banos Sta. L2 | Op Dia.183301
86 | RLP7 | OTHER | L-331 | Crosstied to L-2 and L-401 | C1-V1 | PCE104 | Station | Bayview Road | CNTL | L-331 from L-401 | Oper. Drw - 087998 | Monitor | 12 | 890 | 890 | Tracy | Removed
86 | RLP7 | OTHER | L-331 | Crosstied to L-2 and L-401 | C1-V1 | PCE105 | Station | Bayview Road | CNTL | L-331 from L-401 | Oper. Drw - 087999 | Monitor | 16 | 890 | 890 | Tracy | Removed
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE446 | Station | Elkhorn | SGO | L- 138 | Oper. Drw - 085548 | Monitor | 3 | 650 | 650 | Fresno
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE447 | Station | Elkhorn | SGO | L- 138 | Oper. Drw - 085549 | Monitor | 4 | 650 | 650 | Fresno
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE451 | Meter & Regulator Station | Helm Junction | SGO | L-111 N from L-138A | Oper. Drw - 081541 | Monitor | 9 | 650 | 650 | Fresno
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. | C2-V1 | PCE452 | Meter & Regulator Station | Helm Junction | SGO | L-111 N from L-138A | Oper. Drw - 081541 | Monitor | 10 | 650 | 650 | Fresno
88 | RLP7 | TP_SAN_JOAQUIN_VALLEY | FGLC | FGLC to FJCT | C2-V1 | PCE448 | Gas Load Center | Fresno | SGO | L-138 to L-118 & L-111 | Oper. Drw - 382885 | Monitor | 107 | 400 | 400 | Fresno
88 | RLP7 | TP_SAN_JOAQUIN_VALLEY | FGLC | FGLC to FJCT | C2-V1 | PCE450 | Junction | Fresno | SGO | L- 118 from L-111S | Oper. Drw - 081542 | Monitor | 4 | 400 | 400 | Fresno
89 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118 | FJCT to V-60.45 (Merced). | C4-V2B | PCE450 | Junction | Fresno | SGO | L- 118 from L-111S | Oper. Drw - 0815402 | Monitor | 4 | 400 | 400 | Fresno
91 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Selma | 1209-02. Feed to Selma. | C2-V3 | RLP7PCE815 | Regulator Station | Oper. Drw - |  | Selma DFM Sta. off L138 Leonard N/O South DR J57 | Oper. Drw -
92 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L307/134 | Spreckels to Herndon Jct | C2-V1 | PCE235 | Meter Station | Spreckels Sugar | SGO | L-307 from L-2 | Oper. Drw - 085533 | Monitor | 13 | 500 | 500 | L300-N
92 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L307/134 | Spreckels to Herndon Jct | C2-V1 | PCE234 | Meter Station | Spreckels Sugar | SGO | L-307 from L-2 | Oper. Drw - 085533 | Monitor | 9 | 500 | 500 | L300-N
93 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kerman | Kerman DFM serves Kerman and Biola | C2-V3 | RLP7PCE820 | Regulator Station | Oper. Drw - 0800141 |  | Kerman Reg. Sta L134 | Oper. Drw -
94 | RLP7 | TP_TRACY | Tracy | Serves City of Tracy. | C1-V1 | PCE152 | Station | Tracy | CNTL | L-162 from L-2 | Oper. Drw - 385181 | Monitor | 91 | 365 | 720 | Tracy
94 | RLP7 | TP_TRACY | Tracy | Serves City of Tracy. | C1-V1 | PCE138 | Station | MacArthur Road | CNTL | Tracy from L-2 | Oper. Drw - 081666 | Monitor | 11 | 365 | 365 | Tracy
95 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Baker Commodities | Transmission along Madera Ave that feeds Foster Farms and Baker Commodities. | C1-V2B | RLP7PCE819 | Regulator Station | Oper. Drw - |  | Baker Commodities Reg. Sta. L111A mp 8.83
96 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Herndon & Hayes | Fed from Cattern and Weber. | C1-V3 | RLP7PCE824 | Regulator Station | Oper. Drw - |  | Cattem and Weber DR 45 L118A mp 10.5
97 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kamm Ave Feeder | Served from L111 and feed Con Agra Foods and Helm Sulfur. | C1-V2B | RLP7PCE818 | Regulator Station | Oper. Drw - |  | Kamm Ave. DFM Sta L111 Serving Brita Tomato DR K05
98 | RLP7 | OTHER | L-186 | Serves Dos Palos from L-2. | C2-V3 | RLP7PCE826 | Regulator Station | Oper. Drw - 085509 |  | Dos Palos Sta. L2 | Op Dia. 085509
99 | RLP7 | OTHER | Nees Ave DFM | Serves Olam West (DeFrancisco) from L-2. | C1-V2B | PCE467 | Regulator Station | De Francisco | SGO | De Francisco from L-2 | Oper. Drw - 089657 | Monitor | 3 | 620 | 620 | Yosemite
100 | RLP7 | OTHER | Newman-Gustine | Looped DFM to serve Newman and Gustine. | C2-V3 | PCE134 | Station | Gustine | CNTL | Gustine from L-2 | Oper. Drw - 085529 | Monitor | 11 | 150 | 150 | Tracy
100 | RLP7 | OTHER | Newman-Gustine | Looped DFM to serve Newman and Gustine. | C2-V3 | PCE142 | Station | Newman | CNTL | Newman from L-2 | Oper. Drw - 183202 | Monitor | 11 | 150 | 150 | Tracy
101 | c5s1 | TP_SAN_JOSE | L100 | L100 from Milpitas Terminal to PLS7 | C4-V1 | c5s1PCE800 | Terminal | Milpitas Terminal & L100, San Jose |  | Milpitas Terminal L100 Feed | Milpitas Terminal
102 | c5s1 | TP_SAN_JOSE | Dixon Landing DFM | DFM from L131 at Dixon Landing & 880 to Dixon Landing & Milpitas Blvd. | C2-V1 | c5s1PCE801 | Reg Station | Dixon Landing DFM & L131, San Jose |  | Dixon Landing Reg Station E-15 | Dixon Landing & Hwy 880 Regulator Station
103 | c5s1 | TP_SAN_JOSE | Barber DFM | DFM from Milpitas Terminal to Lundy & Murphy Station (F17) and Abbott-Milpitas Alvisio Road (E11). | C2-V3 | PCE180 | Terminal | Milpitas | CNTL | SJ DFM | Milpitas Terminal (SJDFM) | Monitor | 33 | 160 | 200 | Milpitas
104 | c5s1 | TP_SAN_JOSE | Mabury DFM | DFM from Mabury Station at Mabury Rd & Pine Hollow (F06) to Autumn & Julian Reg Station (F47). | C2-V1 | c5s1PCE802 | Reg Station | Mabury DFM & L100, San Jose |  | Mabury Reg Station F-06 | Mabury Road Regulator Station
105 | c5s1 | TP_SAN_JOSE | Tully DFM | DFM from Tully Station (F78) to Roberts & Fisher Station (D24). | C4-V1 | PCE460 | Station | Tully | SGO | Tully DFM from L-100 | Tully Regulator Station | Monitor | 4 | 200 | 200 | San Jose
106 | c5s1 | TP_SAN_JOSE | Fontanoso DFM | DFM from Fontanoso Reg Station (G77) to Cottle & Poughkeepsie Reg Station (G49). | C1-V1 | c5s1PCE803 | Reg Station | Fontanoso DFM & L300A, San Jose |  | Fontanoso Reg Station G-77 | Fontanoso Road Regulator Station
107 | c5s1 | TP_SAN_JOSE | Blossom Hill DFM | DFM from Cottle & Poughkeepsie Reg Station (G49) to endpoints of Cottle & Santa Teresa Reg Station (G73) and Rajkovich & Almaden Expressway Reg Station (G79). | C3-V1 | c5s1PCE804 | Reg Station | Blossom Hill DFM & Fontanoso DFM, San Jose |  | Cottle & Poughkeepsie Reg Station G-49 | Cottle & Poughkeepsie Road Regulator Station
108 | c5s1 | TP_GILROY | Emado DFM | DFM from Emado Reg Station (H15) to Emado & Hwy 101 Reg Station (H23). | C3-V3 | c5s1PCE805 | Reg Station | Emado DFM & L300A, San Jose |  | Emado Reg Station H-15 | Emado Ave Regulator Station
109 | c5s1 | TP_GILROY | Puppo DFM | DFM from Hwy 101 & Scheller Ave Reg Station (H18) to Monterey Hwy & Puppo R/W Reg Station (H16). | C1-V3 | c5s1PCE806 | Reg Station | Puppo DFM & L300A, San Jose |  | Hwy 101 & Scheller Reg Station H-18 | Hwy 101 and Scheller Ave Regulator Station
110 | c5s1 | TP_GILROY | Cochrane DFM | DFM from Peet & Cochrane Reg Station (H01) to N/S Cochrane, w/o Hwy 101 Reg Station (H03). | C2-V3 | c5s1PCE807 | Reg Station | Cochrane DFM & L300A, Morgan Hill |  | Peet & Cochrane Road Reg Station H-01 | Peet & Cochrane Regulator Station
111 | c5s1 | TP_GILROY | Diana DFM | DFM from Diana Reg Station(H06) east to Diana & L300A Reg Station (H05) and west to Diana e/o Railroad Reg Station (H09). | C2-V2B | c5s1PCE808 | Reg Station | Diana DFM & L300A, Morgan Hill |  | L300A & Diana Reg Station H-06 | Diana Ave Regulator Station
112 | c5s1 | TP_GILROY | Church DFM | DFM from Church Ave Reg Station (H46) to Church & Old 101 Hwy (H33). | C1-V1 | c5s1PCE809 | Reg Station | Church DFM & L300A, San Martin |  | Church Ave Reg Station H-46 | Church Ave Regulator Station
113 | c5s1 | TP_GILROY | Roop DFM | DFM from Roop Road Reg Station (H95) to Roop Road & New Reg Station (H96). | C3-V3 | c5s1PCE810 | Reg Station | Roop Road DFM & L300A, Gilroy |  | Roop Road Reg Station H-95 | Roop Road Regulator Station
114 | c5s1 | TP_GILROY | Bloomfield DFM | DFM from Bloomfield Reg Station (H73) to Kelton Dr & First Reg Station. DFM includes Calpine/Gilroy Power Plant. | C2-V1 | c5s1PCE811 | Reg Station | Bloomfield DFM & L300A, Gilroy |  | Bloomfield Reg Station H-73 | Bloomfield Regulator Station
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | C2-V1 | PCE374 | Tap | Redding Calaveras | NGO | Calaveras Cement from L-400/401 | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | Monitor | 8 | 600 | 600 | North Valley
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | C2-V1 | PCE375 | Tap | Redding Calaveras | NGO | Calaveras Cement from L-400/401 | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | Monitor | 10 | 600 | 600 | North Valley
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | C2-V1 | PCE40 | Tap | Redding Calaveras | NGO | L-400 | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | Relief(QO) | H | 865 | 911 | Willows
116 | ZTR1 | TP_HUMBOLDT | 1309_ALTON_100 | 100 psig DFM served from L177A via the Alton Primary that serves Rio Dell and Scotia | C4-V1 | ZTR1PCE801 | Reg Station | Alton Primary, Humboldt County |  | NCR 67 | Alton Primary OD082931 V-14, 15, 16, 17
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE361 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 71 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE357 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE360 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 70 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE348 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 430 | 430 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE345 | Regulator Station | Arcata | NGO | L-137B to L-137D | Gerber Compressor OD284543 V-21, 22 | Monitor | 27 | 250 | 350 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE346 | Regulator Station | Arcata | NGO | L-137B to L-137D | Gerber Compressor OD284543 V-21, 22 | Monitor | 30 | 250 | 350 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE356 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 350 | 425 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE347 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 430 | 430 | North Coast
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | C4-V1 | PCE38 | Compressor Station | Gerber | NGO | L-177 from L-400/L-401 | Gerber Compressor OD284543 V-21, 22 | Monitor | 21 | 610 | 819 | Willows
118 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_430 | L177A Cummins Creek to Tompkins Hill | C4-V1 | PCE347 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 430 | 430 | North Coast
118 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_430 | L177A Cummins Creek to Tompkins Hill | C4-V1 | PCE348 | Pressure Limiting Station | Cummings Creek | NGO | L-177(Ryan Slough) from L-177 (Gerber) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 430 | 430 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE356 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 7 | 350 | 425 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE357 | Meter & Regulator Station | Tompkins Hill | NGO | L-177(Ryan Slough) from L-177 (Cummings Crk) | Gerber Compressor OD284543 V-21, 22 | Monitor | 8 | 350 | 425 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE360 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 70 | 350 | 425 | North Coast
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | C4-V1 | PCE361 | Meter & Regulator Station | Tompkins Hill | NGO | L-177 from 4" & 6" L-125 | Gerber Compressor OD284543 V-21, 22 | Monitor | 71 | 350 | 425 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE362 | Station | Union Street (Eureka) | NGO | Dist. Regulator Station | Cummins Creek OD082474 V-2, 4, 7, 8 | Monitor | 25 | 50 | 50 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE349 | Regulator Station | Elk River Road | NGO | L-177 to L-126C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 14 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE350 | Regulator Station | Elk River Road | NGO | L-177 to L-126C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 15 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE351 | Regulator Station | Ryan Slough | NGO | L-177 to L-137A & L-137C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 13 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE352 | Regulator Station | Ryan Slough | NGO | L-177 to L-137A & L-137C | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 15 | 167 | 167 | North Coast
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 | C2-V1 | PCE363 | Station | Union Street (Eureka) | NGO | Lines 126 to Line 126 | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 24 | 167 | 167 | North Coast
123 | ZTR1 | TP_HUMBOLDT | L137D_GIUNTOLI_250 | 10" Line from Arcata Reg to Giuntoli | C2-V1 | PCE346 | Regulator Station | Arcata | NGO | L-137B to L-137D | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 30 | 250 | 350 | North Coast
123 | ZTR1 | TP_HUMBOLDT | L137D_GIUNTOLI_250 | 10" Line from Arcata Reg to Giuntoli | C2-V1 | PCE345 | Regulator Station | Arcata | NGO | L-137B to L-137D | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 27 | 250 | 350 | North Coast
124 | ZTR1 | TP_HUMBOLDT | 1310/1311_LOLETA_170 | 2 DFM's fed fro Tompkins Hill serving Loleta and Fernbridge | C2-V1 | PCE359 | Meter & Regulator Station | Tompkins Hill | NGO | Distribution Lines from Mixed Gas | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 62 | 170 | 170 | North Coast
124 | ZTR1 | TP_HUMBOLDT | 1310/1311_LOLETA_170 | 2 DFM's fed fro Tompkins Hill serving Loleta and Fernbridge | C2-V1 | PCE358 | Meter & Regulator Station | Tompkins Hill | NGO | Distribution Lines from Mixed Gas | Tompkins Hill OD183697 V-50, 51, 66, 78 | Monitor | 61 | 170 | 170 | North Coast
126 | ZTR1 | TP_HUMBOLDT | 1001_REDBLUFF_470 | Rawson Road DFM serving Red Bluff West, Pactiv, and Neo Power | C2-V1 | ZTR1PCE800 | Reg Station | Rawson Road, Red Bluff |  | R102 | Tompkins Hill OD183697 V-50, 51, 66, 78
127 | ZTR1 | TP_CHICO | 1027_OROVILLE_110 | Oroville 110# DFM | C3-V1 | ZTR1PCE802 | Reg Station | Lincoln & Oro Dam |  | ORB-11 | Tompkins Hill OD183697 V-50, 51, 66, 78
127 | ZTR1 | TP_CHICO | 1027_OROVILLE_110 | Oroville 110# DFM | C3-V1 | ZTR1PCE803 | Reg Station | 5th & Pomona |  | ORB-51 | Arcata Reg OD082630 V-26, 27, 30, 31
128 | ZTR1 | TP_CHICO | 1027_OROVILLE_235 | Oroville 235# DFM | C4-V1 | PCE378 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (N) | Arcata Reg OD082630 V-26, 27, 30, 31 | Monitor | 28 | 235 | 235 | North Valley
128 | ZTR1 | TP_CHICO | 1027_OROVILLE_235 | Oroville 235# DFM | C4-V1 | PCE377 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (S) | Arcata Reg OD082630 V-26, 27, 30, 31 | Monitor | 24 | 235 | 235 | North Valley
129 | ZTR1 | TP_CHICO | 1004_ORLAND_490 | Orland 490# DFM from Primary to Secondary | C1-V1 | ZTR1PCE804 | Reg Station | Orland Primary at L177 (6th & Wyo) |  | R-001 | Arcata Reg OD082630 V-26, 27, 30, 31
130 | ZTR1 | TP_CHICO | 1004_ORLAND_170 | Orland 170# DFM from Secondary to Tertiary | C1-V1 | ZTR1PCE805 | Reg Station | Orland Secondary |  | R-002 | Tompkins Hill OD183697 V-60, 61, 62, 63
131 | ZTR1 | TP_CHICO | L209/128_WILLOWS_479 | Manville - Willows - Ordbend 479# Line | C1-V2B | PCE42 | Meter & Regulator Station | Johns Manville | NGO | L-209 from L-400 | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 6 | 479 | 720 | Willows
131 | ZTR1 | TP_CHICO | L209/128_WILLOWS_479 | Manville - Willows - Ordbend 479# Line | C1-V2B | PCE41 | Meter & Regulator Station | Johns Manville | NGO | L-209 from L-400 | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 3 | 479 | 720 | Willows
132 | ZTR1 | TP_CHICO | 1022_ARTOIS_200 | DFM serving Artois from Jacinto (L128) 200# | C1-V2B | PCE373 | Regulator Station | Jacinto | NGO | L-128 to Artois DFM | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 29 | 200 | 200 | North Valley
132 | ZTR1 | TP_CHICO | 1022_ARTOIS_200 | DFM serving Artois from Jacinto (L128) 200# | C1-V2B | PCE372 | Regulator Station | Jacinto | NGO | L-128 to Artois DFM | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 25 | 200 | 200 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE369 | Regulator Station | Grape Way | NGO | L-177 to L-177 | Tompkins Hill OD183697 V-60, 61, 62, 63 | Monitor | 9 | 469 | 469 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | ZTR1PCE808 | Reg Station | Butte Station, Chico |  | Butte 177 | Red Bluff & Diamond National Primary OD082621 V-4, 5, 6, 7
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE49 | Regulator & Odor Station | Fell | NGO | L-169 to L-136 | Red Bluff & Diamond National Primary OD082621 V-4, 5, 6, 8 | Monitor | 21 | 550 | 550 | Meridian
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | ZTR1PCE807 | Reg Station | Neal Road, Paradise |  | P-001
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE376 | Meter Station | Richvale "Y" | NGO | L-50 (S) from L-50 (N) | Richvaley Y OD081499 | Monitor | 38 | 250 | 250 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE368 | Regulator Station | Grape Way | NGO | Line 177 to Line 177 | Grape Way OD086447 V-4, 5, 8, 9 | Monitor | 4 | 469 | 469 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE50 | Regulator & Odor Station | Fell | NGO | L-169 to L-136 | Fell Reg & Oderizer OD082551 V-21, 22, 24, 25 | Monitor | 22 | 550 | 550 | Meridian
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE39 | Compressor Station | Gerber | NGO | L-177 from L-400/L-401 | Gerber Compressor OD284543 V-27, 28; Fell Reg & Oderizer OD082551 V-21, 22, 24, 25; Grape Way OD086447 V-4, 5, 8, 9; Butte Station OD284095 V-8, 9, 10, 11, 16, 17, 18, 19; Richvaley Y OD081499 V-28, 30, 32 | Monitor | 28 | 610 | 819 | Willows
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE378 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (N) | Richvaley Y OD081499 | Monitor | 28 | 235 | 235 | North Valley
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | C4-V1 | PCE377 | Meter Station | Richvale "Y" | NGO | Oroville DFM from L-50 (S) | Richvaley Y OD081499 | Monitor | 24 | 235 | 235 | North Valley
135 | ZTR1 | TP_CHICO | L50_CHICO_400 | L50 from Butte Station to Richvale Y, including L50B to Paradise | C4-V1 | ZTR1PCE808 | Reg Station | Butte Station, Chico |  | Butte 177 | Butte Station OD 284095 V-8, 9, 10, 11
135 | ZTR1 | TP_CHICO | L50_CHICO_400 | L50 from Butte Station to Richvale Y, including L50B to Paradise | C4-V1 | ZTR1PCE807 | Reg Station | Neal Road, Paradise |  | P-001 | Butte Station OD 284095 V-8, 9, 10, 11
138 | ZTR1 | TP_CHICO | 1019_HAM-CITY_250 | DFM serving Prune Dryer south of Hamilton City | C2-V3 | ZTR1PCE813 | Reg Station | Hamilton City |  | R-004 | Hamilton City Regulator OD082877 V-56, 57, 60, 61
139 | ZTR1 | TP_REDDING | 1042_MCARTHUR_525 | DFM fed from L400, serving Fall River and McArthur | C1-V3 | ZTR1PCE814 | Reg Station | Red Mtn Rd Glenburn |  | R75 | Red Mt. Rd. Glenburn
140 | ZTR1 | TP_CHICO | 1009_MILLS-ORCHARD_200 | DFM fed from L177A MP9.88 to Mills Orchard and Sunsweet Dryers | C1-V3 | ZTR1PCE815 | Reg Station | Mills Orchard Primary |  | R-008 | Mills Orchard Primary OD0800189 V-2, 4, 5, 7
148 | HxFe | TP_KERN | HXFEPS704 | Pioneer_DFM | C1-V1 | HXFEPCE800 | DFM | Bakersfield |  | Bakersfield reg station feeding the Pioneer_DFM | Bakersfield Reg Sta
152 | TCQ2 | TP_EBAY | DFM_2404_85 | 85 psig DFM near Enterprise in Newark - Salt Dryers | C3-V3 | tcq2PCE801 | DFM | Timber and Central, Newark |  | Timber Reg Station; RF39 | Timber Reg Station; RF39
153 | TCQ2 | TP_EBAY | DFM_3010_100 | Wilbur DFM | C2-V3 | tcq2PCE814 | DFM | Wilbur Ave DFM RS |  | Wilbur Ave DFM RS | Wilbur Reg Station
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | C2-V1 | PCE74 | Terminal | Antioch | CNTL | L-191 from L-400 | Antioch Terminal - Control Valves | Monitor | 93 | 600 | 600 | Los Medanos
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | C2-V1 | PCE75 | Terminal | Antioch | CNTL | L-191 from L-400 | Antioch Terminal - Control Valves | Monitor | 95 | 600 | 600 | Los Medanos
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | C2-V1 | PCE73 | Terminal | Antioch | CNTL | L-191 from L-400 | Antioch Terminal - Control Valves | Monitor | 92 | 600 | 600 | Los Medanos
155 | TCQ2 | TP_EBAY | Line_105_250 | 250 psig Line 105 from Irvington to Enrico Station | C2-V1 | PCE163 | Station | Irvington | CNTL | L- 105N from Mixer | Irvington Station | Monitor | 5 | 250 | 250 | Milpitas
156 | TCQ2 | TP_EBAY | Line_105B_397 | 397 psig Line 105B Herrmann to San Pablo | C2-V1 | PCE332 | Station | Herrmann | NGO | L-210 to 16" L-21 | Hermann Station - Control Valves | Monitor | 2 | 250 | 375 | North Bay
157 | TCQ2 | TP_EBAY | DFM 3004 | Port Costa Feeder from Stanpac 3 | C1-V2B | PCE324 | Regulator Station | Port Costa | NGO | Port Costa Mtr Sta from SP3 | Port Costa Reg Station | Monitor | 6 | 315 | 338 | East Bay-N
157 | TCQ2 | TP_EBAY | DFM 3004 | Port Costa Feeder from Stanpac 3 | C1-V2B | PCE323 | Regulator Station | Port Costa | NGO | Port Costa Mtr Sta from SP3 | Port Costa Reg Station | Monitor | 5 | 315 | 338 | East Bay-N
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | PCE325 | Station | San Pablo | NGO | L-105A from L-105B | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | Monitor | 64 | 150 | 198 | East Bay-N
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | PCE326 | Pressure Limiting Station | Oakland | NGO | L-153 to L-105 N | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | Monitor | 22 | 135 | 198 | East Bay-S
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | PCE327 | Station | Fairway Ave. Crossover | NGO | L-105N from L-153 | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | Monitor | 12 | 135 | 198 | Mission
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | C2-V1 | tcq2PCE800 | LT | Grant Road, San Lorenzo |  | Enrico Station | Fairway Station, Enrico Station, East Bay PLS (All Control Valves)
159 | TCQ2 | TP_EBAY | DFM_0141-01_110 | C&H Sugar DFM | C1-V3 | PCE319 | Station | Crockett | NGO | C&H Sugar Tap From L-105B/21H | Crockett Station | Monitor | 3 | 110 | 110 | East Bay-N
159 | TCQ2 | TP_EBAY | DFM_0141-01_110 | C&H Sugar DFM | C1-V3 | PCE320 | Station | Crockett | NGO | C&H Sugar Tap From L-105B/21H | Crockett Station | Monitor | 4 | 110 | 110 | East Bay-N
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE166 | Station | Irvington | CNTL | Mixer from L- 107 | Irvington Station | Monitor | 66 | 476 | 477 | Milpitas
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE165 | Station | Irvington | CNTL | Mixer from L- 131 | Irvington Station | Monitor | 50 | 476 | 595 | Milpitas
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE163 | Station | Irvington | CNTL | L- 105N from Mixer | Irvington Station | Monitor | 5 | 250 | 250 | Milpitas
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | C1-V1 | PCE167 | Station | Irvington | CNTL | Mixer from L- 303 | Irvington Station | Monitor | 71 | 476 | 477 | Milpitas
161 | TCQ2 | TP_EBAY | Line_153_246 | 246 psig Line 153 from Marina Station to the Oakland PLS | C2-V1 | PCE328 | Station | Marina Blvd | NGO | L-153 Oakland from L-153 Irvington | Marina Station | Monitor | V18.00 | 246 | 246 | Mission
162 | TCQ2 | TP_EBAY | Line 191-1_268 | Line 191-1 from C Street to Plaza station (pipe continues to Reliez station) | C3-V1 | tcq2PCE806 | LT | C Street Station in Martinez off of SP3 |  | C Street Station | C Street Station, Martinez
163 | TCQ2 | TP_EBAY | DFM_2402_01 | 150 psig Castro Valley DFM | C3-V1 | tcq2PCE804 | DFM | A and Yolo Street, Diagram 0800545 |  | A Street Reg Station, RH-05 | C Street Station
164 | TCQ2 | TP_EBAY | DFM_2403_125 | 125 psig Niles DFM from Decoto to Mowry | C4-V1 | tcq2PCE802 | DFM | Decoto and Niles, Fremont |  | Niles Reg Station, RF38 | Niles Reg Station, RF38
165 | TCQ2 | TP_EBAY | DFM_3001-01_170 | Moraga DFM 3001-01 | C4-V1 | PCE315 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to Moraga DFM/12" L-191 | Reliez Station | Monitor | 32 | 170 | 170 | Diablo/Con.
165 | TCQ2 | TP_EBAY | DFM_3001-01_170 | Moraga DFM 3001-01 | C4-V1 | PCE316 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to Moraga DFM/12" L-191 | Reliez Station | Monitor | 33 | 170 | 170 | Diablo/Con.
166 | TCQ2 | TP_EBAY | DFM_3002_170 | Glorietta DFM | C4-V1 | PCE313 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to 12" L-191 | Reliez Station | Monitor | 28 |  |  | Diablo/Con.
166 | TCQ2 | TP_EBAY | DFM_3002_170 | Glorietta DFM | C4-V1 | PCE314 | Regulator Station | Reliez Station Road | NGO | 16" L-191 to 12" L-192 | Reliez Station | Monitor | 29 |  |  | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE310 | Meter Station | Concord | NGO | Concord from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 9 | 170 | 170 | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE309 | Meter Station | Concord | NGO | Concord from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 8 | 170 | 170 | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE317 | Meter Station | Vine Hill | NGO | Concord/PH from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 10 | 170 | 170 | Diablo/Con.
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | C4-V1 | PCE318 | Meter Station | Vine Hill | NGO | Concord/PH from SP3 | Vine Hill Station, Concord Meter Station | Monitor | 11 | 170 | 170 | Diablo/Con.
168 | TCQ2 | TP_EBAY | DFM_3004-01_338 | Foster Wheeler Cogen DFM | C2-V2B | PCE312 | Meter & Regulator Station | Foster-Wheeler | NGO | FW Cogen from L-3 | Foster Wheeler Meter Station off of SP3 | Monitor | 6 | 320 | 600 | Diablo/Con.
168 | TCQ2 | TP_EBAY | DFM_3004-01_338 | Foster Wheeler Cogen DFM | C2-V2B | PCE311 | Meter & Regulator Station | Foster-Wheeler | NGO | FW Cogen from L-3 | Foster Wheeler Meter Station off of SP4 | Monitor | 5 | 320 | 600 | Diablo/Con.
169 | TCQ2 | TP_EBAY | DFM_3010-01_338 | Antioch Vierra DFM - Can be tied to Line 191_338 psig system | C2-V3 | tcq2PCE809 | DFM | Vierra Sation on Line 191 |  | Vierra Station | Antioch/Vierra Reg station
170 | TCQ2 | TP_EBAY | DFM_3012_172 | Dow Chemical and USS DFM | C2-V1 | tcq2PCE815 | DFM | Dow Chemical Feeder RA11 |  | Dow Chemical Feeder | Pittsburg Town Station
171 | TCQ2 | TP_EBAY | DFM_3014-01_338 | Nichols DFM Tapped off of SP3 | C1-V3 | tcq2PCE810 | DFM | Nichols DFM |  | Nichols DFM | Nichols Reg Station
172 | TCQ2 | TP_EBAY | DFM_3019_275 | Rhodia_DFM | C2-V3 | tcq2PCE816 | DFM | Smith Street at MP 8.48 on Line 153 |  | Rhodia DFM RS | Shell Reg Station DIRC29
173 | TCQ2 | TP_EBAY | Line SP3_405 | Stanpac 3 from Los Medanos PLS to Franklin Canyon PLS | C2-V1 | PCE90 | Pressure Limiting Station | Los Medanos | CNTL | SP3 | Los Medanos PLS - Control Valves | Monitor | 705 | 405 | 468 | Los Medanos
173 | TCQ2 | TP_EBAY | Line SP3_405 | Stanpac 3 from Los Medanos PLS to Franklin Canyon PLS | C2-V1 | PCE91 | Pressure Limiting Station | Los Medanos | CNTL | SP3 | Los Medanos PLS - Control Valves | Monitor | 706 | 405 | 468 | Los Medanos
174 | TCQ2 | TP_EBAY | Line SP3_380 | 380 psig Stanpac 3 from Franklin Canyon to San Pablo Station | C2-V1 | PCE322 | Station | Franklin Canyon | NGO | SP3 | Franklin Canyon PLS | Monitor | 10 | 380 | 380 | East Bay-N
174 | TCQ2 | TP_EBAY | Line SP3_380 | 380 psig Stanpac 3 from Franklin Canyon to San Pablo Station | C2-V1 | PCE321 | Station | Franklin Canyon | NGO | SP3 | Franklin Canyon PLS | Monitor | 8 | 380 | 380 | East Bay-N
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE94 | Meter Station | SP3-Line 191 | CNTL | SP-3 to L-191 | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 11 | 338 | 338 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE84 | Terminal | Antioch | CNTL | SP5 from Antioch Header | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 158 | 338 | 390 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE95 | Meter Station | SP3-Line 191 | CNTL | SP-3 to L-191 | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 12 | 338 | 338 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE96 | Meter Station | SP3-Line 191 | CNTL | SP-3 to L-191 | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 20 | 338 | 338 | Los Medanos
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | C4-V1 | PCE81 | Terminal | Antioch | CNTL | SP5 from Antioch Header | Antioch Terminal and SP3/191 Crosstie (control valves) | Monitor | 175 | 338 | 390 | Los Medanos
176 | TCQ2 | TP_EBAY | DFM_2408-01 | Stanley DFM in Pleasanton | C2-V1 | PCE330 | Meter & Regulator Station | Santa Rita Road | NGO | L-131 to Pleasanton DFM | Isabel Staiton/ Santa Rita Station | Monitor | 4 | 160 | 160 | Mission
176 | TCQ2 | TP_EBAY | DFM_2408-01 | Stanley DFM in Pleasanton | C2-V1 | PCE329 | Meter & Regulator Station | Santa Rita Road | NGO | L-131 to Pleasanton DFM | Bay Area Loop - Control Valves | Monitor | 3 | 160 | 160 | Mission
178 | TCQ2 | TP_EBAY | DFM_2805-05_215 | San Ramon DFM | C2-V1 | tcq2PCE808 | DFM | Isabel Station at Line 131 |  | Isabel Station | Altimrano/Arnold reg station
179 | TCQ2 | TP_EBAY | DFM_2403_240 | 240 psig Isabel DFM 2403-02 and 2403-01 | C1-V2B | tcq2PCE803 | DFM | Smith Street at MP 8.48 on Line 153 |  | Smith Reg Station, RF-41 | Smith Reg Station, RF-41
180 | TCQ2 | TP_EBAY | DFM 0107.02 | 160 psig Coral/Tunis DFM (near Oakland Airport) | C2-V2B | tcq2PCE805 | DFM | Coral and Tunis, San Leandro, Diagram 082483 |  | Coral and Tunis Reg Station EBA-09 | Coral and Tunis Regulator Station
181 | TCQ2 | TP_EBAY | DFM_CCPP | Contra Costa Power Plant DFM | C2-V3 | PCE82 | Terminal | Antioch | CNTL | CCPP from Antioch Header | Antioch Terminal valves 155, 156, 157, 173 | Monitor | 155 | 195 | 195 | Los Medanos
181 | TCQ2 | TP_EBAY | DFM_CCPP | Contra Costa Power Plant DFM | C2-V3 | PCE83 | Terminal | Antioch | CNTL | CCPP from Antioch Header | Antioch Terminal valves 155, 156, 157, 174 | Monitor | 156 | 195 | 195 | Los Medanos
182 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | DRJ4PCE820 | Underground Holder | Oper. Drw - 382860.g06 |  | North Sacramento | Franklin Canyon PLS
182 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | PCE404 | Regulator Station | Lincoln Junction | NGO | L-124 to L-123 | Franklin Canyon PLS | Monitor | 16 | 500 | 500 | Sierra
183 | MUMY | TP_SACRAMENTO_VALLEY | 0605_GALT_395 | Galt Primary Reg Sta (PCE) and Thornton Reg Sta (PCE) to the town of Galt at the inlet to DR R_SCSTA_B07. | C1-V1 | DRJ4PCE803 | Regulator Station | Oper. Drw - 0800439.G06 |  | Thornton | Antioch Terminal and SP3/191 Crosstie (control valves)
184 | MUMY | TP_SACRAMENTO_VALLEY | 0606_ELK_GROVE_150 | Elk Grove Emergency Backfeed Sta (PCE) to the inlet to DR R_SRSTA-B17. This looks to be a backup feed to distribution system, not LT | C2-V1 | DRJ4PCE804 | Regulator Station | Oper. Drw - 089653.g06 |  | Elk Grove - Clarksburg | Antioch Terminal and SP3/191 Crosstie (control valves)
185 | MUMY | TP_SACRAMENTO_VALLEY | 0609_FLORIN_150 | Florin Rd & Munson Way Reg Sta (PCE) to DFM 0609. | C4-V1 | DRJ4PCE808 | Regulator Station | Oper. Drw - 0800152.g06 |  | Florin Rd & Munson Way | Isabel Staiton/ Santa Rita Station
186 | MUMY | TP_SACRAMENTO_VALLEY | 0611_MATHER_240 | 20th Av & Martin Luther King Jr Blvd Reg Sta (PCE) to Blue Ravine Reg Station in Folsom - Mather DFM system serving south Sacramento and Rancho Cordova. The Pmin Design Shown is in Folsom at DR R_SCSTA-51 which receives backfeed support from the Folsom D | C2-V1 | DRJ4PCE809 | Meter & Regulator Station | Oper. Drw - 0800151.g06 |  | 20th Ave & Martin Luther King Jr Blvd | Isabel Staiton/ Santa Rita Station
187 | MUMY | TP_SACRAMENTO_VALLEY | 0613_SAC_FLOATER_260 | Sacramento Gas Load Center (PCE) to North Sacramento Holder and North Sacramento 180 psig DFM. Provides the lead supply to the DFM to a secondary backup supply off of L119B/C. The North Sacramento Holder is operated during winter season morning peak hou | C4-V3 | PCE393 | Gas Load Center | Sacramento | NGO | L-116 to North Sac. DFM | Isabel Staiton/ Santa Rita Station | Monitor | 16 | 260 | 260 | Sacramento
187 | MUMY | TP_SACRAMENTO_VALLEY | 0613_SAC_FLOATER_260 | Sacramento Gas Load Center (PCE) to North Sacramento Holder and North Sacramento 180 psig DFM. Provides the lead supply to the DFM to a secondary backup supply off of L119B/C. The North Sacramento Holder is operated during winter season morning peak hou | C4-V3 | PCE394 | Gas Load Center | Sacramento | NGO | L-116 to North Sac. DFM | Isabel Staiton/ Santa Rita Station | Monitor | 20 | 260 | 260 | Sacramento
188 | MUMY | TP_SACRAMENTO_VALLEY | 0615_SAC_METRO_425 | El Centro Rd & Hwy 80 Reg Sta (PCE) to the Sacramento Metropolitan Airport. | C1-V1 | DRJ4PCE801 | Regulator Station | Oper. Drw - 0800492.g06 |  | El Centro Rd & Hwy 80 | Isabel Staiton/ Santa Rita Station
189 | MUMY | TP_SACRAMENTO_VALLEY | 0617_KIRBY_150 | Roseville Rd Reg Sta (PCE) to the inlet to DR R_SCSTA-A37. | C4-V3 | PCE389 | Regulator Station | Roseville Road | NGO | 12" L-119 to Sacto DFM | Bay Area Loop - Control Valves | Monitor | 66 | 150 | 150 | Sacramento
190 | MUMY | TP_SACRAMENTO_VALLEY | 0618_ANTELOPE_WALERGA_175 | Antelope Meter Sta (PCE) to Antelope at the inlet to DR . | C4-V3 | PCE381 | Meter Station | Antelope | NGO | L-123 to Roseville DFM | Bay Area Loop - Control Valves | Monitor | 25 | 180 | 180 | Sacramento
190 | MUMY | TP_SACRAMENTO_VALLEY | 0618_ANTELOPE_WALERGA_175 | Antelope Meter Sta (PCE) to Antelope at the inlet to DR . | C4-V3 | PCE382 | Meter Station | Antelope | NGO | L-123 to Roseville DFM | Smith Reg Station, RF-41 | Monitor | 27 | 180 | 180 | Sacramento
191 | ANY3 | TP_SACRAMENTO_VALLEY | 0619_SOUTH_RIVER_150 | 0619-01: 150# (South River) Included in distribution model: ESDZONE_SA_WEST_SAC_H_W1112_APD_452_(MOP_MINUS_20_STUDY) | C2-V3 | DRJ4PCE810 | Regulator Station | Oper. Drw - 0800230.g06 |  | S River Rd | Coral and Tunis Regulator Station
192 | ANY3 | TP_SACRAMENTO_VALLEY | 0621_ARMFIELD_190 | 0621-01: 190# (Teichert Modeled) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_CFD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) | C2-V3 | DRJ4PCE811 | Regulator Station | Oper. Drw - 081798.g06 |  | Woodland | Antioch Terminal valves 155, 156, 157, 173
193 | ANY3 | TP_SACRAMENTO_VALLEY | 0627_UCDAVIS_175 | 0627-01: 175# Davis Meter and Reg Sta (PCE) to UC Davis Campus at the inlet to DR R_SCDA-001. (AFTER 1st & A St MWC 47 job) Included in distribution model: ESDZONE_SA_DAVIS_H_W1112_CWD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) | C2-V3 | PCE384 | Meter & Regulator Station | Davis | NGO | L-116 to Davis DFM |  | Monitor | 89 | 175 | 175 | Sacramento
193 | ANY3 | TP_SACRAMENTO_VALLEY | 0627_UCDAVIS_175 | 0627-01: 175# Davis Meter and Reg Sta (PCE) to UC Davis Campus at the inlet to DR R_SCDA-001. (AFTER 1st & A St MWC 47 job) Included in distribution model: ESDZONE_SA_DAVIS_H_W1112_CWD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) | C2-V3 | PCE385 | Meter & Regulator Station | Davis | NGO | L-116 to Davis DFM |  | Monitor | 90 | 175 | 175 | Sacramento
194 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_240 | Lurline Rd Sta (PCE) to closed MAOP sdeparation valve V-5. Serves the town of Colusa and Sunsweet Driers. The Pmin Design shown is in Colusa at the inlet to DR R_SCC008 (55 psig Distr system). Lurline DFM Included in distribution model: 07-J07colusaAS | C2-V2B | DRJ4PCE812 | Regulator Station | Oper. Drw - 0800125.g06 |  | Lurline Road
195 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_430 | Marysville Buttes Sta (PCE) to closed MAOP separation valve V-5. Colusa DFM Included in distribution model: 07-J07colusaASD_UTM_Qrc+20%+Noncore_452_MOP_MINUS_20_STUDY.MDB | C2-V2B | DRJ4PCE813 | Regulator Station | Oper. Drw - 081498.g06 |  | Marysville-Buttes
196 | LRS3 | TP_SACRAMENTO_VALLEY | 0632_WILLIAMS_180 | Williams Primary (PCE) to the town of Williams DR R_FM_SCWL04. Williams DFM Included in distribution model: 11-J11WILLIAMSCFD_UTM_45_MOP_MINUS_20_STUDY | C4-V3 | DRJ4PCE815 | Regulator Station | Oper. Drw - 082870.g06 |  | Williams Town
197 | MUMY | TP_SACRAMENTO_VALLEY | 0635_WALNUT_GROWER_210 | West Beehive Bend Reg Sta (PCE) | V3 | DRJ4PCE824 | Meter & Odorizer Station | Oper. Drw - 183096.g06 |  | West Beehive Bend(DREG)
198 | LRS3 | TP_SACRAMENTO_VALLEY | 124C-1_BEALE_AFB_395 | Camp Far West Meter Sta (PCE) to Beale Air Force Base. Beale DFM Included in distribution model: ESDZONE_08-J08wheatbelAPD_UTM_45_MOP_MINUS_20_STUDY | C1-V3 | PCE403 | Meter Station | Camp Far West | NGO | L-124 to l-124 |  | Monitor | 11 | 395 | 400 | Sierra
198 | LRS3 | TP_SACRAMENTO_VALLEY | 124C-1_BEALE_AFB_395 | Camp Far West Meter Sta (PCE) to Beale Air Force Base. Beale DFM Included in distribution model: ESDZONE_08-J08wheatbelAPD_UTM_45_MOP_MINUS_20_STUDY | C1-V3 | PCE402 | Meter Station | Camp Far West | NGO | L-124 to l-124 |  | Monitor | 7 | 395 | 400 | Sierra
199 | LRS3 | TP_SACRAMENTO_VALLEY | 1502_DIST10_120 | Magnolia Rd Sta (PCE) to DFM 1502. District 10 DFM north of Magnolia Rd Reg Station Included in distribution model: 10-J10mryASD_UTM_45_MOP_MINUS_20_STUDY | C4-V2B | DRJ4PCE817 | Regulator Station | Oper. Drw - 0800099.g06 |  | Hwy 70 & Magnolia Rd
200 | LRS3 | TP_SACRAMENTO_VALLEY | 1504_NICOLAUS_274 | Lincoln Jct (PCE) to the town of Lincoln DR R_SRSTA-602 and R_SRSTA-603. Lincoln DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C1-V1 | PCE406 | Regulator Station | Lincoln Junction | NGO | L-124 to Lincoln DFM |  | Monitor | 22 | 274 | 274 | Sierra
200 | LRS3 | TP_SACRAMENTO_VALLEY | 1504_NICOLAUS_274 | Lincoln Jct (PCE) to the town of Lincoln DR R_SRSTA-602 and R_SRSTA-603. Lincoln DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C1-V1 | PCE405 | Regulator Station | Lincoln Junction | NGO | L-124 to Lincoln DFM |  | Monitor | 21 | 274 | 274 | Sierra
201 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L124B_1502_400 | Yuba City Holder (PCE) to Lincoln Jct - 400 psig system serving Marysville and subsystem 1504_NICOLAUS_274. The Pmin Design shown is in Lincoln at the inlet to Lincoln Jct. | C4-V1 | DRJ4PCE806 | Underground Holder | Oper. Drw - 284091.g06 |  | Yuba City
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley | C1-V1 | PCE370 | Station | Gridley Junction | NGO | L-167 to L-50 |  | Monitor | 13 | 250 | 250 | North Valley
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley | C1-V1 | PCE371 | Station | Gridley Junction | NGO | L-167 to L-50 |  | Monitor | 17 | 250 | 250 | North Valley
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley | C1-V1 | PCE376 | Meter Station | Richvale "Y" | NGO | L-50 (S) from L-50 (N) |  | Monitor | 38 | 250 | 250 | North Valley
203 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVN_412 | Las Vinas Sta (PCE) to BTU MLV 66.14. Serves South Sacramento. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B39 and DR R_SCSTA-B37. | C2-V1 | PCE61 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 75 | 400 | 412 | Rio Vista
203 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVN_412 | Las Vinas Sta (PCE) to BTU MLV 66.14. Serves South Sacramento. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B39 and DR R_SCSTA-B37. | C2-V1 | PCE62 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 76 | 400 | 412 | Rio Vista
204 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVS_412 | Las Vinas Sta (PCE) to 8-mile Rd PLS (PCE). Supplies Turner Rd Sta and NCPA-Lodi. The Pmin Design shown is at Armstrong Rd at the inlet to DR R_LOHP77. | C2-V1 | PCE61 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 75 | 400 | 412 | Rio Vista
204 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVS_412 | Las Vinas Sta (PCE) to 8-mile Rd PLS (PCE). Supplies Turner Rd Sta and NCPA-Lodi. The Pmin Design shown is at Armstrong Rd at the inlet to DR R_LOHP77. | C2-V1 | PCE62 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 76 | 400 | 412 | Rio Vista
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- | C1-V1 | PCE397 | Gas Load Center | Sacramento | NGO | L-172 to L-108 |  | Monitor | 7 | 412 | 412 | Sacramento
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- | C1-V1 | PCE395 | Gas Load Center | Sacramento | NGO | L-172 to L-108 |  | Monitor | 3 | 412 | 412 | Sacramento
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- | C1-V1 | PCE396 | Gas Load Center | Sacramento | NGO | L-172 to L-108 |  | Monitor | 5 | 412 | 412 | Sacramento
206 | MUMY | TP_SACRAMENTO_VALLEY | L116_L119A_720 | Swingel Jct (PCE) to Sacramento Gas Load Center and North Sacramento Holder. Supplies North Natomas area, North Sacramento and subsystems L119B_L119C_0617_FOLSOM_500, 0613_SAC_FLOATER_260, L119D_0614_NSAC_180, and 0615_SAC_METRO_425. The Pmin Design show | C1-V1 | PCE398 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/119 |  | Monitor | 21 | 533 | 720 | Sacramento
206 | MUMY | TP_SACRAMENTO_VALLEY | L116_L119A_720 | Swingel Jct (PCE) to Sacramento Gas Load Center and North Sacramento Holder. Supplies North Natomas area, North Sacramento and subsystems L119B_L119C_0617_FOLSOM_500, 0613_SAC_FLOATER_260, L119D_0614_NSAC_180, and 0615_SAC_METRO_425. The Pmin Design show | C1-V1 | PCE399 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/119 |  | Monitor | 29 | 533 | 720 | Sacramento
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. | C4-V3 | PCE409 | Underground Holder | North Sacramento | NGO | Sacto Load Center to Sacto DFM |  | Monitor | 167 | 180 | 180 | Sierra
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. | C4-V3 | PCE408 | Underground Holder | North Sacramento | NGO | Sacto Load Center to Sacto DFM |  | Monitor | 137 | 180 | 180 | Sierra
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. | C4-V3 | PCE407 | Underground Holder | North Sacramento | NGO | Sacto Load Center to Sacto DFM |  | Monitor | 93 | 180 | 180 | Sierra
208 | MUMY | TP_SACRAMENTO_VALLEY | L121_485 | Marysville Buttes Sta (PCE) to Yuba City Holder Sta (PCE). Yuba City Holder Sta provides backup supply into L121 at 420 psig when the Yuba City Cogen comes on-line to maintain an elevated delivery service pressure of 375 psig at the meter. | C2-V3 | DRJ4PCE814 | Meter & Regulator Station | Oper. Drw - 081498.g06 |  | Marysville-Buttes
209 | MUMY | TP_SACRAMENTO_VALLEY | L123_L173_500, L119B_L119C_0617_FOLSOM_500 | Lincoln Junction (PCE) to North Sacramento Underground Holder (PCE) 500 psig system serving Auburn and El Dorado Hills. These two subsystems have the same MAOP and operate as a single system under Design Day conditions across L123 Open BTU MLV 3.42 at Ba | C4-V1 | DRJ4PCE820 | Underground Holder | Oper. Drw - 382860.g06 |  | North Sacramento
209 | MUMY | TP_SACRAMENTO_VALLEY | L123_L173_500, L119B_L119C_0617_FOLSOM_500 | Lincoln Junction (PCE) to North Sacramento Underground Holder (PCE) 500 psig system serving Auburn and El Dorado Hills. These two subsystems have the same MAOP and operate as a single system under Design Day conditions across L123 Open BTU MLV 3.42 at Ba | C4-V1 | PCE404 | Regulator Station | Lincoln Junction | NGO | L-124 to L-123 |  | Monitor | 16 | 500 | 500 | Sierra
210 | MUMY | TP_SACRAMENTO_VALLEY | L124A_L202_1511_600 | Yuba City Holder (PCE) to Lincoln Jct - 600 psig system serving Grass Valley and subsystem L123_L173_500. The Pmin design shown is in Grass Valley at DR R_SRSTA-112. | C4-V1 | PCE413 | Underground Holder | Yuba City | NGO | L-167 to L-124 |  | Monitor | 53 | 600 | 600 | Sierra
211 | MUMY | TP_SACRAMENTO_VALLEY | L150_0626_0600_125 | Pleasant Creek Line 159 Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D13. | C4-V3 | PCE379 | Regulator Station | Pleasant Creek Line 159 | NGO | L-159 to L-159 |  | Monitor | 5 | 125 | 750 | Sacramento
211 | MUMY | TP_SACRAMENTO_VALLEY | L150_0626_0600_125 | Pleasant Creek Line 159 Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D13. | C4-V3 | PCE380 | Regulator Station | Pleasant Creek Line 159 | NGO | L-159 to L-160 |  | Monitor | 9 | 125 | 750 | Sacramento
212 | MUMY | TP_SACRAMENTO_VALLEY | L172A_500 | Swingle Jct (PCE) to Sacramento Gas Load Center. Supplies West Sacramento and subsystem L108_SGLC_412. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609-02. | C2-V1 | PCE401 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/172 |  | Monitor | 53 | 500 | 520 | Sacramento
212 | MUMY | TP_SACRAMENTO_VALLEY | L172A_500 | Swingle Jct (PCE) to Sacramento Gas Load Center. Supplies West Sacramento and subsystem L108_SGLC_412. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609-02. | C2-V1 | PCE400 | Meter & Regulator Station | Swingle Junction | NGO | L-172 to L-116/172 |  | Monitor | 52 | 500 | 520 | Sacramento
213 | MUMY | TP_SACRAMENTO_VALLEY | L172A_N_L169_L167_800 | Hershey Jct North (PCE) to Fell Station and Yuba City Holder. Receives withdrawal gas from Wild Goose Storage Field (PCE) and local California Production in the Willows Field area. The Pmin Design shown is in Grass Valley at the inlet to DR R_SRSTA-112 | C4-V1 | PCE51 | Junction | Hershey | NGO | L-172 from L-302 |  | Monitor | 2 | 800 | 800 | Willows
213 | MUMY | TP_SACRAMENTO_VALLEY | L172A_N_L169_L167_800 | Hershey Jct North (PCE) to Fell Station and Yuba City Holder. Receives withdrawal gas from Wild Goose Storage Field (PCE) and local California Production in the Willows Field area. The Pmin Design shown is in Grass Valley at the inlet to DR R_SRSTA-112 | C4-V1 | PCE54 | Storage Interconnect | Wild Goose Gridley | NGO | Storage metering run |  | Monitor | 6 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE52 | Junction | Hershey | NGO | L-172 from L-302 |  | Monitor | 3 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE44 | Pressure Limiting Station | Yolo Station | NGO | L-172 from L-406 |  | Monitor | 5 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE45 | Pressure Limiting Station | Yolo Station | NGO | L-172 from L-406 |  | Monitor | 11 | 800 | 800 | Willows
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. | C4-V1 | PCE43 | Pressure Limiting Station | Yolo Station | NGO | L-172 from L-406 |  | Monitor | 2 | 800 | 800 | Willows
215 | MUMY | TP_SACRAMENTO_VALLEY | L195_L196_L200_L210B_800 | Creed Sta (PCE) to Las Vinas Sta. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B37 and DR R_SCSTA-B05. | C2-V1 | PCE56 | Station | Creed | NGO | L-210 E from L400/L401 |  | Monitor | 11 | 686 | 800 | Rio Vista
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr | C2-V2A | PCE61 | Station | Las Vinas | NGO | L-108S from L-196A/B |  | Monitor | 75 | 400 | 412 | Rio Vista
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr | C2-V2A | PCE64 | Station | Las Vinas | NGO | L-197A/B from L-108S |  | Monitor | 96 | 300 | 300 | Rio Vista
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr | C2-V2A | DRJ4PCE800 | Regulator Station | Oper. Drw - 081929.g06 |  | Turner Rd
217 | MUMY | TP_SACRAMENTO_VALLEY | L220_500 | Lines 172 & 220 Crosstie (PCE) to Davis Meter and Reg Sta | C1-V1 | PCE387 | Crosstie | Line 172/220 | NGO | L-172 to L-221 |  | Monitor | 6 | 500 | 500 | Sacramento
217 | MUMY | TP_SACRAMENTO_VALLEY | L220_500 | Lines 172 & 220 Crosstie (PCE) to Davis Meter and Reg Sta | C1-V1 | PCE386 | Crosstie | Line 172/220 | NGO | L-172 to L-220 |  | Monitor | 5 | 500 | 500 | Sacramento
218 | LRS3 | TP_SACRAMENTO_VALLEY | South Sutter Co Reg Sta (PCE) to DR R_FM_B-85. South Sutter DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY | South Sutter DFM | C4-V2B | DRJ4PCE816 | Regulator Station | Oper. Drw - 087571.g06 |  | So Sutter Co
219 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | District 10 DFM between L-50 tap & Magnolia Rd (no source Reg) Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | PCE404 | Regulator Station | Lincoln Junction | NGO | L-124 to L-123 |  | Monitor | 16 | 500 | 500 | Sierra
219 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | District 10 DFM between L-50 tap & Magnolia Rd (no source Reg) Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY | C2-V2B | DRJ4PCE820 | Underground Holder | Oper. Drw - 382860.g06 |  | North Sacramento
220 | ANY3 | TP_SACRAMENTO_VALLEY | 0600_DIXON_158 | Dixon Reg Sta (PCE) to Dixon at the inlet to DR R_FM_R-22. 0600-05: 158# Included in distribution model:ESDZONE_SA_DIXON_H_W1112_APD_452_(MOP_MINUS_20_STUDY) | C2-V1 | DRJ4PCE805 | Regulator Station | Oper. Drw - 081529.g06 |  | Dixon
221 | LRS3 | TP_SACRAMENTO_VALLEY | 0634_COLUSA_GLENN_DRIER_600 | Maxwell Primary Reg Sta (PCE) to Maxwell and Comet Rice Drier. Included in distribution model: -BASE_08-J07maxwellAPD_UTM_452_MOP_MINUS_STUDY.MDB | C1-V2B | DRJ4PCE823 | Regulator Station | Oper. Drw - 0800496.g06 |  | Maxwell Primary
222 | LRS3 | TP_SACRAMENTO_VALLEY | 0643_ARBUCKLE_150 | Arbuckle DFM Included in distribution model: BASE-07-J07ArbuckleAPD_UTM_452_MOP_MINUS_20_STUDY.MDB | C4-V1 | PCE48 | Station | Arbuckle | NGO | Arbuckle DFM from Intermediate |  | Relief | H | 150 | 150 | Meridian
222 | LRS3 | TP_SACRAMENTO_VALLEY | 0643_ARBUCKLE_150 | Arbuckle DFM Included in distribution model: BASE-07-J07ArbuckleAPD_UTM_452_MOP_MINUS_20_STUDY.MDB | C4-V1 | PCE47 | Station | Arbuckle | NGO | Arbuckle DFM from Intermediate |  | Relief | F | 150 | 150 | Meridian
223 | LRS3 | TP_SACRAMENTO_VALLEY | 1514_TOWNSHIP_150 | North Township DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY | C2-V3 | DRJ4PCE818 | Regulator Station | Oper. Drw - 0800098.g06 |  | Almendra & Township Rds
224 | ANY3 | TP_SACRAMENTO_VALLEY | L116_L150_200 | L-150/L-116: 200# Davis Meter and Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D08. -included in distribution model: ESDZONE_SA_DAVIS_H_W1112_APD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) | C2-V3 | PCE383 | Meter & Regulator Station | Davis | NGO | L-150 to L-116 |  | Monitor | 105 | 200 | 500 | Sacramento
225 | ANY3 | TP_SACRAMENTO_VALLEY | L158_L220_500 | D. Q. Scott Reg Sta (PCE) to Clark Pacific Concrete Plant. L-158/L-220 (Woodland?) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_APD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) | C1-V1 | DRJ4PCE821 | Regulator Station | Oper. Drw - 087220.g06 |  | D.q. Scott

## MOP -20 Results (hidden)
HIS_ID | Plng Engr | Planning Model | HIS Name | HIS Description | Regulator Station Name | Est. Footage (Miles) | Pipeline Section(s) | Pressure Control Equipment | Validation Status | MOP (psig) | MOP Remarks | NOP (psig) | NOP as Modeled | Pmin Design (psig) | CWD110%Res Pmin (psig) | APD110%Res Pmin (psig) | Analysis Results | New CWD110%Res Pmin (psig) | New APD110%Res Pmin (psig) | Investment Description | Investment Cost ($) | Analysis Notes | Result | PSEP PR Pipe EXIST? | Cust. Impacts | MOP | P min | CDW Pmin | APD P min | CWD ΔP ² | APD ΔP ²
1 | MJA3 | TP_NORTH_BAY | Benica_175 | Benicia DFM | Glenn Cove & Benicia Rd Reg OD 800103 V-3, 4, 5, 6; Vallejo Station OD 086452 V-33, 34, 35, 36 | 7.5 | MJA3PS700 | PCE340, PCE341 | V1-Meets Plng Guide validation criteria | 175 | PCE340,PCE341 valve numbers to do match V-3 and V-4 on operating diagram 0800103 | 170 | 165 | 90 | 140 | 117 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 122 | 96 | Rebuild V18 at Southhampton Rd & Highway 80 in Benicia | $500,000 | No noncore customers | C4-V1 | Y |  | 175 | 90 | 140 | 117 | 48.9456 | 75.1876
2 | MJA3 | TP_NORTH_BAY | Benicia_Ind_Park_175 | Benicia Industrial Park | E. 2nd St & Resvr Rd OD0800104 V-3, 4, 5, 6 | 1.9 | MJA3PS701 | MJA3PCE800 | V1-Meets Plng Guide validation criteria | 175 |  | 168 | 165 | 90 | 149 | 161 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 134 | 147 | Rebuild V38 at Industrial Way & E Channel Rd in Benicia Industrial Park | $500,000 | This analysis includes 100% stage 2 curtailment of Valero Refining (C428) | C4-V1 | Y |  | 175 | 90 | 149 | 161 | 37.3984 | 20.8835
3 | MJA3 | TP_NORTH_BAY | Calistoga_150 | Calistoga DFM serving Calistoga & Angwin | York Creek Reg OD0800390 V-3, 4, 5, 6 | 11.2 | MJA3PS702 | MJA3PCE801 | V1-Meets Plng Guide validation criteria | 150 |  | 146 | 144 | 90 | 117 | 102 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 98 | 80 | Parallel 3,200' 6" with 8" on Highway 29, north of Angwin tap | $2,061,000 | This analysis includes 100% stage 2 curtailment of Pacific Union College (4433 & C406) and St Helena Hospital (C405) | C3-V1 | Y | Y | 150 | 90 | 117 | 102 | 61.1875 | 84
4 | MJA3 | TP_NORTH_BAY | Calistoga_250 | Calistoga 250# DFM | Hwy 29 & Zinfandel OD0800126, V-3, 4, 5, 6 | 4 | PS623, MJA3PS721 | MJA3PCE802 | V1-Meets Plng Guide validation criteria | 250 |  | 246 | 243 | 158 | 230 | 226 | C2-NOP can be lowered to MOP-20 now | 212 | 208 | N/A | N/A | This analysis includes 100% stage 2 curtailments of three customers from the Calistoga_150 subsystem | C2-V1 | Y | Y | 250 | 158 | 230 | 226 | 25.5754 | 30.4348
5 | MJA3 | TP_NORTH_BAY | Cotati_150 | Cotati DFM | Hwy 101 & Old Redwood Hwy OD0800129 V-19, 20, 21, 22; Cotati Reg OD081596 V-4, 5 | 9.5 | PS626, MJA3PS703 | PCE364, PCE365, MJA3PCE803 | V3-Insufficient P data to complete validation | 150 |  | 147 | 145 | 90 | 137 | 131 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 117 | 110 | Rebuild R477 at Penngrove Pitt in Penngrove | $500,000 | This analysis includes 100% stage 2 curtailment of Sonoma State University (C519). Do not lower pressure until pressure data is available to validate model! | C4-V3 | Y |  | 150 | 90 | 137 | 131 | 25.9097 | 37.0764
6 | MJA3 | TP_NORTH_BAY | Fairfield_230 | Fairfield DFM to Tabor & Dover | Suisun-Fairfield Reg OD081528 V-56, 57, 58, 59 | 2.8 | MJA3PS704 | MJA3PCE804 | V1-Meets Plng Guide validation criteria | 230 |  | 220 | 220 | 90 | 184 | 153 | C2-NOP can be lowered to MOP-20 now | 173 | 139 | N/A | N/A | This analysis includes 100% stage 2 curtailment of City of Fairfield Cogen (9178) and County of Solano (9190) | C2-V1 |  | Y | 230 | 90 | 184 | 153 | 42.5089 | 65.8281
7 | MJA3 | TP_NORTH_BAY | Fulton_150 | Fulton & Grant Rd DFM to Wikiup and Healdsburg | Grant School Rd Reg OD082460 V-8, 9, 10, 11 ; Fulton Reg OD0800190 V-13, 14, 15, 16 | 11.6 | MJA3PS705 | MJA3PCE807, MJA3PCE808 | V1-Meets Plng Guide validation criteria | 150 |  | 147 | 143 | 90 | 126 | 110 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 107 | 87 | Parallel 1,130' 3" with 6" on River Rd, east of Fulton Rd, rebuild R108 and R122 at Windsor Rd & Airport Blvd in Santa Rosa | $1,756,900 | This analysis includes 100% stage 2 curtailment of The Airport Club (4581) and Syar Industries(C508 & C509) | C4-V1 |  |  | 150 | 90 | 126 | 110 | 46 | 72.2222
8 | MJA3 | TP_NORTH_BAY | Fairfield_400 | Fairfield DFM to Travis AFB and Vacaville Prison | Vacaville Regulator Station OD081527 V-R1, R2, R3, R4 | 8 | PS609, MJA3PS722 | MJA3PCE806 | V1-Meets Plng Guide validation criteria | 400 |  | 380 | 377 | 90 | 371 | 374 | C1-Existing NOP offset is 20 psi or more | 371 | 374 | N/A | N/A | This analysis includes 100% stage 2 curtailment of Ball Corporation (9177), Calif State Prison (9183), Travis AFB (F134), and American National (F159) | C1-V1 |  |  | 400 | 90 | 371 | 374 | 14.7196 | 13.2482
9 | MJA3 | TP_NORTH_BAY | Fairfield_275 | Fairfield DFM to Rancho Solano | Cordelia & Chadbourne Reg OD0800494 V-4, 5, 8, 9 | 5 | MJA3PS706 | MJA3PCE805 | V3-Insufficient P data to complete validation | 275 |  | 240 | 237 | 90 | 216 | 205 | C1-Existing NOP offset is 20 psi or more | 233 | 222 | N/A | N/A | This analysis includes 100% stage 2 curtailment of 4 customers (9189, 9193, F160, F288). Do not lower pressure until pressure data is available to validate model! | C1-V3 |  |  | 275 | 90 | 216 | 205 | 42.9011 | 49.7593
10 | MJA3 | TP_NORTH_BAY | Hiddenbrook_175 | Hiddenbrook DFM to Sky Valley | Sky Valley OD0800479 V-3, 4, 5, 6 | 2.7 | MJA3PS707 | MJA3PCE809 | V1-Meets Plng Guide validation criteria | 175 |  | 145 | 140 | 90 | 133 | 128 | C1-Existing NOP offset is 20 psi or more | 133 | 128 | N/A | N/A | No noncore customers | C1-V1 |  |  | 175 | 90 | 133 | 128 | 57.4295 | 63.2231
11 | MJA3 | TP_NORTH_BAY | Mare_Island_100 | Mare Island DFM | Pine & Woodrow Ave OD0800157 V-5, 6, 7, 8 | 3.6 | MJA3PS708 | MJA3PCE810 | V1-Meets Plng Guide validation criteria | 100 |  | 95 | 92 | 90 | 89 | 88 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 104 | 72 | Install 3.5 miles 8" DFM to float off Vallejo 250# DFM. Rebuild of 6 reg stations | $9,202,200 | Installation of new main ($7,252,200) will allow for floating off L21H and removal of reg station at Pine & Woodrow. Also includes rebuilds of 6 reg stations ($1,950,000) | C4-V1 | Y |  | 100 | 90 | 89 | 88 | 109.4211 | 118.7368
12 | MJA3 | TP_NORTH_BAY | Marin_175 | Marin DFM | San Rafael Meter & Reg OD183804 V-6, 7, 8, 9, 15, 16, 17, 18 | 20.4 | PS625, MJA3PS709 | PCE338, PCE339 | V1-Meets Plng Guide validation criteria | 175 |  | 168 | 168 | 90 | 148 | 134 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 131 | 115 | Rebuild A39 at Meadowsweet & Conow in Corte Madera. Utilization at 84% for MOP-10 | $500,000 | This analysis includes 100% stage 2 curtailment of 5 customers including San Quentin Prison (4120, C104, C105, C110, C114) | C3-V1 | Y | Y | 175 | 90 | 148 | 134 | 38.717 | 56.2442
13 | MJA3 | TP_NORTH_BAY | Marine_World_125 | Marine World DFM | Hwy 80 & Coach Lane 0800102 V-1 | 0.4 | MJA3PS710 | MJA3PCE811 | V2B-Incomplete validation - results suspect | 125 | Questionable whether MOP is 125 or 250#. Requested PLE to research 3/28/12 | 125 | 125 | 90 | 124 | 124 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 104 | 103 | Rebuild V47 at Coach Ln & Fairgrounds Dr in Vallejo. Utilization at 75% for MOP-10 | $500,000 | No noncore customers. Do not lower pressure until pressure data is available to validate model! | C3-V2B |  |  | 125 | 90 | 124 | 124 | 3.309 | 3.309
14 | MJA3 | TP_NORTH_BAY | Napa_Valley_150 | Napa Valley 150# DFM | Solano Ave Reg OD0800130 V-3, 4, 5, 6 | 10.9 | MJA3PS711 | MJA3PCE812 | V2B-Incomplete validation - results suspect | 150 |  | 148 | 145 | 90 | 139 | 139 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 121 | 121 | RebuildL31 at West Park & Solano in Napa for MOP-20. Utilization at 89% for MOP-10 | $500,000 | This analysis includes 100% stage 2 curtailment of the Veterans Home (C412). Do not lower pressure until pressure data is available to validate model! | C3-V2B | Y |  | 150 | 90 | 139 | 139 | 22.0764 | 22.0764
15 | MJA3 | TP_NORTH_BAY | North_Bay_450 | North Bay 450, Napa Y to Calistoga, Marin, and Santa Rosa | Napa Y OD385170 V-5, 11, 25.98, 60 | 154.5 | PS4, PS5, PS6, PS7, PS8, PS9, PS11, PS12, PS621, PS622, PS624, PS627, PS628, MJA3PS712 | PCE333, PCE334 | V1-Meets Plng Guide validation criteria | 450 | Set point remotely controlled by SF operators | 445 | 445 | 160 | 269 | 199 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 244 | 156 | Rebuild R130 at Piner Rd in Santa Rosa and R597 at Temelec in Sonoma for MOP-20. | $1,000,000 | This analysis includes 100% stage 2 curtailment of 9 customers (4432, C111, 4566, 4578, 4579, 4580, C514, C534, C558) & 22 customers from d/s subsystems | C4-V1 | Y |  | 450 | 160 | 269 | 199 | 73.5664 | 92.0854
16 | MJA3 | TP_NORTH_BAY | North_Bay_610 | North Bay 610, Santa Rosa Compressor to Willits | Santa Rosa Compressor OD082485 | 86.8 | PS10, MJA3PS723 | PCE354, PCE355 | V1-Meets Plng Guide validation criteria | 610 | Current MOP limited to 610 until potential of long seam threats are eliminated. Should be resolved after latest L21E Hopland to Ukiah pig run results are reviewed | 600 | 600 | 160 | 269 | 199 | C2-NOP can be lowered to MOP-20 now | 244 | 156 | N/A | N/A | This analysis includes 100% stage 2 curtailment of 3 customers (4576, C305, and 4571) | C2-V1 | Y | Y | 610 | 160 | 269 | 199 | 86.5048 | 95.9593
17 | MJA3 | TP_NORTH_BAY | North_Bay_650 | North Bay 650, Creed to Napa "Y" and Herrmann Station | Creed Station OD182416 V-7, 8, 10, 14, 16, 17 | 74.2 | PS233, PS234, PS236, PS237, PS238, PS603, PS604, PS605, MJA3PS724 | PCE57, PCE58 | V1-Meets Plng Guide validation criteria | 650 | Set point remotely controlled by SF operators | 645 | 645 | 430 | 453 | 454 | C2-NOP can be lowered to MOP-20 now | 431 | 421 | N/A | N/A | Curtailment of Crocket Cogen and 3 major refineries (Valero, Chevron, Conoco-Philips). This analysis includes 100% stage 2 curtailment of 8 customers (C413, C427, 9169, 9171, 9173, 9174, 9179, 9180), 56 customers from d/s subsystems & 3 customers across | C2-V1 | Y | Y | 650 | 430 | 453 | 454 | 91.4524 | 91.0707
18 | MJA3 | TP_NORTH_BAY | Novato_150 | Novato DFM, Novato Blvd and Diabl to Novato Blvd & Reservoir Rd | Diablo Ave & S. Novato Blvd OD0800128 V-5, 6, 7, 8 | 1.2 | MJA3PS713 | MJA3PCE813 | V3-Insufficient P data to complete validation | 150 |  | 144 | 144 | 90 | 137 | 131 | C2-NOP can be lowered to MOP-20 now | 122 | 116 | N/A | N/A | No noncore customers. Do not lower pressure until pressure data is available to validate model! | C2-V3 |  |  | 150 | 90 | 137 | 131 | 25.9097 | 37.0764
19 | MJA3 | TP_NORTH_BAY | Pine_St_150 | Pine St 150# DFM, Pine St Napa Meter Station to Browns Valley | Pine St Reg OD081513 V-13, 24, E | 1.5 | MJA3PS714 | MJA3PCE814 | V3-Insufficient P data to complete validation | 150 |  | 149 | 147 | 90 | 145 | 143 | C2-NOP can be lowered to MOP-20 now | 125 | 123 | N/A | N/A | No noncore customers. Do not lower pressure until pressure data is available to validate model! | C2-V3 | Y |  | 150 | 90 | 145 | 143 | 10.2431 | 14.2431
20 | MJA3 | TP_NORTH_BAY | Schellville_150 | Schellville DFM, Schellville Reg Station to 5th St West & MacArthur | Shellville Reg 081514 V-10, 11, 12, 13 | 3.9 | MJA3PS715 | MJA3PCE815 | V1-Meets Plng Guide validation criteria | 150 |  | 147 | 145 | 90 | 134 | 125 | C2-NOP can be lowered to MOP-20 now | 115 | 106 | N/A | N/A | No noncore customers | C2-V1 |  |  | 150 | 90 | 134 | 125 | 31.5556 | 47.7431
21 | MJA3 | TP_NORTH_BAY | Sebastopol_150 | Sebastopol 150# DFM, Stone Station Reg to Graton | Stone Reg Station OD0800563 V-4, 5, 6, 7 | 9.9 | MJA3PS716 | MJA3PCE816 | V1-Meets Plng Guide validation criteria | 150 |  | 146 | 146 | 90 | 129 | 117 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 111 | 97 | Rebuild R387 at Graton and R405 at Occidental/Peachland in Sebastopol for MOP-20. | $1,000,000 | No noncore customers | C4-V1 | Y |  | 150 | 90 | 129 | 117 | 40.6875 | 61.1875
22 | MJA3 | TP_NORTH_BAY | Sebastopol_275 | Sebastopol 275# DFM, Madrone Station to Stone Station | Madrone Ave Reg OD082329 V-23, 24, 27, 28 | 5.2 | MJA3PS717 | MJA3PCE817 | V1-Meets Plng Guide validation criteria | 275 |  | 270 | 265 | 160 | 248 | 236 | C2-NOP can be lowered to MOP-20 now | 232 | 213 | N/A | N/A | This analysis includes 100% stage 2 curtailment of City of Sebastopol (C552) | C2-V1 | Y |  | 275 | 160 | 248 | 236 | 28.2279 | 39.8381
23 | MJA3 | TP_NORTH_BAY | Sonoma_200 | Sonoma DFM, Monroe Station to Mountain View Reg and 5th St West & MacArthur to Oakmont | Monroe Reg OD081915 V-18, 19, 20, 21; 5th St West & Macarthur Reg OD0800211 V-6, 7 | 37.9 | PS629 | PCE366, PCE367, MJA3PCE818 | V1-Meets Plng Guide validation criteria | 200 |  | 196 | 196 | 90 | 160 | 136 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 140 | 113 | Rebuild R330 at Bennett Valley in Santa Rosa, R639 at Academy Ln in Sonoma, R672 at Sunnyside Ave in Sonoma, and R729 at Oakmont in Santa Rosa for MOP-20. | $2,000,000 | This analysis includes 100% stage 2 curtailment of 9 customers including Memorial Hospital & Santa Rosa Jr College (4585, 4586, C512, C516, C521, C527, C528, C530, C550) | C4-V1 |  |  | 200 | 90 | 160 | 136 | 45.1411 | 67.4107
24 | MJA3 | TP_NORTH_BAY | Soscol_150 | Soscol DFM, Napa Y to Soscol & Souza (R42) | Napa Y OD385170 V-70, 71, 76, 79, Kaiser Rd Reg OD0800127 V-3, 4, 5, 6 | 7.3 | MJA3PS718 | PCE336,PCE337,MJA3PCE819 | V1-Meets Plng Guide validation criteria | 150 |  | 145 | 144 | 90 | 117 | 121 | C2-NOP can be lowered to MOP-20 now | 96 | 101 | N/A | N/A | This analysis includes 100% stage 2 curtailment of Napa State Hospital (C409 & C 418), Napa Jr College (C117), and Syar Industies (C414) | C2-V1 | Y | Y | 150 | 90 | 117 | 121 | 61.1875 | 54.5764
25 | MJA3 | TP_NORTH_BAY | Trancas_250 | Trancas DFM, Napa | Coffield Reg OD0800210 V-3, 4, 5, 6 | 6.1 | MJA3PS719 | MJA3PCE820 | V1-Meets Plng Guide validation criteria | 250 |  | 247 | 240 | 90 | 202 | 172 | C2-NOP can be lowered to MOP-20 now | 181 | 148 | N/A | N/A | This analysis includes 100% stage 2 curtailment of Queen of the Valley Hospital (C419) | C2-V1 |  |  | 250 | 90 | 202 | 172 | 39.8824 | 60.5074
26 | MJA3 | TP_NORTH_BAY | Vallejo_250 | Vallejo DFM, Herrmann Station to Napa "Y" | Napa Y OD385170 V-9, 10; Hermann Station 082454 V-2, 9 | 13.1 | PS15, PS16, PS17, MJA3PS720 | PCE332,PCE335 | V1-Meets Plng Guide validation criteria | 250 |  | 235 | 233 | 90 | 226 | 221 | C2-NOP can be lowered to MOP-20 now | 223 | 218 | N/A | N/A | This analysis includes 100% stage 2 curtailments of four customers from the Mare_Island_100 subsystem (4430, 4437, C116, C426) | C2-V1 |  |  | 250 | 90 | 226 | 221 | 21 | 25.1085
27 | MJA3 | TP_VACAVILLE | Vacaville_400 | Vacaville 400 DFM supplied from Hawkins & Lewis Primary Reg Station | Hawkins & Lewis Primary Reg Station OD0800154 V-R1, R2, R3, R4 | 13.5 | PS600, PS602, PS607, MJA3PS725 | MJA3PCE821 | V1-Meets Plng Guide validation criteria | 400 |  | 390 | 390 | 90 | 233 | 142 | C2-NOP can be lowered to MOP-20 now | 216 | 113 | N/A | N/A | This analysis includes 100% stage 2 curtailments of four customers (9343, 9342, F130, F131). Consideration should be given towards replacing 1000' of 3/2" to low pressure point that is very sensitive to load and has a 120# pressure drop | C2-V1 | Y | Y | 400 | 90 | 233 | 142 | 69.5925 | 92.0579
28 | MJA3 | TP_VACAVILLE | Vacaville_450 | Vacaville 450 DFM supplied from Vaca Dixon Primary Reg Station | Vaca Dixon Primary Reg OD0800153 V- 4, 5, 8, 9 | 3.7 | PS598,MJA3PS726 | MJA3PCE822 | V1-Meets Plng Guide validation criteria | 450 |  | 370 | 370 | 90 | 300 | 288 | C1-Existing NOP offset is 20 psi or more | 300 | 288 | N/A | N/A | This analysis includes 100% stage 2 curtailments of four customers (9361, 9360, 9362, F164) | C1-V1 | Y |  | 450 | 90 | 300 | 288 | 57.8704 | 61.5
29 | NAH1 | TP_PENINSULA | RAYCHEM DFM | DCUST 5760, EQ000032, 1M1559 to RINGB84 | Van Buren Dr & Ringwood Ave Station, B-84 | 1.18 | PS372 | nah1PCE800 | V3-Insufficient P data to complete validation | 175 | From 089868, feeds into 120 psig Middlefield Ringwood DFM | 170 | 170 | 120 | 154.3 | 140.4 | C2-NOP can be lowered to MOP-20 now | 137.5 | 122.1 |  |  | SRI is elevated pressure customer which may be affected. CWD is lower than APD pressure at node RAYCHEM, but above design minimum listed above, which is inlet to downstream Middlefield/Ringwood feeder. Needs further validation before pressure lowering c | C2-V3 |  |  | 175 | 120 | 154.3 | 140.4 | 42.0124 | 67.2594
30 | NAH1 | TP_PENINSULA | MIDDLEFIELD RINGWOOD DFM | EQ000027, SRIEXT to SREGDN | Middlefield & Ringwood Reg Station, B-83 | 2.01 | PS353, PS361 | nah1PCE801 | V2B-Incomplete validation - results suspect | 120 | From 086868 | 120 | 120 | 90 | 116.6 | 112.2 | C2-NOP can be lowered to MOP-20 now | 96 | 90.7 |  |  | Small DFM with loading which should be confirmed and results validated | C2-V2B |  |  | 120 | 90 | 116.6 | 112.2 | 12.7689 | 28.7486
31 | NAH1 | TP_PENINSULA | HEALY TO MARTIN | SEGMENT OF LINE NEAR CRESSMAN THAT IS OPERATING AT 200 PSIG | Healy Reg Station | 6.62 | nah1PS700 | nah1PCE802 | V1-Meets Plng Guide validation criteria | 300 | 086868, currently operating at 200 psig and modeled as such for all scenarios | 200 | 200 | 155 | 140.2 | 110 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 300 | 155 | 140.2 | 110 | 106.6221 | 118.075
32 | NAH1 | TP_PENINSULA | 145 PSIG SF LOOP | DFM system fed by Sullivan, Martin, Lomita | Sullivan Station, C-97; Martin Station, Lomita Park Station | 28.87 | PS56, PS116, PS34 | PCE168, PCE169, PCE170, PCE171, PCE191, PCE192 | V1-Meets Plng Guide validation criteria | 145 | From 086868 | 141 | 141 | 90 | 133.2 | 95.3 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 117.9 | 84.4 | Uprate/replace as needed to bring Sullivan to Lomita to 275#; add regulation at SFGLC and run segment between Martin and SFGLC at 145#. Replacement of pipeline downstream of Sullivan totals 1 mile direct replacement, 2 miles of lined pipe replacement. | $20,165,120 | Resulting Pmins above in (17) and (18) are the results at 17th/Missouri without uprate/replacement. Included as FYI | C4-V1 | Y |  | 145 | 90 | 133.2 | 95.3 | 25.3985 | 92.4016
33 | NAH1 | TP_PENINSULA | L109 L132 HMB | Milpitas to Sullivan; Milpitas to Healy; control point is Sullivan inlet. CWD model currently operates at 285# at Milpitas. For CWD analysis changed Milpitas supply to 280#. For APD changed regulation at Milpitas and Sierra Vista to 280#. APD is control | Milpitas Terminal L132, L109 | 100.15 | PS115, PS55, PS349 | nah1PCE816, PCE182, PCE183 | V1-Meets Plng Guide validation criteria | 300 | From 086868 | 285 | 285 | 130 | 139.9 | 104.2 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 130.7 | 94.4 | Install Regulation from L147 (L101) into L132/L109 at Edgewood per plans currently in place; completion planned for 10/31/12 per Richard Geraghty. Estimated at $700k per Richard G. San Bruno Ave x-tie estimated at $3MM per Scott Fannin (2500' total L132 | $3,700,000 | Resulting Pmins above in (17) and (18) are the results without uprate/replacement. Included as FYI These Pmins are for Milpitas L101 at 345#, but Pmin with Milpitas L101 at 350# is also deficient. Pipeline Section PS55 also includes the 6.67 mile secti | C4-V1 | Y |  | 300 | 130 | 139.9 | 104.2 | 96.3447 | 108.2659
34 | NAH1 | TP_PENINSULA | ZANKER | Zanker Rd DFM, San Jose, 0829-01 | Zanker Rd Reg Station, E-03 | 0.72 | PS459 | nah1PS701 | V3-Insufficient P data to complete validation | 170 | From 086868 | 170 | 170 | 90 | 164.5 | 170 | C2-NOP can be lowered to MOP-20 now | 143.8 | 150 |  |  | Service' to customer. Needs validation before pressure lowering can occur. | C2-V3 |  |  | 170 | 90 | 164.5 | 170 | 8.845 | 0
35 | NAH1 | TP_PENINSULA | L101 | Milpitas to Lomita | Milpitas Terminal L101 | 33.68 | PS32, PS33 | nah1PCE817 | V1-Meets Plng Guide validation criteria | 365 | Verified with PLE Scott Fannin | 350 | 350 | 130 | 198 | 131.6 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 198.5 | 123.5 | Likely operational modifications will allow for reduction to 345#. Modifications include backing off pressure support from L147 to L132/L109 at Edgewood, backing off pressure support from L132A into L132/L109 at Sierra Vista, Closing MLV 10.32 during win | TBD | For purposes of this analysis, Edgewood was installed at is feeding into L132/L109 at 285#. Edgewood cost captured on L132 L109 HMB HIS. Possible 'uprate to 397#' of L101 acceleration of hydrotests on spurs | C4-V1 | Y |  | 365 | 130 | 198 | 131.6 | 80.8261 | 99.6402
36 | NAH1 | TP_PENINSULA | FOSTER CITY DFM | 0214-01 aka Poinsettia DFM | Pointsettia Ave. Reg Station, A-74 | 1.69 | PS360 | nah1PCE803 | V2B-Incomplete validation - results suspect | 170 | From 086868 | 170 | 170 | 90 | 165.5 | 130.2 | C2-NOP can be lowered to MOP-20 now | 144.9 | 123.1 |  |  | DFM loading should be validated further before pressure dropped | C2-V2B |  |  | 170 | 90 | 165.5 | 130.2 | 7.2584 | 57.4421
37 | NAH1 | TP_PENINSULA | EL MONTE DFM | Fed at Sierra Vista into recently uprated 201 MOP system | Sierra Vista Ave Reg Station, B-28 | 4.08 | PS401 | nah1PCE804 | V3-Insufficient P data to complete validation | 201 | From 086868 | 192 | 192 | 90 | 153 | 116 | C2-NOP can be lowered to MOP-20 now | 139.2 | 98.1 |  |  | DFM loading should be validated further before pressure dropped | C2-V3 |  |  | 201 | 90 | 153 | 116 | 52.6052 | 83.4185
38 | NAH1 | TP_PENINSULA | TODO EL MUNDO DFM | 0207-01 | Woodside and L109 Reg Station, C-10 | 1.17 | PS357 | nah1PCE805 | V3-Insufficient P data to complete validation | 125 | From 086868 | 120 | 120 | 90 | 113.4 | 104 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 97.5 | 86.7 | ~3500 8" downstream segment replaced with 12" is possibility. More research needed on constraining segment more lead to more appropriate investment | $2,765,000 | 10 psig lowering yields 98.3 psig. Further validation needed. | C3-V3 |  |  | 125 | 90 | 113.4 | 104 | 36.75 | 63.907
39 | NAH1 | TP_PENINSULA | RALSTON POLHEMUS DFM | 0208-02 Ralston 0209-01 Polhemus both fed from common reg station, with Ralston endpoint as design control | Ralston Ave. Reg Station, B-03 | 3.28 | PS358, PS359 | nah1PCE811 | V3-Insufficient P data to complete validation | 150 | From 086868, based on uprate of 2010 | 147 | 147 | 90 | 109.2 | 15 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 101.7 | TBD - Per JTRc uprate planned for 2012. Planned pressure increase is to 222# MOP for 11/1/12 completion with $500k cost per Scott Fannin. Also added $80k for reg station rebuild as model shows deficiency. Should be confirmed with Scott F. | $580,000 | Further work with Distribution is required to verify loading. Uprate currently planned for 222# per Scott Fannin. 202# NOP. Once complete, this should be adequate to allow for 20# setpoint lowering. | C4-V3 |  |  | 150 | 90 | 109.2 | 15 | 73.44 | 154.6875
40 | NAH1 | TP_PENINSULA | PACIFICA DFM | 0213-02, floats off L109 to San Pedro Reg at MP 0.91; Beyond 0.91 the MOP is 90# | San Pedro Valley Reg Station, C-50 | 4.25 | PS366 | nah1PCE806 | V3-Insufficient P data to complete validation | 90 | From 086868 | 86 | 86 | 65 | 77.9 | 65.8 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 145.8 | Replacement of all pipe d/s of San Pedro and eliminate San Pedro Valley Reg Station 17817 ft of 8". Float off L109/L132 | $14,075,430 | Did not change setpoints in the -20 models as no reason to do so on a 90 psig MOP | C4-V3 | Y |  | 90 | 65 | 77.9 | 65.8 | 52.4281 | 97.2996
41 | NAH1 | TP_PENINSULA | NORTH FIRST ST DFM | 0806-01 San Jose | N. First St & Tasman Dr Reg Station, E-05 | 3.01 | PS442 | nah1PCE807 | V2B-Incomplete validation - results suspect | 200 | From 086868 | 190 | 190 | 90 | 160.5 | 140.2 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Conservative investment would be full replacement of 15,840' with 8" | $12,513,600 | Per JTRc can not trust model results as likely under-loaded and currently constrained. As such, we cannot lower by 20# without further analysis on distribution system modeling | C4-V2B |  |  | 200 | 90 | 160.5 | 140.2 | 44.6387 | 63.7742
42 | NAH1 | TP_PENINSULA | GRANT STEVENS CREEK LAWRENCE DFM | 8805-03,04,23 Grant; 8807-01 Lawrence; 8806-01 Stevens Creek; Fed from 2 regs Lawrence and Whisman | Whisman & Middlefield Reg Station, B-34 ; Lawrence & Lakehaven Dr. Reg Station, C-20 | 26.95 | PS400, PS402 | nah1PCE808, nah1PCE809 | V2B-Incomplete validation - results suspect | 180 | From 086868 | 175 | 175 | 90 | 135.5 | 86.7 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Uprate of Lawrence DFM to ?? Psig and PLS installation near Stevens Creek | TBD | Per JTRc can not trust model results as likely under-loaded and currently constrained. As such, we cannot lower by 20# without further analysis on distribution system modeling | C4-V2B |  |  | 180 | 90 | 135.5 | 86.7 | 57.7767 | 102.3996
43 | NAH1 | TP_PENINSULA | LAFAYETTE DFM | 0804-03, Santa Clara | Lafayette & Hogan Reg Station, E-07 | 6.39 | PS439 | nah1PCE810 | V2B-Incomplete validation - results suspect | 180 | From 086868 | 175 | 175 | 90 | 115.1 | 147.9 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Large portions are parallel main with newer pipe (1967, 1973) parelleling older pipe (1949). Possibility of abandonment of 1949 pipeline and uprate of newer pipe. Pipe downstream of these parellel sections is 1957, 1962, 1980 era. | TBD | Per JTRc can not trust model results as likely under-loaded and currently constrained. As such, we cannot lower by 20# without further analysis using distribution system modeling. This DFM is CWD controlled vs APD. Possible uprate due to newer pipeline | C4-V2B | Y |  | 180 | 90 | 115.1 | 147.9 | 78.8148 | 43.3152
44 | JTRc | TP_PENINSULA | SUNNYVALE DFM | aka Britton Ave, GCUST 5813 | Reg Station C-18 | 1.37 | PS406 | nah1PCE812 | V3-Insufficient P data to complete validation | 400 | From 086868 | 225 | 225 | 90 | 224.9 | 225 | C1-Existing NOP offset is 20 psi or more |  |  | TBD - see notes | TBD | Minimal load exists on this DFM on the Peninsula LTS model. Valid analysis not possible | C1-V3 |  |  | 400 | 90 | 224.9 | 225 | 72.0342 | 72.0046
45 | NAH1 | TP_PENINSULA | ALPINE DFM | 0204-01 | Alpine Rd & Piers Ln Reg Station, C-37 | 1.62 | PS354 | nah1PCE813 | V3-Insufficient P data to complete validation | 170 | From 086868 | 170 | 170 | 90 | 170 | 170 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | TBD | TBD | Minimal load exists on this DFM on the Peninsula LTS model. No determination can be made. | C4-V3 |  |  | 170 | 90 | 170 | 170 | 0 | 0
46 | NAH1 | TP_PENINSULA | WALSH DFM | 0205-01 | Walsh Rd Reg Station, C-21 | 1.04 | PS355 | nah1PCE814 | V3-Insufficient P data to complete validation | 230 | 130# MOP listed on 086868, but should be 230# per SWL8. Modeled as 225# in Peninsula LTS. Discuss with JTRc SWL8 | 225 | 225 | 90 | 176.5 | 74.1 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 113 | Possible parallel 1/2 mile with 8" downstream of current 4"/6"parellel section' | $2,085,600 | 130# MOP listed on 086868. Modeled as 225# in Peninsula LTS. SWL8 confirmed this should be listed as 230# MOP | C4-V3 | Y |  | 230 | 90 | 176.5 | 74.1 | 48.5441 | 105.8241
47 | NAH1 | TP_PENINSULA | HACIENDAS DFM | 0206-01 | Woodside Rd Reg Station, C-13 | 0.7 | PS356 | nah1PCE815 | V3-Insufficient P data to complete validation | 110 | From 086868 | 110 | 110 | 90 | 110 | 110 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | TBD | TBD | Minimal load exists on this DFM. Needs Distribution model analysis and further validation for determination to be made. | C4-V3 |  |  | 110 | 90 | 110 | 110 | 0 | 0
48 | BHH2 | TP_CENTRAL_COAST | L306_839 | L306 - 20" transmission from Kettleman to Estrella River PLS. The Town of Avenal has small DFM's off L306 but these DFM's were modeled at 630 PSIG. | Kettleman to Milpitas Lines 100, 190 & 300 382704 Sht 1 | 43.44 | PS288, BHH2PS700, BHH2PS701, BHH2PS702 | PCE208, PCE209 | V1-Meets Plng Guide validation criteria | 840 | L306 has not operated with an inlet of 750 PSIG for years. Morro Bay Power Plant is a peaker and has a total capacity of 7,000 MCFH | 700 | 630 | 500 | 528 | 523 | C1-Existing NOP offset is 20 psi or more | 528 | 523 | No investments needed to reduce the pressure at L300 (Kettlemen) |  | Morro Bay is a peaker plant and has a total capacity of 7,000 MCFH, which is a lot less than the line was originally designed. | C1-V1 | Y |  | 840 | 500 | 528 | 523 | 93.6822 | 94.8356
49 | BHH2 | TP_CENTRAL_COAST | L306_636 | L306 - 20" transmission from Estralla PLS to Morro Bay Power Plant 275 PSIG primary. SoCal gas company has a tap for emergency supply to their customers. | Estrella River PLS 089659 | 29.72 | PS289 | PCE225, PCE226 | V1-Meets Plng Guide validation criteria | 636 |  | 550 | 500 | 250 | 439 | 437 | C1-Existing NOP offset is 20 psi or more | 439 | 437 | No investments needed to lower the MOP due to Morro Bay Power plants is a peaker and load is 7,000 MCFH |  | This power plant can run on either CWD or APD | C1-V1 | Y |  | 636 | 250 | 439 | 437 | 61.9232 | 62.4355
50 | BHH2 | TP_CENTRAL_COAST | L306_275 | L306 - Primary to Morro Bay Power Plant. Short piping to the plant from the primary. Min Flow is 450 MSCF, Maximum flow is 7,000 MSCF | Morro Bay PP Pri Reg Sta 083657 | 0.42 | BHH2PS704 | BHH2PCE800 | V1-Meets Plng Guide validation criteria | 275 | The power plant requires 100 PSIG with a low alarm at 90 PSIG | 150 | 100 | 90 | 99 | 99 | C1-Existing NOP offset is 20 psi or more | 99 | 99 | No investment needed because of Morro Bay Power Plant is a peaker and loads are 7,000 MCFH |  | This power plant can run on either a CWD or APD. | C1-V1 |  |  | 275 | 90 | 99 | 99 | 97.4809 | 97.4809
51 | BHH2 | TP_CENTRAL_COAST | L310_840 | L310 - Tres Pinos to Metz. This line feeds Calpine Cogen and Calpines peaker unit. The feed comes from Tres Pinos off L300A and B. The maximum inlet pressures over the years has been no more than 750 PSIG from L300. Loads 1500 MMCF + 300 MMCF | Tres Pinos Station 089179 | 37.57 | PS293 | BHH2PCE801 | V1-Meets Plng Guide validation criteria | 840 | Newer line installed to serve Calpine Cogen (old BAF) and the new peaker plant | 750 | 750 | 360 | 528 | 732 | C1-Existing NOP offset is 20 psi or more | 528 | 732 | No investments needed for this line. |  | Calpine and Calpine peaker are U/S of Metz and need to have a minimum of 360 PSIG | C1-V1 | Y |  | 840 | 360 | 528 | 732 | 74.1 | 29.475
52 | BHH2 | TP_CENTRAL_COAST | L301A_396 | Line 301A - Old MOP 396 PSIG, CROP 394 PSIG (2011). This line is exclusive to Moss PP units 6&7. Max capacity of this line is 7,000 mcfh. Units 6&7 peak at 13,800 mcfh and the additional load will come from L301G. This line is currently operating at 3 | Hollister Meter Station 282255 | 25.2 | PS270 | PCE204, PCE207 | V1-Meets Plng Guide validation criteria | 394 | CROP 394 8/3/11. Regulators currently set at 374 PSIG. | 374 | 374 | 150 | 177 | 177 | C1-Existing NOP offset is 20 psi or more | 177 | 177 | No investment needed |  | Line is currently lowered MOP - 20. Moss power plant will be able to use 7,000 MMCF off this line during a CWD, APD because it does not effect Monterey and Santa Cruz | C1-V1 | Y |  | 394 | 150 | 177 | 177 | 93.3485 | 93.3485
53 | BHH2 | TP_CENTRAL_COAST | CARMEL_125 | Carmel DFM - 125 PSIG MOP. This system comes off the Monterey system tied to L301B. Aguaito cuts the pressure into Carmel at 125 PSIG. | Aguajito Road Reg Sta 086445 | 2.5 | PS416 | BHH2PCE802 | V1-Meets Plng Guide validation criteria | 125 |  | 118 | 105 | 90 | 97 | 70 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 99 | 90 | Replace the 13,200' 8" with 10" transmission main tested to 313 PSIG. Highly Congested $790/ft includes 70k move around charge. Distribution needs 3 stations rebuilt at $300k each | $11,398,000 | Highly sensitive and political area | C4-V1 | Y |  | 125 | 90 | 97 | 70 | 82.6047 | 142.5249
54 | BHH2 | TP_CENTRAL_COAST | KING_CITY_130 | King City 130 DFM has 2 feeds. The primary is from King City (off L187) and the secondary is off L310 (Metz). Both regulators are set around 125 PSIG | King City Primary Regulator Station 0800096, and Metz Road Station 183721 | 3.9 | PS427 | PCE426, PCE427, PCE428, PCE429 | V1-Meets Plng Guide validation criteria | 130 | 2 Regulator stations feed this DFM, and with both systems, the DFM has adequate capacity | 125 | 125 | 90 | 122 | 121 | C2-NOP can be lowered to MOP-20 now | 109 | 108 | No investments needed since this DFM has 2 feeds going into it |  | The long term investment of this DFM is to uprate it to 313 MOP and have only one regulator station at Metz | C2-V1 |  |  | 130 | 90 | 122 | 121 | 22.9091 | 25.6705
55 | BHH2 | TP_CENTRAL_COAST | L301BCEF_408 | L301BCEF - 408 MOP CROP 344 MOP regulators set at 324 PSIG at Dolan. This system feeds primarily the Ford Ord, Monterey and Carmel areas. Secondary feed is to Harkins which feeds L187, but is now secondary to L187 and L103 is the primary | Dolan Road Meter Sta 083812 | 32.63 | PS271, PS272, PS274, PS275, PS411, PS417 | PCE202, PCE203 | V3-Insufficient P data to complete validation | 408 | ASSUME CROP IS CLEARED where CROP reduction on L301B has caused this line to be reduced 20% until a 300' section of main can be hydro tested in 2012. | 388 | 388 | 300 | 318 | 306 | C1-Existing NOP offset is 20 psi or more | 323 | 309 |  |  | PS411, PS417 does not have any pressure recorders and one will be installed to collect data this winter | C1-V3 | Y |  | 408 | 300 | 318 | 306 | 85.452 | 95.2448
56 | BHH2 | TP_CENTRAL_COAST | L103_350 | L103 - 350 MOP system. Bolsa set at 330 PSIG to California Street Regulator station | Bolsa Meter Station 089655 | 26.4 | PS35, PS423, PS424, PS426, PS430 | PCE200, PCE201 | V1-Meets Plng Guide validation criteria | 350 | MOP lowered to 330 PSIG for analysis. California street is the control point and needs 250 at California. L103 is the primary, and Harkins is the secondary going into L187 | 347 | 330 | 250 | 257 | 249 | C2-NOP can be lowered to MOP-20 now | 257 | 249 | No Investments needed. Pmin at San Ardo is 114 PSIG CWD, and 170 PSIG APD. Pmin required at San Ardo is 110 PSIG. |  | L103 is the primary feed, with Harkins as the secondary, due to the CROP reduction on L301B | C2-V1 | Y | Y | 350 | 250 | 257 | 249 | 94.085 | 100.8317
57 | BHH2 | TP_CENTRAL_COAST | L301G_500 | L301G - 500 MOP is the main transmission line that feeds the Central Coast area. This line directly feeds Moss power plant units 1&2 and extra capacity for units 6&7. There is a back feed regulator set at the end of L301G at 260 PSIG to allow pressure t | Hollister Meter Station 282255 | 39.5 | PS276, PS412, PS418, PS434 | PCE205, PCE206 | V3-Insufficient P data to complete validation | 500 | Modeled at 480 PSIG. Old regulators set at 490-495 PSIG from Hollister and L300A&B | 490 | 480 | 260 | 353 | 473 | C2-NOP can be lowered to MOP-20 now | 353 | 473 | PS412 there was a ERX installed in March of 2012, but data was not collected in the winter of 2011-12. Need to wait until 2013 to validate the DFM. |  | Assuming adequate pressure (480 PSIG +) from L300A and B at Hollister. Control valves regulate pressure coming into L301A and G. | C2-V3 | Y |  | 500 | 260 | 353 | 473 | 68.7451 | 14.403
58 | BHH2 | TP_CENTRAL_COAST | L301A_275 | 275 - MOP Moss units 6&7 units 6&7. This is the primary regulator station for Moss units 6&7, and piping to the power plant. Units 6&7 are peaker units and could operate during a CWD | Moss LandingPower Plant Primary Reg Sta 083811 | 0.9 | PS436 | PCE430, PCE431, PCE432, PCE433, PCE434 | V1-Meets Plng Guide validation criteria | 275 | Moss units 6&7 primary regulator station. Regulators set at 125 PSIG with secondary regulators at 120 PSIG from L301G. | 125 | 125 | 110 | 117 | 120 | C1-Existing NOP offset is 20 psi or more | 117 | 120 | No investments needed since this primary is off L301A which is almost exclusive to Moss units 6&7 |  | During a APD, Moss will be able to use 7,000 off L301A since this line does not feed into Monterey and Santa Cruz. | C1-V1 |  |  | 275 | 110 | 117 | 120 | 97.4986 | 96.3794
59 | BHH2 | TP_CENTRAL_COAST | L103_L187_313 | L103-L187 Transmission main from California Reg Station (off L103) to Harkins Road (off L301C) to San Ardo. Primary feed used to be from L301C but had to be shifted to L103 due to the CROP | Dolan Road Meter Sta 083812, California Street Reg Station 089570 and Harkins Rd Regulator Sta 082856 | 69.89 | PS36, PS192, PS193, PS425, PS437, PS431, PS432, PS433 | PCE423, PCE424, PCE425 | V3-Insufficient P data to complete validation | 313 | Because of the CROP reduction on L301B the primary feed to San Ardo will be switched from L301C to L103 (california reg station) | 307 | 293 | 110 | 114 | 170 | C2-NOP can be lowered to MOP-20 now | 114 | 170 | PS425, DCUST2139, DREG4259, PS437 do not have pressure recorders and will be installed this winter to collect data. |  | Numerous customers and several small DFM's have not had recording devices to monitor winter pressures in the past. T&R does not have charts or ERX's | C2-V3 | Y |  | 313 | 110 | 114 | 170 | 98.9566 | 80.4353
60 | BHH2 | TP_CENTRAL_COAST | MTY1_2_313 | 1813, 1815 Monterey - 313 MOP system. Two stations feed the Fort Ord, Monterey area. 1st & 8th and Davis - Reservation | 8th St and 1st Ave Regulator Station 087211 and Davis-Reservation Roads Regulator Station 089572 | 35.9 | PS410, PS414, PS415 | BHH2PCE803, BHH2PCE804 | V1-Meets Plng Guide validation criteria | 313 | ASSUME CROP IS CLEARED where U/S subsystem L301B was lowered from 408 PSIG to 344 PSIG because of a CROP. | 307 | 293 | 200 | 215 | 200 | C2-NOP can be lowered to MOP-20 now | 244 | 174 |  |  | Pressure problems in Carmel and Monterey occur when the CROP is not cleared off L301B | C2-V1 | Y | Y | 313 | 200 | 215 | 200 | 89.2615 | 100
61 | BHH2 | TP_CENTRAL_COAST | L181A_DFM1_303 | 1816 - 303 PSIG system from San Jaun to Blain Street (inlet to Felton DFM) | San Juan Road Reg Station 0800062, Front St Regulator Station 0800097, Watsonville Crosstie Reg Sta 0800407 and Rob Roy Junction Pressure Limiting Sta 087212 | 34.6 | PS182, PS183, PS407, PS413, PS420, PS421, PS422 | PCE435, PCE436, PCE437, PCE438 | V3-Insufficient P data to complete validation | 303 | This section is D/S of Rob Roy which is the control point. Assumes that L1816 is back in service and not locked in at 225 PSIG. | 295 | 283 | 90 | 147 | 73 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 147 | 92 | In order to get Felton back up to 90 PSIG it is necessary to replace the existing 10" main coming out of Rob Roy (1.87 miles) with 16". This is also assuming that 1816 will be hydro tested and placed back in service. 9900' 16" x $980/ft = $9.8 million p | $10,700,000 | This analysis is based on the fact that L181A (1816) will be hydro tested and back in service from San Juan to Rob Roy to feed into Santa Cruz. | C4-V3 | Y |  | 303 | 90 | 147 | 73 | 83.862 | 103.3103
62 | BHH2 | TP_CENTRAL_COAST | DFM1_2_3_303 | 1816 and 1818 DFM (Felton and Davenport DFM's, Santa Cruz holder). Systems past Rob Roy | Rob Roy Junction Pressure Limiting Sta 087212 and the Santa Cruz Underground Holder 080393 | 37.2 | PS409, PS419, PS429 | PCE435, PCE436 | V1-Meets Plng Guide validation criteria | 303 | Controlling point is Rob Roy which L181A and B converge. Pmin is at Felton where the Santa Cruz holder will supply extra feed at 180 PSIG | 295 | 283 | 90 | 147 | 73 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 147 | 92 | See L181_DFM1_303 - Same investment needed. | See L181_DFM1_303 | This analysis is based on the fact that L181A (1816) will be hydro tested and back in service from San Juan to Rob Roy to feed into Santa Cruz. | C4-V1 | Y |  | 303 | 90 | 147 | 73 | 83.862 | 103.3103
63 | BHH2 | TP_CENTRAL_COAST | L181B_DFM2_400 | 1817 - 400 MOP system starting at Cole Road Regulator Station and endind at Rob Roy. Cole is the primary feed, and San Juan is the secondary feed | Cole Road Reg Sta 089666 and San Juan 0800062 | 16.7 | PS184, PS185, PS273, PS277 PS408, PS435 | BHH2PCE808, BHH2PCE809 | V1-Meets Plng Guide validation criteria | 400 | System reduced to determine what impacts there are. Controlling point is Rob Roy where L181A and B converge. Pmin is at Felton | 395 | 380 | 90 | 147 | 73 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 147 | 92 | See L181_DFM1_303 - Same investment needed. | See L181_DFM1_303 | This analysis is based on the fact that L181A (1816) will be hydro tested and back in service from San Juan to Rob Roy to feed into Santa Cruz. | C4-V1 | Y |  | 400 | 90 | 147 | 73 | 91.1066 | 101.8242
64 | BHH2 | TP_CENTRAL_COAST | SANTA_CRUZ_HOLDER | The underground holder is used during winter months to make up capacity to serve the Felton area. It is manually filled each time it is used during a cold event. There is no permanent connection to the transmission system that could over pressure it. | Santa Cruz Underground Holder 080393 | 2.33 | BHH2PS705 | PCE439, PCE440 | V1-Meets Plng Guide validation criteria | 618 | Undergournd holder is typically re-charged at 600-605 PSIG when the holder is used in the winter months. | 600 | 598 | 170 | 499 | 125 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 521 | 137 | See L181_DFM1_303 - Same investment needed. | See L181_DFM1_303 | Reduced capacity by reducing the holder's pressure. At 618 = 3.016 MMCF, at 598 PSIG = 2.912 MMCF (Difference 0.104 MMCF) | C4-V1 |  |  | 618 | 170 | 499 | 125 | 37.6527 | 103.7604
65 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Tap | L138A, L138B |  | 36.96 | PS130, PS131, PS126 | RLP7PCE811 | V1-Meets Plng Guide validation criteria | 800 | None | 700 | 700 | 590 | 593 | 605 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 800 | 590 | 593 | 605 | 98.7842 | 93.8592
66 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Fresno Belt Main | System d/s of Tarpey, Chestnut/Clay and FGLC |  | 36.71 | PS478 | PCE443, PCE449, RLP7PCE800 | V1-Meets Plng Guide validation criteria | 204 | 204 | 195 | 195 | 90 | 130 | 90 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Upgrading the Fresno Belt Main was previously identified and is a current project in engineering. TSP has already identified the need to complete by November 1, 2012. | TBD |  | C4-V1 |  |  | 204 | 90 | 130 | 90 | 73.7439 | 100
67 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Tap | Vernalis Tap to Vernalis Field Valve Lot |  | 4.59 | PS48 | PCE154 | V1-Meets Plng Guide validation criteria | 1040 | None | 720 | 715 | 650 | 653 | 668 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 1040 | 650 | 653 | 668 | 99.4069 | 96.4005
68 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L108 Vernalis Valve Lot | Vernalis Field Valve Lot to Ripon Reg Station |  | 14.53 | PS49, PS519 | RLP7PCE809 | V1-Meets Plng Guide validation criteria | 720 | None | 715 | 715 | 395 | 426 | 564 | C2-NOP can be lowered to MOP-20 now | 400 | 545 |  |  |  | C2-V1 | Y |  | 720 | 395 | 426 | 564 | 92.9766 | 55.2753
69 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L215 | Oak Flat to West Ave Reg. |  | 45.93 | PS240, PS491, PS78 | RLP7PCE808 | V1-Meets Plng Guide validation criteria | 787 | CROP in place that reduced MOP from 890 psig to 787 psig. | 750 | 750 | 290 | 305 | 629 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 787 | 290 | 305 | 629 | 98.3326 | 41.7973
70 | RLP7 | TP_SAN_JOAQUIN_VALLEY | 7224-19 | Stanislaus DFM |  | 1.34 | RLP7PS702 | RLP7PCE806 | V2B-Incomplete validation - results suspect | 95 | None | 95 | 95 | 90 | 92 | 91 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 72 | 70 | Install 1.34 miles 8" or larger pipe with MAOP of 720 psig. | $3,500,000 |  | C4-V2B |  |  | 95 | 90 | 92 | 91 | 60.6486 | 80.4324
71 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Oakdale | Oakdale, Escalon, Riverbank |  | 31.76 | RLP7PS703 | PCE465 | V1-Meets Plng Guide validation criteria | 180 | None | 175 | 175 | 90 | 139 | 139 | C2-NOP can be lowered to MOP-20 now | 109 | 109 |  |  | ASD controls due to canning loads. Pressures shown above are ASD pressures. | C2-V1 |  | Y | 180 | 90 | 139 | 139 | 53.823 | 53.823
72 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Turlock-Modesto DFM | 260 psig system. Serves Modesto, Ceres, Turlock. |  | 44.62 | RLP7PS706, RLP7PS707, RLP7PS708, RLP7PS709 | PCE463, PCE464, RLP7PCE816, RLP7PCE817 | V3-Insufficient P data to complete validation | 260 | None | 255 | 255 | 125 | 199 | 201 | C2-NOP can be lowered to MOP-20 now | 179 | 179 |  |  |  | C2-V3 |  |  | 260 | 125 | 199 | 201 | 53.8701 | 52.3309
73 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Modesto | 408 psig system. |  | 49.47 | PS489, PS518, PS486, RLP7PS700, RLP7PS701 | RLP7PCE802 | V1-Meets Plng Guide validation criteria | 408 | none | 403 | 403 | 200 | 203 | 206 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | See notes. | See notes | 2012 PSEP replacement is scheduled for construction by end of 2012. This will replace about 4 miles of 8" pipe with 16" pipe on DFM 7221-10. Pressure reduction should not happen until this is complete. | C4-V1 | Y |  | 408 | 200 | 203 | 206 | 99.044 | 98.0738
74 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118N | Bradbury to Merced (V-60.45) |  | 34.45 | PS75, PS76, PS77, PS78, PS80 | RLP7PCE803, RLP7PCE804, PCE450 | V1-Meets Plng Guide validation criteria | 400 | BTU separation V60.45 is opened on Design Days to support Merced south. | 395 | 395 | 90 | 70 | 172 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | see notes | see notes | 2013 PSEP project planned to extend L352 to Herndon Jct. This will be 24" pipe with a new reg station feeding into L118. After project is complete, pressure reductions can be done. | C4-V1 | Y |  | 400 | 90 | 70 | 172 | 102.1066 | 85.8565
75 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Eight Mile Road DFM | Eight Mile Road DFM fed from L108. |  | 16.48 | PS511 | RLP7PCE822 | V3-Insufficient P data to complete validation | 412 | none | 385 | 385 | 90 | 278 | 293 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressures above are prior to the upgrade. Eight Mile Road will be regulated to line 11. | C1-V3 |  |  | 412 | 90 | 278 | 293 | 57.1998 | 51.9011
76 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L148 | McMullin Ranch to Morgan/Whitmore |  | 17.63 | PS141, PS488, PS485 | RLP7PCE801 | V1-Meets Plng Guide validation criteria | 326 | Under MOP from 408 psig to 326 psig. Currently operating 15 psig below 326 psig. | 311 | 311 | 220 | 209 | 210 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | See notes | See notes | Hydrotest is progress. Pressure restoration 12/1/12, tentatively, to 408 psig. | C4-V1 | Y |  | 326 | 220 | 209 | 210 | 108.1536 | 107.4297
77 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Hammertown | Hammertown and Tom 'O' Shanter | Brown Rd at Red Mountain Reg OD0800470 V- R1, R2, R3, R4 | 7.22 | PS513 | RLP7PCE823 | V3-Insufficient P data to complete validation | 412 | none | 385 | 385 | 90 | 287 | 300 | C1-Existing NOP offset is 20 psi or more |  | 300 |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressures above are prior to the upgrade. Hammertown will be regulated to Line 11. | C1-V3 |  |  | 412 | 90 | 287 | 300 | 54.054 | 49.3331
78 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Louise Ave DFM | Louise Ave DFM served from L108. |  | 2.61 | PS515 | PCE814 | V2B-Incomplete validation - results suspect | 408 | none | 385 | 385 | 90 | 358 | 374 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressure above are prior to the upgrade. Lousie Ave DFM will be regulated to line 11. | C1-V2B |  |  | 408 | 90 | 358 | 374 | 24.1848 | 16.7892
79 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Zephyr Road DFM | Fed from L108 1606 at Carpenter Rd |  | 2.51 | PS509 | RLP7PCE821 | V3-Insufficient P data to complete validation | 408 | none | 385 | 385 | 90 | 330 | 348 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | L108, between Ripon-Modesto Meter Station and Eight Mile Road, is to be upgraded from 408 psig to 720 psig, in May 2012. The pressure above are prior to the upgrade. Zephyr Road DFM will be regulated to line 11. | C1-V3 |  |  | 408 | 90 | 330 | 348 | 36.3492 | 28.6429
80 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Alpine DFM | 1621-01, DREG 4939. Fed from L108. |  | 2.1 | PS537 | RLP7PCE805 | V3-Insufficient P data to complete validation | 100 | none | 100 | 100 | 90 | 93 | 91 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | 2.1 miles of 8" or larger, 720 psig. | $8,800,000 |  | C4-V3 |  |  | 100 | 90 | 93 | 91 | 71.1053 | 90.4737
81 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Manteca DFM | 1602-01. MP 0.7 - MP 2.66 |  | 2 | PS531 | RLP7PCE807 | V3-Insufficient P data to complete validation | 120 |  | 115 | 115 | 90 | 108 | 105 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 103 | 99 | Reinforce with approx 0.75 miles, 8" steel | $3,100,000 |  | C3-V3 |  |  | 120 | 90 | 108 | 105 | 43.4286 | 53.5714
82 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Hazelton DFM | Hazelton DFM, Pacific Paperboard DFM. Serves the Port of Stockton. |  | 10.95 | PS514 | PCE813 | V2B-Incomplete validation - results suspect | 175 |  | 170 | 170 | 90 | 151 | 163 | C2-NOP can be lowered to MOP-20 now | 134 | 147 |  |  |  | C2-V2B |  |  | 175 | 90 | 151 | 163 | 34.7347 | 18.0067
83 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Stockton L108 | Ripon-Modesto Meter Station to Eight Mile Road. |  | 24.4 | PS50, PS51 | RLP7PCE825 | V1-Meets Plng Guide validation criteria | 408 | This section of L108 to be upgraded from 408 psig to 720 psig in July 2012 (?), in conjunction with NCPA Lodi coming on-line. | 403 | 403 | 275 | 275 | 293 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Finish the pressure upgrade to 720 psig. |  | Pressure upgrade in progress. Once upgrade is complete to 720 psig, MOP-20 can be implemented. | C4-V1 | Y |  | 408 | 275 | 275 | 293 | 100 | 88.7449
84 | RLP7 | OTHER | Patterson DFM | Served from L-2. |  | 3.45 | RLP7PS715 | PCE149 | V3-Insufficient P data to complete validation | 395 |  | 250 | 250 | 90 | 210 | 210 | C2-NOP can be lowered to MOP-20 now | 210 | 210 |  |  | NOP is uncertain. | C2-V3 |  |  | 395 | 90 | 210 | 210 | 75.6633 | 75.6633
85 | RLP7 | OTHER | Los Banos DFM | Served from L-2. |  | 7.89 | PS507 | RLP7PCE810 | V1-Meets Plng Guide validation criteria | 394 |  | 385 | 350 | 90 | 275 | 217 | C2-NOP can be lowered to MOP-20 now | 275 | 217 |  |  | NOP is uncertain. | C2-V1 |  |  | 394 | 90 | 275 | 217 | 54.1071 | 73.5014
86 | RLP7 | OTHER | L-331 | Crosstied to L-2 and L-401 |  | 15.7 | PS308, PS309 | PCE104, PCE105 | V1-Meets Plng Guide validation criteria | 787 | CROP reduced MOP to 787 psig from 890 psig. | 610 | 610 | 120 | 150 | 150 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | ASD controls. Seasonal Load. | C1-V1 | Y |  | 787 | 120 | 150 | 150 | 98.6611 | 98.6611
87 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Helm Jct/Elkhorn | Downstream of Helm Jct and Elkhorn. 650 psig system. |  | 158.34 | PS57, PS59, PS311, PS312, PS127, PS128, PS129, PS132, PS133, PS482, PS483 | PCE451, PCE452, PCE446, PCE447 | V1-Meets Plng Guide validation criteria | 650 |  | 645 | 645 | 225 | 304 | 328 | C2-NOP can be lowered to MOP-20 now | 229 | 320 |  |  |  | C2-V1 | Y | Y | 650 | 225 | 304 | 328 | 88.7621 | 84.6833
88 | RLP7 | TP_SAN_JOAQUIN_VALLEY | FGLC | FGLC to FJCT |  | 12.49 | PS73, PS58 | PCE448, PCE450 | V1-Meets Plng Guide validation criteria | 400 |  | 390 | 390 | 300 | 316 | 313 | C2-NOP can be lowered to MOP-20 now | 306 | 302 |  |  | 2012 PSEP replacement pipe will improve pressures. | C2-V1 |  | Y | 400 | 300 | 316 | 313 | 85.92 | 88.6157
89 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L118 | FJCT to V-60.45 (Merced). |  | 126.76 | PS73, PS74, PS75, PS79 | PCE450 | V2B-Incomplete validation - results suspect | 400 |  | 395 | 395 | 90 | 63 | 136 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | PSEP to extend L352 to Herndon and install a new reg station. This is planned for 2013 or 2014. | TBD |  | C4-V2B | Y |  | 400 | 90 | 63 | 136 | 102.7196 | 93.156
90 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Ave 13 | 7211-01 |  | 3.37 | RLP7PS704 | PCE812 | V2B-Incomplete validation - results suspect | 150 | Not sure of MOP | 150 | 150 | 90 | 133 | 149 | C2-NOP can be lowered to MOP-20 now | 110 | 129 |  |  |  | C2-V2B |  |  | 150 | 90 | 133 | 149 | 33.4097 | 2.0764
91 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Selma | 1209-02. Feed to Selma. |  | 4 | RLP7PS705 | RLP7PCE815 | V3-Insufficient P data to complete validation | 230 |  | 230 | 230 | 90 | 203 | 193 | C2-NOP can be lowered to MOP-20 now | 181 | 169 |  |  | NOP is uncertain. | C2-V3 | Y |  | 230 | 90 | 203 | 193 | 26.096 | 34.9353
92 | RLP7 | TP_SAN_JOAQUIN_VALLEY | L307/134 | Spreckels to Herndon Jct |  | 73.36 | PS290, PS291, PS292, PS119, PS120, PS479 | PCE234, PCE235 | V1-Meets Plng Guide validation criteria | 500 |  | 495 | 495 | 280 | 310 | 328 | C2-NOP can be lowered to MOP-20 now | 291 | 309 |  |  |  | C2-V1 | Y | Y | 500 | 280 | 310 | 328 | 89.6853 | 82.993
93 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kerman | Kerman DFM serves Kerman and Biola |  | 7.86 | PS480 | RLP7PCE820 | V3-Insufficient P data to complete validation | 283 |  | 275 | 275 | 90 | 184 | 125 | C2-NOP can be lowered to MOP-20 now | 166 | 98 |  |  |  | C2-V3 |  |  | 283 | 90 | 184 | 125 | 64.2223 | 89.547
94 | RLP7 | TP_TRACY | Tracy | Serves City of Tracy. |  | 25.5 | PS155, PS516 | PCE152, PCE138 | V1-Meets Plng Guide validation criteria | 365 |  | 325 | 320 | 90 | 306 | 300 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 365 | 90 | 306 | 300 | 31.6396 | 34.5455
95 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Baker Commodities | Transmission along Madera Ave that feeds Foster Farms and Baker Commodities. |  | 9 | RLP7PS711 | RLP7PCE819 | V2B-Incomplete validation - results suspect | 250 |  | 200 | 200 | 90 | 166 | 200 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V2B |  |  | 250 | 90 | 166 | 200 | 64.2353 | 41.3603
96 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Herndon & Hayes | Fed from Cattern and Weber. |  | 1.23 | RLP7PS713 | RLP7PCE824 | V3-Insufficient P data to complete validation | 400 |  | 200 | 200 | 90 | 195 | 193 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V3 |  |  | 400 | 90 | 195 | 193 | 80.2995 | 80.8104
97 | RLP7 | TP_SAN_JOAQUIN_VALLEY | Kamm Ave Feeder | Served from L111 and feed Con Agra Foods and Helm Sulfur. |  | 4.09 | RLP7PS710 | RLP7PCE818 | V2B-Incomplete validation - results suspect | 300 | MOP from Fresno T&R | 270 | 270 | 100 | 255 | 255 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | ASD controls. | C1-V2B |  |  | 300 | 100 | 255 | 255 | 31.2188 | 31.2188
98 | RLP7 | OTHER | L-186 | Serves Dos Palos from L-2. |  |  | PS190, PS191 | RLP7PCE826 | V3-Insufficient P data to complete validation | 270 |  | 250 | 250 | 90 | 186 | 186 | C2-NOP can be lowered to MOP-20 now | 186 | 186 |  |  | NOP uncertain. | C2-V3 | Y |  | 270 | 90 | 186 | 186 | 59.1111 | 59.1111
99 | RLP7 | OTHER | Nees Ave DFM | Serves Olam West (DeFrancisco) from L-2. |  | 7.52 | PS501, RLP7PS712 | PCE467 | V2B-Incomplete validation - results suspect | 620 |  | 400 | 400 | 90 | 153 | 153 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | NOP uncertain. ASD controls. | C1-V2B |  |  | 620 | 90 | 153 | 153 | 95.9317 | 95.9317
100 | RLP7 | OTHER | Newman-Gustine | Looped DFM to serve Newman and Gustine. |  | 15.75 | RLP7PS714 | PCE134, PCE142 | V3-Insufficient P data to complete validation | 150 |  | 145 | 145 | 90 | 126 | 133 | C2-NOP can be lowered to MOP-20 now | 109 | 116 |  |  | NOP is uncertain. | C2-V3 |  |  | 150 | 90 | 126 | 133 | 46 | 33.4097
101 | c5s1 | TP_SAN_JOSE | L100 | L100 from Milpitas Terminal to PLS7 | Milpitas Terminal | 12 | PS31 | c5s1PCE800 | V1-Meets Plng Guide validation criteria | 365 | Original MOP of 400 psig. Reduced to 300 psig by CPUC. CPUC approved raising of MOP to 365 psig in Dec 2011. | 350 | 345 | 225 | 249.02 | 196.54 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Parallel ~4 miles of L100 from M.P. 500.69 to MLV 144.67 with 16" pipe. | $17,400,000 | N/A | C4-V1 | Y |  | 365 | 225 | 249.02 | 196.54 | 86.2155 | 114.5242
102 | c5s1 | TP_SAN_JOSE | Dixon Landing DFM | DFM from L131 at Dixon Landing & 880 to Dixon Landing & Milpitas Blvd. | Dixon Landing & Hwy 880 Regulator Station | 0.94 | PS453 | c5s1PCE801 | V1-Meets Plng Guide validation criteria | 175 |  | 168 | 163 | 90 | 147.72 | 139.53 | C2-NOP can be lowered to MOP-20 now | 133.37 | 124.31 | N/A | N/A | N/A | C2-V1 |  |  | 175 | 90 | 147.72 | 139.53 | 39.0846 | 49.5289
103 | c5s1 | TP_SAN_JOSE | Barber DFM | DFM from Milpitas Terminal to Lundy & Murphy Station (F17) and Abbott-Milpitas Alvisio Road (E11). | Milpitas Terminal (SJDFM) | 4.1 | PS445, PS443 | PCE180 | V3-Insufficient P data to complete validation | 160 | Original MOP of 200 psig. Reduced to 160 psig by CPUC 2/2011. No indication that original MOP will be restored. | 145 | 140 | 90 | 132.21 | 127.74 | C2-NOP can be lowered to MOP-20 now | 126.94 | 122.31 | N/A | N/A | N/A | C2-V3 |  |  | 160 | 90 | 132.21 | 127.74 | 46.4029 | 53.0428
104 | c5s1 | TP_SAN_JOSE | Mabury DFM | DFM from Mabury Station at Mabury Rd & Pine Hollow (F06) to Autumn & Julian Reg Station (F47). | Mabury Road Regulator Station | 5.1 | PS457, PS447 | c5s1PCE802 | V1-Meets Plng Guide validation criteria | 200 |  | 190 | 185 | 90 | 165.44 | 153.95 | C2-NOP can be lowered to MOP-20 now | 154.24 | 141.91 | N/A | N/A | N/A | C2-V1 |  |  | 200 | 90 | 165.44 | 153.95 | 39.5912 | 51.0953
105 | c5s1 | TP_SAN_JOSE | Tully DFM | DFM from Tully Station (F78) to Roberts & Fisher Station (D24). | Tully Regulator Station | 33.5 | PS452, PS454, PS466, PS467, PS450, c5s1PS700 | PCE460 | V1-Meets Plng Guide validation criteria | 200 |  | 195 | 190 | 90 | 131.25 | 60.28 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | (1) Parallel ~0.96 miles of 0840-01 with 6" pipe from MLV 13-14C to MLV 13-J5B. (2) Parallel ~3.8 miles of 0821-02 with 12" pipe from MLV 74-A5A to Reg D26. | $20,800,000 | N/A | C4-V1 | Y |  | 200 | 90 | 131.25 | 60.28 | 71.3901 | 114.001
106 | c5s1 | TP_SAN_JOSE | Fontanoso DFM | DFM from Fontanoso Reg Station (G77) to Cottle & Poughkeepsie Reg Station (G49). | Fontanoso Road Regulator Station | 2.9 | PS448 | c5s1PCE803 | V1-Meets Plng Guide validation criteria | 400 |  | 365 | 360 | 260 | 348 | 340.48 | C1-Existing NOP offset is 20 psi or more |  |  | N/A | N/A | N/A | C1-V1 |  |  | 400 | 260 | 348 | 340.48 | 42.0952 | 47.6985
107 | c5s1 | TP_SAN_JOSE | Blossom Hill DFM | DFM from Cottle & Poughkeepsie Reg Station (G49) to endpoints of Cottle & Santa Teresa Reg Station (G73) and Rajkovich & Almaden Expressway Reg Station (G79). | Cottle & Poughkeepsie Road Regulator Station | 9 | PS449 | c5s1PCE804 | V1-Meets Plng Guide validation criteria | 242 |  | 235 | 230 | 90 | 168.26 | 114.37 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 164.25 | 108.69 | Replace approximately 1.1 miles of 6" with 10" starting 6000' downstream of G55 to G79. | $5,300,000 | N/A | C3-V1 |  |  | 242 | 90 | 168.26 | 114.37 | 59.9488 | 90.1306
108 | c5s1 | TP_GILROY | Emado DFM | DFM from Emado Reg Station (H15) to Emado & Hwy 101 Reg Station (H23). | Emado Ave Regulator Station | 0.71 | PS451 | c5s1PCE805 | V3-Insufficient P data to complete validation | 100 |  | 90 | 90 | 80 | 89.8 | 89.8 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 89.9 | 89.9 | Replace ~3700 ft (whole DFM) of 2" with 6". | $1,100,000 | N/A | C3-V3 | Y |  | 100 | 80 | 89.8 | 89.8 | 53.7767 | 53.7767
109 | c5s1 | TP_GILROY | Puppo DFM | DFM from Hwy 101 & Scheller Ave Reg Station (H18) to Monterey Hwy & Puppo R/W Reg Station (H16). | Hwy 101 and Scheller Ave Regulator Station | 0.84 | PS458 | c5s1PCE806 | V3-Insufficient P data to complete validation | 400 |  | 250 | 245 | 90 | 241.3 | 238.5 | C1-Existing NOP offset is 20 psi or more |  |  | N/A | N/A | N/A | C1-V3 |  |  | 400 | 90 | 241.3 | 238.5 | 67.0009 | 67.8853
110 | c5s1 | TP_GILROY | Cochrane DFM | DFM from Peet & Cochrane Reg Station (H01) to N/S Cochrane, w/o Hwy 101 Reg Station (H03). | Peet & Cochrane Regulator Station | 0.88 | PS455 | c5s1PCE807 | V3-Insufficient P data to complete validation | 320 |  | 308 | 303 | 90 | 235.5 | 186.4 | C2-NOP can be lowered to MOP-20 now | 225.2 | 173.3 | N/A | N/A | N/A | C2-V3 |  |  | 320 | 90 | 235.5 | 186.4 | 49.777 | 71.7445
111 | c5s1 | TP_GILROY | Diana DFM | DFM from Diana Reg Station(H06) east to Diana & L300A Reg Station (H05) and west to Diana e/o Railroad Reg Station (H09). | Diana Ave Regulator Station | 2.9 | PS444 | c5s1PCE808 | V2B-Incomplete validation - results suspect | 250 |  | 240 | 235 | 90 | 171.1 | 119.3 | C2-NOP can be lowered to MOP-20 now | 157.2 | 99.3 | N/A | N/A | An uprate of Diana DFM from an MOP of 250# to 350# is scheduled to be complete by the end of 2012. | C2-V2B |  |  | 250 | 90 | 171.1 | 119.3 | 61.075 | 88.727
112 | c5s1 | TP_GILROY | Church DFM | DFM from Church Ave Reg Station (H46) to Church & Old 101 Hwy (H33). | Church Ave Regulator Station | 2.6 | PS460, c5s1PS701 | c5s1PCE809 | V1-Meets Plng Guide validation criteria | 335 |  | 300 | 295 | 90 | 191.8 | 99.9 | C1-Existing NOP offset is 20 psi or more |  |  | N/A | N/A | N/A | C1-V1 |  |  | 335 | 90 | 191.8 | 99.9 | 72.4492 | 98.1945
113 | c5s1 | TP_GILROY | Roop DFM | DFM from Roop Road Reg Station (H95) to Roop Road & New Reg Station (H96). | Roop Road Regulator Station | 1.3 | PS446 | c5s1PCE810 | V3-Insufficient P data to complete validation | 120 |  | 115 | 110 | 90 | 104.7 | 102 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 99.4 | 96.7 | Replace ~3,450 ft of 2" with 4" from H94 at Estates Drive & Roop Road to H97 at Sugar Babe Road & Roop Road | $1,760,000 | N/A | C3-V3 | Y |  | 120 | 90 | 104.7 | 102 | 54.57 | 63.4286
114 | c5s1 | TP_GILROY | Bloomfield DFM | DFM from Bloomfield Reg Station (H73) to Kelton Dr & First Reg Station. DFM includes Calpine/Gilroy Power Plant. | Bloomfield Regulator Station | 9.1 | PS461, PS462, PS463, PS464, PS465 | c5s1PCE811 | V1-Meets Plng Guide validation criteria | 400 |  | 395 | 390 | 90 | 362.5 | 353.5 | C2-NOP can be lowered to MOP-20 now | 346.3 | 336.8 | N/A | N/A | N/A | C2-V1 |  |  | 400 | 90 | 362.5 | 353.5 | 18.8241 | 23.0663
115 | ZTR1 | TP_REDDING | L402_REDDING_600 | L402 from Redding/ Calaveras Tap (L400) to Lehigh Cement and associated DFM's | Redding Calaveras Tap OD083694 V-8, 9, 10, 11 | 54 | PS344, PS545, PS547, PS548, PS549, PS559, PS561, ZTR1PS700 | PCE374, PCE375, PCE40 | V1-Meets Plng Guide validation criteria | 600 | There is currently a CROP in place of 426 psig; however, I anticipate that CROP being lifted in June once a short section of main is replaced at DREG5477. | 594 | 590 | 120 | 386 | 419 | C2-NOP can be lowered to MOP-20 now | 364 | 400 | None |  | 086868 and GIS are off regarding Route Numbers and Pipe Descriptions. Model has not been updated to include new DR 98 at North end of Airport DFM Extension. Redding Calveras Pressure modeled with flat profile. No Growth was added to the model. | C2-V1 |  | Y | 600 | 120 | 386 | 419 | 61.0544 | 53.3678
116 | ZTR1 | TP_HUMBOLDT | 1309_ALTON_100 | 100 psig DFM served from L177A via the Alton Primary that serves Rio Dell and Scotia | Alton Primary OD082931 V-14, 15, 16, 17 | 4.2 | ZTR1PS701 | ZTR1PCE801 | V1-Meets Plng Guide validation criteria | 100 | Pipeline Engineering is currently exploring raising the MOP of this line to meet the 5/20 analysis, and projected new loads | 94 | 92 | 66 | 70 | 59 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | 4 miles of 4" Replaced with 6" at 250#, upgrade Regs as needed, 4 bores/ bridge hangings. | $5,600,000 | Minimum Design Based on R73 36# Outlet Pressure. 13.9Mcfh Commercial/ Industrial Growth consistent with current RFC. | C4-V1 |  |  | 100 | 66 | 70 | 59 | 90.3614 | 115.5032
117 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_819 | During a Design Day, several subsystems will operate as a single subsystem and these have all been combined for this analysis: L177_EUREKA_819, L177_EUREKA_430, L177_EUREKA_350, L137B_GIUNTOLI_250 | Gerber Compressor OD284543 V-21, 22 | 126 | PS181, PS176, PS177, PS178, PS100, PS102, PS123, PS194 | PCE38, PCE347, PCE348, PCE356, PCE357, PCE360, PCE361, PCE345, PCE346 | V1-Meets Plng Guide validation criteria | 819 | 819#, 430#, 350#, and 250# | 819 | 819 | 90 | 89 | 215 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | 10miles 12" L177 Reinfocement; Arcata Trans Reg Rebuild, R38, R41, R09 DR Rebuilds | $16,800,000 | Assuming HBGS allowable CWD burn rate of 870 Mcfh remains unchanged. Several Reg Stations undersized for lower inlet pressures. | C4-V1 | Y |  | 819 | 90 | 89 | 215 | 100.027 | 94.2467
118 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_430 | L177A Cummins Creek to Tompkins Hill | Cummins Creek OD082474 V-2, 4, 7, 8 | 15 | PS177 | PCE347, PCE348 | V1-Meets Plng Guide validation criteria | 430 |  | 423 | 422 | 260 | 244 | 347 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 241 | 334 | Investments included in 819# Subsystem Analysis |  | Analysis completed assuming 819# setpoint at Gerber | C4-V1 | Y |  | 430 | 260 | 244 | 347 | 106.8747 | 54.9795
119 | ZTR1 | TP_HUMBOLDT | L177_EUREKA_350 | L177A from Tompkins Hill to Ryan Slough: L126A, L126B, L189, L137B | Tompkins Hill OD183697 V-50, 51, 66, 78 | 45 | PS178, PS100, PS102, PS123, PS194 | PCE356, PCE357, PCE360, PCE361 | V1-Meets Plng Guide validation criteria | 350 |  | 340 | 340 | 130 | 121 | 266 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Investments included in 819# Subsystem Analysis |  | Analysis completed assuming 423# setpoint at Cummins Creek and 819# setpoint at Gerber | C4-V1 | Y |  | 350 | 130 | 121 | 266 | 102.1392 | 49
120 | ZTR1 | TP_HUMBOLDT | L126-137_EUREKA_167 | EUREKA LT L126A,C,D; L137A,C; 1313-01 |  | 18 | PS101, PS103, PS104, PS122, PS124, ZTR1PS702 | PCE349, PCE350, PCE351, PCE352, PCE362, PCE363 | V1-Meets Plng Guide validation criteria | 167 |  | 161 | 159 | 90 | 150 | 149 | C2-NOP can be lowered to MOP-20 now | 140 | 138 |  |  | This system currently has excess capacity with Evergreen Pulp off. | C2-V1 | Y |  | 167 | 90 | 150 | 149 | 27.2323 | 28.7432
123 | ZTR1 | TP_HUMBOLDT | L137D_GIUNTOLI_250 | 10" Line from Arcata Reg to Giuntoli | Arcata Reg OD082630 V-26, 27, 30, 31 | 3.1 | PS125 | PCE345, PCE346 | V1-Meets Plng Guide validation criteria | 250 |  | 245 | 233 | 90 | 119 | 223 | C2-NOP can be lowered to MOP-20 now | 118 | 215 |  |  | Analysis completed assuming 350# setpoint at Tompkins Hill, 423# setpoint at Cummins Creek and 819# setpoint at Gerber | C2-V1 |  | Y | 250 | 90 | 119 | 223 | 88.8585 | 23.4761
124 | ZTR1 | TP_HUMBOLDT | 1310/1311_LOLETA_170 | 2 DFM's fed fro Tompkins Hill serving Loleta and Fernbridge | Tompkins Hill OD183697 V-60, 61, 62, 63 | 3.5 | ZTR1PS703, ZTR1PS704 | PCE358, PCE359 | V1-Meets Plng Guide validation criteria | 170 |  | 166 | 160 | 90 | 153 | 160 | C2-NOP can be lowered to MOP-20 now | 132 | 140 |  |  | *High APD min pressure due to low flow and elevation change. | C2-V1 | Y |  | 170 | 90 | 153 | 160 | 26.399 | 15.8654
126 | ZTR1 | TP_HUMBOLDT | 1001_REDBLUFF_470 | Rawson Road DFM serving Red Bluff West, Pactiv, and Neo Power | Red Bluff & Diamond National Primary OD082621 V-4, 5, 6, 7 | 3.4 | PS558 | ZTR1PCE800 | V1-Meets Plng Guide validation criteria | 470 | DWG 086868 lists 1001-02 as 911# MOP, GIS lists this pipe as 1001-01 | 458 | 455 | 110 | 343 | 433 | C2-NOP can be lowered to MOP-20 now | 332 | 425 |  |  |  | C2-V1 |  |  | 470 | 110 | 343 | 433 | 49.4497 | 16.0014
127 | ZTR1 | TP_CHICO | 1027_OROVILLE_110 | Oroville 110# DFM | 5th & Pomona OD0800188 V-8, 9; Lincoln & Oro Dam OD0800187 V-4, 5 | 1.9 | ZTR1PS705, ZTR1PS706 | ZTR1PCE802, ZTR1PCE803 | V1-Meets Plng Guide validation criteria | 110 |  | 105 | 102 | 85 | 96 | 92 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 91 | 87 | 3800ft of 6-in Steel Reinforcement | $900,000 | 1400ft of the 3800ft is on the 2012/13 Investment Plan. Modeling L177A Investments required for model balance. | C3-V1 | Y |  | 110 | 85 | 96 | 92 | 59.159 | 74.5846
128 | ZTR1 | TP_CHICO | 1027_OROVILLE_235 | Oroville 235# DFM | Richvaley Y OD081499 V-28, 30, 32 | 14.3 | ZTR1PS707, ZTR1PS708, ZTR1PS709, ZTR1PS710, ZTR1PS711, ZTR1PS712, ZTR1PS713 | PCE377, PCE378 | V1-Meets Plng Guide validation criteria | 235 |  | 217 | 217 | 140 | 169 | 142 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  | Required Investments are on L50A Subsystem and L177A Subsystem |  | Analysis assumed Fell Station and Richvale Y winter operations are unavailable due to 5/20 on Sac LT System and extensive Investments have been made on L050A and L177A | C4-V1 | Y |  | 235 | 140 | 169 | 142 | 74.8463 | 98.4168
129 | ZTR1 | TP_CHICO | 1004_ORLAND_490 | Orland 490# DFM from Primary to Secondary | Orland Primary OD082434 V-20, 21, C | 6.2 | PS555, ZTR1PS714 | ZTR1PCE804 | V1-Meets Plng Guide validation criteria | 490 |  | 400 | 387 | 130 | 386 | 385 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 490 | 130 | 386 | 385 | 40.8172 | 41.1626
130 | ZTR1 | TP_CHICO | 1004_ORLAND_170 | Orland 170# DFM from Secondary to Tertiary | Orland Secondary OD0800192 V-3, 4, 5, 6 | 1.6 | PS556 | ZTR1PCE805 | V1-Meets Plng Guide validation criteria | 170 |  | 100 | 100 | 78 | 97 | 95 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 170 | 78 | 97 | 95 | 85.4269 | 87.1099
131 | ZTR1 | TP_CHICO | L209/128_WILLOWS_479 | Manville - Willows - Ordbend 479# Line | Johns Manville Meter & Reg OD085542 V-3, 6, 10, 13 | 17 | ZTR1PS715, ZTR1PS716, ZTR1PS717 | PCE41, PCE42 | V2B-Incomplete validation - results suspect | 479 |  | 455 | 450 | 90 | 153 | 400 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | October Peak Nut Drying Season, No Load file or validation yet completed. | C1-V2B |  |  | 479 | 90 | 153 | 400 | 93.0835 | 31.3729
132 | ZTR1 | TP_CHICO | 1022_ARTOIS_200 | DFM serving Artois from Jacinto (L128) 200# | Jacinto Reg OD082893 V-25, 29, 30, 31 | 3 | ZTR1PS718 | PCE372, PCE373 | V2B-Incomplete validation - results suspect | 200 |  | 175 |  | 80 |  |  | C1-Existing NOP offset is 20 psi or more |  |  |  |  | Partially Built Model is not validated | C1-V2B |  |  | 200 | 80 | 0 | 0 | 119.0476 | 119.0476
133 | ZTR1 | TP_CHICO | 1017_PARADISE_200 | DFM from Paradise Primary to Secondary | Paradise Primary OD0800095 V-R1, R2, R3, R4 | 1.1 | PS557 | PCE806 | V1-Meets Plng Guide validation criteria | 200 |  | 190 | 187 | 150 | 183 | 182 | C2-NOP can be lowered to MOP-20 now | 172 | 171 | See L177A Subsystem |  | Assumes all investments on L177A are completed. | C2-V1 | Y |  | 200 | 150 | 183 | 182 | 37.2057 | 39.2914
134 | ZTR1 | TP_CHICO | L177_CHICO_819 | All Stations will flow wide open from Gerber Compressor to 5th & Pomona. So this subsystem encompasses many of the downstream subsystems: L177B_CHICO_469, L136_CHICO_550, L50_CHICO_400, 1027_OROVILLE_235 | Gerber Compressor OD284543 V-27, 28; Fell Reg & Oderizer OD082551 V-21, 22, 24, 25; Grape Way OD086447 V-4, 5, 8, 9; Butte Station OD284095 V-8, 9, 10, 11, 16, 17, 18, 19; Richvaley Y OD081499 V-28, 30, 32 | 100 | PS21, PS22, PS121, PS149, PS172, PS173, PS174, PS175, PS179, PS180, PS206, PS207, PS208, PS310, PS544, ZTR1PS719, ZTR1PS721, ZTR1PS722, ZTR1PS723 | PCE39, PCE368, PCE369, PCE376, PCE377, PCE378, PCE49, PCE50, ZTR1PCE807, ZTR1PCE808 | V1-Meets Plng Guide validation criteria | 618 | CROP Reduction from 819# to 618#. CROP may or may not be raised in 2012 depending on Thomes Creek Crossing Replacement. | 618 | 618 | 140 | 148 | 0 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 0 | 19 Miles L177A 16" Parallel from Corning Northdome (MP29.09) to Hamilton City Tap (MP9.88). 3 Miles of L050A 8" Parallel between Butte College Tap (V-37.42) and Richvale Y (MP 27.82). Rebuild Butte L177 Regs to have full opening stand-by run. Rebuild R | $9,700,000 | During current CROP, system relies heavily on support from L169B (Fell) and L050A South (Richvale Y). This analysis did not include any support from L169B or L050A as this may not be available if the 5/20 setpoint offset is implemented on the Sacramento | C4-V1 | Y |  | 618 | 140 | 148 | 0 | 99.3641 | 105.4095
135 | ZTR1 | TP_CHICO | L50_CHICO_400 | L50 from Butte Station to Richvale Y, including L50B to Paradise | Butte Station OD 284095 V-8, 9, 10, 11 | 33 | ZTR1PS723, PS544, PS557 | ZTR1PCE807, ZTR1PCE808 | V1-Meets Plng Guide validation criteria | 400 |  | 390 | 390 | 180 | 172 | 0 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 0 | See L177 Subsystem |  | Butte L136 is normally modeled at 390, L177 is modeled at 384: New Analysis utilizes 380/374. Pmin Design of 180# required for the Oroville 235# system to maintain 140#. Model does not include support from L50A South from Richvale as this support may not | C4-V1 | Y |  | 400 | 180 | 172 | 0 | 102.2069 | 125.3918
138 | ZTR1 | TP_CHICO | 1019_HAM-CITY_250 | DFM serving Prune Dryer south of Hamilton City | Hamilton City Regulator OD082877 V-56, 57, 60, 61 | 2.5 | PS551 | ZTR1PCE813 | V3-Insufficient P data to complete validation | 250 |  | 235 | 230 | 90 | 229 | 230 | C2-NOP can be lowered to MOP-20 now | 224 | 229 |  |  | Modeled 70 Mcfh Summer Prune Drying Load at Verschagin's. Pressure should be recorded at Vershagin's for July 1 - Sep 30 to validate model. | C2-V3 |  |  | 250 | 90 | 229 | 230 | 18.4908 | 17.6471
139 | ZTR1 | TP_REDDING | 1042_MCARTHUR_525 | DFM fed from L400, serving Fall River and McArthur |  | 7.5 | PS554 | ZTR1PCE814 | V3-Insufficient P data to complete validation | 525 | The MAOP is 911-960 psig for all of the pipe segments, not sure what the limiting factor is causing the MOP to be 525 psig. | 485 | 475 | 90 | 247 | 193 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | This DFM is part of the NV_FallRiver_Macarthur_H model. | C1-V3 |  |  | 525 | 90 | 247 | 193 | 80.2228 | 89.1042
140 | ZTR1 | TP_CHICO | 1009_MILLS-ORCHARD_200 | DFM fed from L177A MP9.88 to Mills Orchard and Sunsweet Dryers | Mills Orchard Primary OD0800189 V-2, 4, 5, 7 | 1.9 | ZTR1PS720 | ZTR1PCE815 | V3-Insufficient P data to complete validation | 200 |  | 180 | 170 | 90 | 163 | 170 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | Summer Prune Drying Load. | C1-V3 |  |  | 200 | 90 | 163 | 170 | 42.1034 | 34.7962
142 | HxFe | TP_KERN | HXFEPS702 | Ridgecrest | Ridgecrest Primary Reg Sta | 13.35 | HXFEPS702, HXFEPS706 | PS313 | V1-Meets Plng Guide validation criteria | 400 | GIS | 380 | 380 | 250 | 264 | 213 | C1-Existing NOP offset is 20 psi or more | 264 | 213 |  |  | While this has no immediate impact on customers, it does reduce the capacity for future expansion that is currently being offered to 2 industrial customers. | C1-V1 | Y |  | 400 | 250 | 264 | 213 | 92.6195 | 117.5703
143 | HxFe | TP_KERN | HXFEPS701 | Down Stream of the West End Reg Station | West End | 3.62 | HXEFPS701 | PS294 | V1-Meets Plng Guide validation criteria | 240 | GIS | 230 | 230 | 120 | 226 | 230 | C2-NOP can be lowered to MOP-20 now | 216 | 220 |  |  | While this has no immediate impact on customers, it does reduce the capacity for future expansion that is currently being offered to 2 industrial customers. | C2-V1 |  |  | 240 | 120 | 226 | 230 | 15.1019 | 10.8796
144 | HxFe | TP_KERN | PCE266 | Down Stream of the Trona Tap | Floats off line 300 | 64.65 | PS294, PS313 | PS295 | V1-Meets Plng Guide validation criteria | 700 | GIS | 650 | 650 | 450 | 600 | 578 | C1-Existing NOP offset is 20 psi or more | 600 | 578 |  |  | While this has no immediate impact on customers, it does reduce the capacity for future expansion that is currently being offered to 2 industrial customers. | C1-V1 | Y |  | 700 | 450 | 600 | 578 | 45.2174 | 54.2317
145 | HxFe | TP_KERN | PCE286 | Down Stream of the Lucerne Valley Tap | Floats off line 300 | 38.78 | PS297 | PS297 | V1-Meets Plng Guide validation criteria | 573 | GIS | 453 | 453 | 250 | 490 | 453 | C1-Existing NOP offset is 20 psi or more | 490 | 453 |  |  |  | C1-V1 |  |  | 573 | 250 | 490 | 453 | 33.1901 | 46.3155
146 | HxFe | TP_KERN | PCE296 | Down Stream of the Riverside Reg | Riverside Reg | 19.51 | PS298 | PS299 | V1-Meets Plng Guide validation criteria | 550 | GIS | 435 | 435 | 250 | 423 | 434 | C1-Existing NOP offset is 20 psi or more | 423 | 434 |  |  |  | C1-V1 | Y |  | 550 | 250 | 423 | 434 | 51.4879 | 47.56
147 | HxFe | TP_KERN | HXFEPS703 | Down Stream of the Hinkley Tap | Floats off line 300 | 24.29 | PS298 | PS298 | V1-Meets Plng Guide validation criteria | 861 | GIS | 500 | 500 | 450 | 466 | 500 | C1-Existing NOP offset is 20 psi or more | 466 | 500 |  |  |  | C1-V1 | Y |  | 861 | 450 | 466 | 500 | 97.28 | 91.1845
148 | HxFe | TP_KERN | HXFEPS704 | Pioneer_DFM | Bakersfield Reg Sta | 5.49 | HXFEPS704 | HXFEPCE800 | V1-Meets Plng Guide validation criteria | 240 | GIS | 210 | 210 | 90 | 176 | 163 | C1-Existing NOP offset is 20 psi or more | 176 | 163 |  |  |  | C1-V1 |  |  | 240 | 90 | 176 | 163 | 53.7859 | 62.6889
149 | HxFe | TP_KERN | HXFEPS700 | 142S Down Stream of Brundage & V | Brundage&V AND Bakersfield Reg | 2.53 | PS136 | PS136 | V1-Meets Plng Guide validation criteria | 300 | GIS | 290 | 290 | 200 | 289 | 280 | C2-NOP can be lowered to MOP-20 now | 275 | 270 |  |  |  | C2-V1 | Y |  | 300 | 200 | 289 | 280 | 12.958 | 23.2
150 | HxFe | TP_KERN | PCE419 | 142S Down Stream of Gosford | Gosford Station | 9.29 | PS135 | PS135 | V1-Meets Plng Guide validation criteria | 478 | GIS | 465 | 465 | 220 | 432 | 376 | C2-NOP can be lowered to MOP-20 now | 423 | 361 |  |  |  | C2-V1 | Y |  | 478 | 220 | 432 | 376 | 23.2447 | 48.3708
151 | HxFe | TP_KERN | PCE223 | 142N | Bakersfield Tap | 36.03 | PS134, PS314, PS315, PS316, PS317, PD318, PS319 | PS134 | V1-Meets Plng Guide validation criteria | 475 | GIS | 465 | 465 | 410 | 418 | 420 | C2-NOP can be lowered to MOP-20 now | 408 | 411 |  |  |  | C2-V1 | Y |  | 475 | 410 | 418 | 420 | 88.485 | 85.5715
152 | TCQ2 | TP_EBAY | DFM_2404_85 | 85 psig DFM near Enterprise in Newark - Salt Dryers | Timber Reg Station; RF39 | 3.1 | tcq2PS700 | tcq2PCE801 | V3-Insufficient P data to complete validation | 85 |  | 80 | 80 | 75 | 77.59 | 79.58 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 62.1 | 64.48 | RF03/RF04 Reg stations replumbed with new regs. | $160,000 | Two Distribution Regulator sets at 50 psig replumbed. May consider turning into distribution main. | C3-V3 |  |  | 85 | 75 | 77.59 | 79.58 | 75.2995 | 55.7515
153 | TCQ2 | TP_EBAY | DFM_3010_100 | Wilbur DFM | Wilbur Reg Station | 0.75 | tcq2PS709 | tcq2PCE814 | V3-Insufficient P data to complete validation | 100 |  | 95 | 95 | 85 | 65.47 | 95 | C2-NOP can be lowered to MOP-20 now | 65.47 | 95 |  |  | Pipeline Engineering is working with the only elevated customer on this line to test a 20 psig reduction. Proposal to eliminate regulation from Pipeline Engineering. | C2-V3 |  |  | 100 | 85 | 65.47 | 95 | 205.8983 | 35.1351
154 | TCQ2 | TP_EBAY | SP3_System_600 | Stanpac 3 System from Antioch to Los Medanos | Antioch Terminal - Control Valves | 14.4 | PS636, PS196, PS644 | PCE73, PCE74, PCE75 | V1-Meets Plng Guide validation criteria | 600 |  | 600 | 590 | 430 | 546.36 | 560.71 | C2-NOP can be lowered to MOP-20 now | 541.72 | 559.38 |  |  | Impacts Los Medanos Injection Capability | C2-V1 | Y |  | 600 | 430 | 546.36 | 560.71 | 35.1175 | 26.0447
155 | TCQ2 | TP_EBAY | Line_105_250 | 250 psig Line 105 from Irvington to Enrico Station | Irvington Station | 16 | PS43, PS42, PS41 | PCE163 | V1-Meets Plng Guide validation criteria | 250 |  | 245 | 245 | 160 | 237.95 | 235.14 | C2-NOP can be lowered to MOP-20 now | 222.49 | 219.49 |  |  |  | C2-V1 | Y |  | 250 | 160 | 237.95 | 235.14 | 15.9344 | 19.5371
156 | TCQ2 | TP_EBAY | Line_105B_397 | 397 psig Line 105B Herrmann to San Pablo | Hermann Station - Control Valves | 17.6 | PS38, PS39, PS389, PS390 | PCE332 | V1-Meets Plng Guide validation criteria | 397 | Recent reduction to 397 due to Chevron service downrate to 397 psig | 380 | 380 | 320 | 356.19 | 378.16 | C2-NOP can be lowered to MOP-20 now | 342.01 | 370.21 |  |  | May impact Crocket Cogen and Chevron. Currently set at 380 psig. | C2-V1 | Y | Y | 397 | 320 | 356.19 | 378.16 | 55.6751 | 26.4522
157 | TCQ2 | TP_EBAY | DFM 3004 | Port Costa Feeder from Stanpac 3 | Port Costa Reg Station | 1.2 | PS388 | PCE323, PCE324 | V2B-Incomplete validation - results suspect | 315 |  | 95 | 95 | 80 | 96.31 | 96.29 | C1-Existing NOP offset is 20 psi or more | 96.31 | 96.29 |  |  |  | C1-V2B |  |  | 315 | 80 | 96.31 | 96.29 | 96.9021 | 96.9063
158 | TCQ2 | TP_EBAY | Line_105_150 | 150 psig Oakland System | Fairway Station, Enrico Station, East Bay PLS (All Control Valves) | 47 | PS40, PS44, PS148, PS37, PS391 | PCE325, PCE326, PCE327, tcq2PCE800 | V1-Meets Plng Guide validation criteria | 121 | Currently under a TROP of 121 psig since December 2011. | 121 | 145 | 90 | 115.85 | 116.92 | C2-NOP can be lowered to MOP-20 now | 112.74 | 113.44 |  |  | Berkeley Cogen, California Oils Cogen, NCPA Cogen might be impacted due to lower than normal delivery pressure | C2-V1 | Y |  | 121 | 90 | 115.85 | 116.92 | 18.6482 | 14.8404
159 | TCQ2 | TP_EBAY | DFM_0141-01_110 | C&H Sugar DFM | Crockett Station | 23.2 | tcq2PS705 | PCE319, PCE320 | V3-Insufficient P data to complete validation | 110 |  | 100 | 100 | 90 | 89.97 | 90.02 | C1-Existing NOP offset is 20 psi or more | 89.97 | 90.02 |  |  |  | C1-V3 | Y |  | 110 | 90 | 89.97 | 90.02 | 100.135 | 99.91
160 | TCQ2 | TP_EBAY | Line_153_336 | 336 psig Line 153 from Irvington to Marina Station | Irvington Station | 18 | PS145, PS393, PS147 | PCE163, PCE165, PCE166, PCE167 | V1-Meets Plng Guide validation criteria | 336 | Current under a CROP. Reduced 20% from old 420 psig MAOP | 335 | 306 | 275 | 214.23 | 204.34 | C1-Existing NOP offset is 20 psi or more | 227.24 | 215.53 |  |  | Line under a 20% crop. New Russell City Power Plant may push for restoration of previous MAOP | C1-V1 | Y |  | 336 | 275 | 214.23 | 204.34 | 179.7685 | 190.8754
161 | TCQ2 | TP_EBAY | Line_153_246 | 246 psig Line 153 from Marina Station to the Oakland PLS | Marina Station | 10 | PS145 | PCE328 | V1-Meets Plng Guide validation criteria | 246 |  | 235 | 235 | 180 | 160.14 | 153.1 | C2-NOP can be lowered to MOP-20 now | 165.03 | 154.99 |  |  |  | C2-V1 | Y | Y | 246 | 180 | 160.14 | 153.1 | 124.0261 | 131.8694
162 | TCQ2 | TP_EBAY | Line 191-1_268 | Line 191-1 from C Street to Plaza station (pipe continues to Reliez station) | C Street Station, Martinez | 10.5 | PS201, PS202, PS203, PS204, PS205 | tcq2PCE806 | V1-Meets Plng Guide validation criteria | 268 |  | 258 | 258 | 190 | 177.27 | 176.38 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 233.1 | 224.75 |  | TBD |  | C3-V1 | Y | Y | 268 | 190 | 177.27 | 176.38 | 113.0874 | 113.9685
163 | TCQ2 | TP_EBAY | DFM_2402_01 | 150 psig Castro Valley DFM | C Street Station | 3.87 | PS392 | tcq2PCE804 | V1-Meets Plng Guide validation criteria | 160 | MAOP sheet says segments qualified for 250 psig. Segment may be U/S of regulation. | 155 | 155 | 90 | 126 | 114 | C3-NOP can be lowered to MOP-10. Investments needed for MOP-20. | 106.55 | 85.38 | Replace RH12 with larger regulation | $80,000 | May not even need this job as 85 psig may be sufficient due to networked distribution. | C3-V1 |  |  | 160 | 90 | 126 | 114 | 55.5657 | 72.0229
164 | TCQ2 | TP_EBAY | DFM_2403_125 | 125 psig Niles DFM from Decoto to Mowry | Niles Reg Station, RF38 | 4 | tcq2PS701 | tcq2PCE802 | V1-Meets Plng Guide validation criteria | 125 |  | 120 | 120 | 90 | 96.38 | 97.03 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 77.57 | 78.37 |  | See Note | Current 2013 Uprate job will resolve this issue. | C4-V1 |  |  | 125 | 90 | 96.38 | 97.03 | 84.1979 | 82.5273
165 | TCQ2 | TP_EBAY | DFM_3001-01_170 | Moraga DFM 3001-01 | Reliez Station | 4.15 | tcq2PS706 | PCE315, PCE316 | V1-Meets Plng Guide validation criteria | 170 |  | 170 | 165 | 90 | 113.02 | 51.79 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 88 | 34.04 |  | See Note | Current 2013 Reinforcement Job will resolve this issue | C4-V1 |  |  | 170 | 90 | 113.02 | 51.79 | 77.5312 | 126.0471
166 | TCQ2 | TP_EBAY | DFM_3002_170 | Glorietta DFM | Reliez Station | 7.18 | PS201, tcq2PS2707 | PCE313, PCE314 | V1-Meets Plng Guide validation criteria | 182 | Line 191S is part of this DFM from Plaza Station to Reliez Station | 177 | 177 | 90 | 107.08 | 75.37 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 109.87 | 56.77 |  | TBD |  | C4-V1 | Y |  | 182 | 90 | 107.08 | 75.37 | 86.5484 | 109.6682
167 | TCQ2 | TP_EBAY | DFM_3006/3008_170 | Concord DFM | Vine Hill Station, Concord Meter Station | 13.67 | PS379, tcq2PS708 | PCE317, PCE318, PCE309, PCE310 | V1-Meets Plng Guide validation criteria | 170 |  | 165 | 165 | 90 | 107.24 | 100.12 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 102.3 | 93.54 |  | TBD |  | C4-V1 |  |  | 170 | 90 | 107.24 | 100.12 | 83.6518 | 90.7499
168 | TCQ2 | TP_EBAY | DFM_3004-01_338 | Foster Wheeler Cogen DFM | Foster Wheeler Meter Station off of SP3 | 0.98 | PS383 | PCE311, PCE312 | V2B-Incomplete validation - results suspect | 338 |  | 320 | 320 | 300 | 312.16 | 320.01 | C2-NOP can be lowered to MOP-20 now | 310.11 | 318.01 |  |  | LC Delivery pressure impact: Foster Wheeler Cogen. Currently at 320 psig delivery pressure | C2-V2B |  |  | 338 | 300 | 312.16 | 320.01 | 69.2961 | 48.8269
169 | TCQ2 | TP_EBAY | DFM_3010-01_338 | Antioch Vierra DFM - Can be tied to Line 191_338 psig system | Antioch/Vierra Reg station | 0.68 | PS387 | tcq2PCE809 | V3-Insufficient P data to complete validation | 338 |  | 320 | 320 | 130 | 320 | 320.16 | C2-NOP can be lowered to MOP-20 now | 318 | 318.16 |  |  | Pipeline is proposing absorbing DFM_3010_100 into this system. | C2-V3 | Y |  | 338 | 130 | 320 | 320.16 | 12.1672 | 12.0619
170 | TCQ2 | TP_EBAY | DFM_3012_172 | Dow Chemical and USS DFM | Pittsburg Town Station | 2.18 | PS711, PS710 | tcq2PCE815 | V1-Meets Plng Guide validation criteria | 172 |  | 165 | 165 | 100 | 162.74 | 165.08 | C2-NOP can be lowered to MOP-20 now | 147.51 | 150.07 |  |  |  | C2-V1 |  |  | 172 | 100 | 162.74 | 165.08 | 15.8277 | 11.9107
171 | TCQ2 | TP_EBAY | DFM_3014-01_338 | Nichols DFM Tapped off of SP3 | Nichols Reg Station | 1.56 | PS384 | tcq2PCE810 | V3-Insufficient P data to complete validation | 338 |  | 255 | 255 | 100 | 257.6 | 257.6 | C1-Existing NOP offset is 20 psi or more | 237.38 | 237.38 |  |  |  | C1-V3 | Y |  | 338 | 100 | 257.6 | 257.6 | 45.9367 | 45.9367
172 | TCQ2 | TP_EBAY | DFM_3019_275 | Rhodia_DFM | Shell Reg Station DIRC29 | 1.03 | tcq2PS712 | tcq2PCE816 | V3-Insufficient P data to complete validation | 95 |  | 90 | 90 | 90 | 90.05 | 90.15 | C2-NOP can be lowered to MOP-20 now | 90.05 | 90.15 |  |  | Potential LC pressure impact: Rhodia | C2-V3 |  |  | 95 | 90 | 90.05 | 90.15 | 99.0268 | 97.0786
173 | TCQ2 | TP_EBAY | Line SP3_405 | Stanpac 3 from Los Medanos PLS to Franklin Canyon PLS | Los Medanos PLS - Control Valves | 15 | PS637, PS645 | PCE90, PCE91 | V1-Meets Plng Guide validation criteria | 405 |  | 395 | 395 | 380 | 367.11 | 379.52 | C2-NOP can be lowered to MOP-20 now | 357.38 | 373.27 |  |  | Large Customer Pressure Impacts: Chevron Refinery | C2-V1 |  | Y | 405 | 380 | 367.11 | 379.52 | 149.0713 | 101.8577
174 | TCQ2 | TP_EBAY | Line SP3_380 | 380 psig Stanpac 3 from Franklin Canyon to San Pablo Station | Franklin Canyon PLS | 9.4 | PS638, PS639 | PCE321, PCE322 | V1-Meets Plng Guide validation criteria | 380 |  | 370 | 360 | 320 | 360.87 | 360.94 | C2-NOP can be lowered to MOP-20 now | 357.01 | 360.94 |  |  | Not currently used, but will be backup service for Chevron | C2-V1 |  |  | 380 | 320 | 360.87 | 360.94 | 33.7449 | 33.6246
175 | TCQ2 | TP_EBAY | Line_191_338 | 338 psig Line 191 system (includes parts of SP3 and SP5) | Antioch Terminal and SP3/191 Crosstie (control valves) | 34.2 | PS197, PS198, PS199, PS643, PS200, PS385 | PCE81, PCE84, PCE94, PCE95, PCE96 | V1-Meets Plng Guide validation criteria | 338 |  | 335 | 335 | 90 | 195.33 | 90 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | 137.8 | 90 | Parallel/Replace 2 miles of Danville DFM | $5,280,000 | Large reinforcement necessary due to reductions on three separate interelated subsystems. Everything comes back to Danvile DFM | C4-V1 | Y |  | 338 | 90 | 195.33 | 90 | 71.6858 | 100
176 | TCQ2 | TP_EBAY | DFM_2408-01 | Stanley DFM in Pleasanton | Isabel Staiton/ Santa Rita Station | 8.83 | PS396 | PCE329, PCE330 | V1-Meets Plng Guide validation criteria | 160 |  | 155 | 155 | 90 | 139.83 | 136.82 | C2-NOP can be lowered to MOP-20 now | 123.14 | 119.75 |  |  |  | C2-V1 | Y |  | 160 | 90 | 139.83 | 136.82 | 34.5575 | 39.3159
177 | TCQ2 | TP_EBAY | DFM_2408-05_497 | Dublin and Blackhawk DFM's | Bay Area Loop - Control Valves | 17.22 | PS397, PS399 | PCE329 | V1-Meets Plng Guide validation criteria | 497 | MOP depends on Line 131/114 MOP (Bay Area Loop) | 400 | 400 | 90 | 264.16 | 163.52 | C1-Existing NOP offset is 20 psi or more | 264.19 | 163.59 |  |  | Floats off Line 131. Always 20 psig under MAOP | C1-V1 |  |  | 497 | 90 | 264.16 | 163.52 | 74.1824 | 92.1984
178 | TCQ2 | TP_EBAY | DFM_2805-05_215 | San Ramon DFM | Altimrano/Arnold reg station | 7.92 | PS398 | tcq2PCE808 | V1-Meets Plng Guide validation criteria | 215 |  | 210 | 210 | 90 | 152.88 | 147.9 | C2-NOP can be lowered to MOP-20 now | 132.45 | 126.84 |  |  |  | C2-V1 |  |  | 215 | 90 | 152.88 | 147.9 | 59.9415 | 63.8704
179 | TCQ2 | TP_EBAY | DFM_2403_240 | 240 psig Isabel DFM 2403-02 and 2403-01 | Smith Reg Station, RF-41 | 3.71 | tcq2PS702 | tcq2PCE803 | V2B-Incomplete validation - results suspect | 240 |  | 220 | 220 | 90 | 211.35 | 207.73 | C1-Existing NOP offset is 20 psi or more | 211.35 | 208.03 |  |  |  | C1-V2B |  |  | 240 | 90 | 211.35 | 207.73 | 26.1236 | 29.1884
180 | TCQ2 | TP_EBAY | DFM 0107.02 | 160 psig Coral/Tunis DFM (near Oakland Airport) | Coral and Tunis Regulator Station | 0.75 | tcq2PS703 | tcq2PCE805 | V2B-Incomplete validation - results suspect | 160 |  | 155 | 155 | 90 | 145.14 | 141.72 | C2-NOP can be lowered to MOP-20 now | 129.08 | 125.26 |  | See Note | Validation Data required. | C2-V2B | Y |  | 160 | 90 | 145.14 | 141.72 | 25.9107 | 31.5168
181 | TCQ2 | TP_EBAY | DFM_CCPP | Contra Costa Power Plant DFM | Antioch Terminal valves 155, 156, 157, 173 | 1 | tcq2PS704 | PCE82, PCE83 | V3-Insufficient P data to complete validation | 195 |  | 180 | 180 | 155 | 180 | 160 | C2-NOP can be lowered to MOP-20 now | 175 | 155 |  | See Note | LC Delivery Pressure impact. Genon PP DFM is currently 15 psig below MOP. Under high demand (6 Mmcfh) Lo Lo alarms will be breached. | C2-V3 |  |  | 195 | 155 | 180 | 160 | 40.1786 | 88.75
182 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY |  |  | PS93, PS168, PS583, PS586, PS582, PS85, PS85, PS563 | PCE404, DRJ4PCE820 | V2B-Incomplete validation - results suspect | 500 |  | 493 | 490 | 90 |  | 452 | C2-NOP can be lowered to MOP-20 now |  | 437 | none |  | DRJ4: This analysis only looks at a lateral off of the L123_L173_500, and should be treated as part of that analysis. Therefore, the pressure should NOT be reduced until further analysis. | C2-V2B | Y |  | 500 | 90 | 0 | 452 | 103.3485 | 18.8905
183 | MUMY | TP_SACRAMENTO_VALLEY | 0605_GALT_395 | Galt Primary Reg Sta (PCE) and Thornton Reg Sta (PCE) to the town of Galt at the inlet to DR R_SCSTA_B07. |  | 9.54 | PS571 | DRJE802, DRJ4PCE803 | V1-Meets Plng Guide validation criteria | 395 | The Galt DFM is supplied by two regulator stations, Galt Primary at 360 psig and Thornton Meter Station at 355 psig | 360 | 360 | 90 | 250 | 165 | C1-Existing NOP offset is 20 psi or more |  |  |  |  | CWD was Res Pmin 110% was estimated and not modeled. | C1-V1 |  |  | 395 | 90 | 250 | 165 | 63.2246 | 87.0712
184 | MUMY | TP_SACRAMENTO_VALLEY | 0606_ELK_GROVE_150 | Elk Grove Emergency Backfeed Sta (PCE) to the inlet to DR R_SRSTA-B17. |  | 12.55 | drj4PS701 | DRJ4PCE804 | V1-Meets Plng Guide validation criteria | 150 |  | 145 | 145 | 80 | 133 | 127 | C2-NOP can be lowered to MOP-20 now | 116 | 112 |  |  |  | C2-V1 |  |  | 150 | 80 | 133 | 127 | 29.882 | 39.5714
185 | MUMY | TP_SACRAMENTO_VALLEY | 0609_FLORIN_150 | Florin Rd & Munson Way Reg Sta (PCE) to DFM 0609. |  | 2.03 | drj4PS702 | DRJ4PCE808 | V1-Meets Plng Guide validation criteria | 150 |  | 147 | 147 | 90 | 98 | 74 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 |  |  | 150 | 90 | 98 | 74 | 89.5556 | 118.2222
186 | MUMY | TP_SACRAMENTO_VALLEY | 0611_MATHER_240 | 20th Av & Martin Luther King Jr Blvd Reg Sta (PCE) to Blue Ravine Reg Station in Folsom - Mather DFM system serving south Sacramento and Rancho Cordova. The Pmin Design Shown is in Folsom at DR R_SCSTA-51 which receives backfeed support from the Folsom D |  | 44.74 | drj4PS703 | DRJ4PCE809 | V1-Meets Plng Guide validation criteria | 240 |  | 235 | 233 | 90 |  |  | C2-NOP can be lowered to MOP-20 now |  |  |  |  | DRJ: Has a backfeed from Folsom DFM, and Folsom DFM is not constrained. Need a pressure recorder at the end of the Douglas-Sunrise DFM to Validate | C2-V1 |  |  | 240 | 90 | 0 | 0 | 116.3636 | 116.3636
187 | MUMY | TP_SACRAMENTO_VALLEY | 0613_SAC_FLOATER_260 | Sacramento Gas Load Center (PCE) to North Sacramento Holder and North Sacramento 180 psig DFM. Provides the lead supply to the DFM to a secondary backup supply off of L119B/C. The North Sacramento Holder is operated during winter season morning peak hou |  | 6.24 | PS565 | PCE393, PCE394 | V3-Insufficient P data to complete validation | 260 |  | 250 | 250 | 90 | 195 | 165 | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 260 | 90 | 195 | 165 | 49.7059 | 67.8571
188 | MUMY | TP_SACRAMENTO_VALLEY | 0615_SAC_METRO_425 | El Centro Rd & Hwy 80 Reg Sta (PCE) to the Sacramento Metropolitan Airport. |  | 6.79 | drj4PS704 | DRJ4PCE801 | V1-Meets Plng Guide validation criteria | 425 |  | 410 | 390 | 90 | 275 | 246 | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 |  |  | 425 | 90 | 275 | 246 | 60.8607 | 69.6183
189 | MUMY | TP_SACRAMENTO_VALLEY | 0617_KIRBY_150 | Roseville Rd Reg Sta (PCE) to the inlet to DR R_SCSTA-A37. |  | 0.97 | drj4PS705 | PCE389 | V3-Insufficient P data to complete validation | 150 |  | 145 | 145 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 150 | 90 | 0 | 0 | 156.25 | 156.25
190 | MUMY | TP_SACRAMENTO_VALLEY | 0618_ANTELOPE_WALERGA_175 | Antelope Meter Sta (PCE) to Antelope at the inlet to DR . |  | 2.94 | drj4PS706 | PCE381,PCE382 | V3-Insufficient P data to complete validation | 175 |  | 170 | 170 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 175 | 90 | 0 | 0 | 135.96 | 135.96
191 | ANY3 | TP_SACRAMENTO_VALLEY | 0619_SOUTH_RIVER_150 | 0619-01: 150# (South River) Included in distribution model: ESDZONE_SA_WEST_SAC_H_W1112_APD_452_(MOP_MINUS_20_STUDY) |  | 1.21 | drj4PS707 | DRJ4PCE810 | V3-Insufficient P data to complete validation | 150 |  | 147 | 145 | 80 |  | 137 | C2-NOP can be lowered to MOP-20 now |  | 115 | none |  | SOURCE REG: WS-012 - System Configuration may change due to potential WRO relocation of 6" DFM ("Raley Landing" project). DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. | C2-V3 |  |  | 150 | 80 | 0 | 137 | 139.7516 | 23.1739
192 | ANY3 | TP_SACRAMENTO_VALLEY | 0621_ARMFIELD_190 | 0621-01: 190# (Teichert Modeled) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_CFD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) |  | 0.96 | drj4PS708 | DRJ4PCE811 | V3-Insufficient P data to complete validation | 190 |  | 180 | 180 | 80 |  | 131 | C2-NOP can be lowered to MOP-20 now | 117 |  | none |  | SOURCE REG: WO-16; CFD is controlling season. DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. Pac Coast Prod. Load was modified from LCSea from 900 mcfh to 600 mcfh to align better with AMR usage (60 psig delivery pressure). | C2-V3 |  |  | 190 | 80 | 0 | 131 | 121.5488 | 63.7677
193 | ANY3 | TP_SACRAMENTO_VALLEY | 0627_UCDAVIS_175 | 0627-01: 175# Davis Meter and Reg Sta (PCE) to UC Davis Campus at the inlet to DR R_SCDA-001. (AFTER 1st & A St MWC 47 job) Included in distribution model: ESDZONE_SA_DAVIS_H_W1112_CWD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) |  | 0.7 | drj4PS709 | PCE384, PCE385 | V3-Insufficient P data to complete validation | 175 |  | 170 | 168 | 85 | 133 |  | C2-NOP can be lowered to MOP-20 now | 113 |  | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE REG: DA-11; CWD is the controlling season Should validate system performance once PM 30882075 is constructed which will remove bottleneck and increase utilization out of DA- | C2-V3 |  |  | 175 | 85 | 133 | 0 | 55.2821 | 130.8761
194 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_240 | Lurline Rd Sta (PCE) to closed MAOP sdeparation valve V-5. Serves the town of Colusa and Sunsweet Driers. The Pmin Design shown is in Colusa at the inlet to DR R_SCC008 (55 psig Distr system). Lurline DFM Included in distribution model: 07-J07colusaAS |  | 4.2 | PS593 | DRJ4PCE812 | V2B-Incomplete validation - results suspect | 240 |  | 223 | 220 | 85 |  | 99 | C2-NOP can be lowered to MOP-20 now |  | 93 | none |  | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Min pressure is at node where future added load is applied near the end of the dfm | C2-V2B | Y |  | 240 | 85 | 0 | 99 | 114.3424 | 94.8864
195 | LRS3 | TP_SACRAMENTO_VALLEY | 0630_COLUSA_MERIDIAN_430 | Marysville Buttes Sta (PCE) to closed MAOP separation valve V-5. Colusa DFM Included in distribution model: 07-J07colusaASD_UTM_Qrc+20%+Noncore_452_MOP_MINUS_20_STUDY.MDB |  | 12.86 | drj4PS710 | DRJ4PCE813 | V2B-Incomplete validation - results suspect | 430 |  | 385 | 375 | 90 |  | 348 | C2-NOP can be lowered to MOP-20 now |  | 315 | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. The station feeding butte station reg is operated by Meridian | C2-V2B |  |  | 430 | 90 | 0 | 348 | 104.5814 | 36.0837
196 | LRS3 | TP_SACRAMENTO_VALLEY | 0632_WILLIAMS_180 | Williams Primary (PCE) to the town of Williams DR R_FM_SCWL04. Williams DFM Included in distribution model: 11-J11WILLIAMSCFD_UTM_45_MOP_MINUS_20_STUDY |  | 3.72 | PS597 | DRJ4PCE815 | V3-Insufficient P data to complete validation | 180 |  | 175 | 174 | 80 |  | 61 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 80 | 4,200 ft of 6" pipe starting at source | $2,646,000 | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Rice loads in fall are constraining loads. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost Guide Rev 4/16/2012 provided by GPS | C4-V3 |  |  | 180 | 80 | 0 | 61 | 124.6154 | 110.3038
197 | MUMY | TP_SACRAMENTO_VALLEY | 0635_WALNUT_GROWER_210 | West Beehive Bend Reg Sta (PCE) |  | 1.16 | drj4PS711 | DRJ4PCE824 | V3-Insufficient P data to complete validation | 210 |  | 200 | 200 | 90 | [8 empty] | V3 |  |  | 210 | 90 | 0 | 0 | 122.5 | 122.5
198 | LRS3 | TP_SACRAMENTO_VALLEY | 124C-1_BEALE_AFB_395 | Camp Far West Meter Sta (PCE) to Beale Air Force Base. Beale DFM Included in distribution model: ESDZONE_08-J08wheatbelAPD_UTM_45_MOP_MINUS_20_STUDY |  | 4.48 | PS97 | PCE402, PCE403 | V3-Insufficient P data to complete validation | 395 |  | 375 | 372 | 90 |  | 364 | C1-Existing NOP offset is 20 psi or more |  | 364 | none |  | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Already operating at MOP-20# | C1-V3 |  |  | 395 | 90 | 0 | 364 | 105.4757 | 15.906
199 | LRS3 | TP_SACRAMENTO_VALLEY | 1502_DIST10_120 | Magnolia Rd Sta (PCE) to DFM 1502. District 10 DFM north of Magnolia Rd Reg Station Included in distribution model: 10-J10mryASD_UTM_45_MOP_MINUS_20_STUDY |  | 5.11 | drj4PS713 | DRJ4PCE817 | V2B-Incomplete validation - results suspect | 120 |  | 115 | 112 | 70 |  | 74 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 70 | 2,400 ft of 6" pipe starting at source | $1,512,000 | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. 51# at end of DFM w/o reinf. Pmin = 70 for rice drier cust reg sets at end of DFM. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost | C4-V2B | Y |  | 120 | 70 | 0 | 74 | 151.5789 | 93.9368
200 | LRS3 | TP_SACRAMENTO_VALLEY | 1504_NICOLAUS_274 | Lincoln Jct (PCE) to the town of Lincoln DR R_SRSTA-602 and R_SRSTA-603. Lincoln DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY |  | 2.53 | PS579 | PCE405, PCE406 | V1-Meets Plng Guide validation criteria | 274 |  | 250 | 247 | 80 |  | 229 | C1-Existing NOP offset is 20 psi or more |  |  | none |  | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. Already operating at MOP-20#. Sierra & Sac models merged. Preesure points in dstr system to force balance does not effect this DFM capacity/pressures. | C1-V1 |  |  | 274 | 80 | 0 | 229 | 109.3191 | 32.9591
201 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L124B_1502_400 | Yuba City Holder (PCE) to Lincoln Jct - 400 psig system serving Marysville and subsystem 1504_NICOLAUS_274. The Pmin Design shown is in Lincoln at the inlet to Lincoln Jct. |  | 39.85 | PS18, PS95, PS575 | DRJ4PCE806 | V1-Meets Plng Guide validation criteria | 400 |  | 395 | 395 | 250 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 |  |  | 400 | 250 | 0 | 0 | 164.1026 | 164.1026
202 | MUMY | TP_SACRAMENTO_VALLEY | L050A_L151_250 | Gridley Jct (PCE) to Richvale Y and Yuba City Holder (PCE). Yuba City Holder is normally set as a secondary supply and not flowing into L050A. A CROP in place on L151, which is part of the subsystem, requires operating the subsystem in two HIS - Gridley |  | 51.66 | PS19, PS20, PS144, PS581 | PCE370, PCE371, PCE376 | V1-Meets Plng Guide validation criteria | 210 | A CROP is in place reducing the MOP from 250 psig to 210 psig, with the regulators set at 190 psig due to creep. | 190 | 190 | 90 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 210 | 90 | 0 | 0 | 122.5 | 122.5
203 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVN_412 | Las Vinas Sta (PCE) to BTU MLV 66.14. Serves South Sacramento. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B39 and DR R_SCSTA-B37. |  | 41.16 | PS52, PS53, PS54 | PCE61, PCE62 | V1-Meets Plng Guide validation criteria | 400 | A CROP is currently in place reducing the MOP from 410 to 400 psig. This is not expected to be cleared before the winter season. | 385 | 385 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V1 | Y |  | 400 | 90 | 0 | 0 | 105.3325 | 105.3325
204 | MUMY | TP_SACRAMENTO_VALLEY | L108_LVS_412 | Las Vinas Sta (PCE) to 8-mile Rd PLS (PCE). Supplies Turner Rd Sta and NCPA-Lodi. The Pmin Design shown is at Armstrong Rd at the inlet to DR R_LOHP77. |  | 10.3 | PS51 | PCE61, PCE62 | V1-Meets Plng Guide validation criteria | 400 | A CROP is currently in place reducing the MOP from 410 to 400 psig. This is not expected to be cleared before the winter season. | 385 | 385 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V1 | Y |  | 400 | 90 | 0 | 0 | 105.3325 | 105.3325
205 | MUMY | TP_SACRAMENTO_VALLEY | L108_SGLC_412 | Sacramento Gas Load Center (PCE) to closed BTU Separation valve V-66.14. Supplies South Sacramento area and subsystem 0611_MATHER_240. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609- |  | 15 | PS54 | PCE395, PCE396, PCE397 | V1-Meets Plng Guide validation criteria | 410 | MOP was lowered from 412 psig (MAOP) to 410 psig MOP per validation test that was done on L-108 (MP-61.66 Elk Grove Station to MP-74.50 Sac Load Center) on 1/8/09. | 385 | 385 | 180 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 410 | 180 | 0 | 0 | 123.8762 | 123.8762
206 | MUMY | TP_SACRAMENTO_VALLEY | L116_L119A_720 | Swingel Jct (PCE) to Sacramento Gas Load Center and North Sacramento Holder. Supplies North Natomas area, North Sacramento and subsystems L119B_L119C_0617_FOLSOM_500, 0613_SAC_FLOATER_260, L119D_0614_NSAC_180, and 0615_SAC_METRO_425. The Pmin Design show |  | 31.98 | PS82, PS83, PS68, PS70, PS71, PS72, PS166 | PCE398, PCE399 | V1-Meets Plng Guide validation criteria | 720 | A CROP at 533 psig is in place, but is scheduled to be cleared through a Validation Dig or replacement the week of 4/16. | 710 | 700 | 90 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 720 | 90 | 0 | 0 | 101.5873 | 101.5873
207 | BHH2 | TP_SACRAMENTO_VALLEY | L119D_0614_NSAC_180 | North Sacramento Holder Sta (PCE) to DFM 0614. The North Sacramento Underground Holder storage is manually operated during winter season mornning hours to take over supplying the DFM at 180 psig. |  | 34.75 | PS86, PS562 | PCE407, PCE408, PCE409 | V3-Insufficient P data to complete validation | 180 |  | 180 | 180 | 80 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 |  |  | 180 | 80 | 0 | 0 | 124.6154 | 124.6154
208 | MUMY | TP_SACRAMENTO_VALLEY | L121_485 | Marysville Buttes Sta (PCE) to Yuba City Holder Sta (PCE). Yuba City Holder Sta provides backup supply into L121 at 420 psig when the Yuba City Cogen comes on-line to maintain an elevated delivery service pressure of 375 psig at the meter. |  | 17.34 | PS89, PS90, PS91, PS92, PS580 | DRJ4PCE814 | V3-Insufficient P data to complete validation | 485 |  | 478 | 465 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V3 | Y |  | 485 | 90 | 0 | 0 | 103.5663 | 103.5663
209 | MUMY | TP_SACRAMENTO_VALLEY | L123_L173_500, L119B_L119C_0617_FOLSOM_500 | Lincoln Junction (PCE) to North Sacramento Underground Holder (PCE) 500 psig system serving Auburn and El Dorado Hills. These two subsystems have the same MAOP and operate as a single system under Design Day conditions across L123 Open BTU MLV 3.42 at Ba |  | 118.5 | PS93, PS168, PS583, PS586, PS582, PS85, PS85, PS563 | PCE404, DRJ4PCE820 | V1-Meets Plng Guide validation criteria | 500 |  | 495 | 495 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 | Y |  | 500 | 90 | 0 | 0 | 103.3485 | 103.3485
210 | MUMY | TP_SACRAMENTO_VALLEY | L124A_L202_1511_600 | Yuba City Holder (PCE) to Lincoln Jct - 600 psig system serving Grass Valley and subsystem L123_L173_500. The Pmin design shown is in Grass Valley at DR R_SRSTA-112. |  | 67.32 | PS94, PS227, PS576, PS584 | PCE413 | V1-Meets Plng Guide validation criteria | 600 | SCADA sensing line is downstream of regulators and record a lower pressure out of the station than at the regulators. | 595 | 591 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 | Y |  | 600 | 90 | 0 | 0 | 102.3018 | 102.3018
211 | MUMY | TP_SACRAMENTO_VALLEY | L150_0626_0600_125 | Pleasant Creek Line 159 Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D13. |  | 20.16 | PS142 | PCE379, PCE380 | V3-Insufficient P data to complete validation | 125 |  | 120 | 120 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V3 | Y |  | 125 | 90 | 0 | 0 | 207.6412 | 207.6412
212 | MUMY | TP_SACRAMENTO_VALLEY | L172A_500 | Swingle Jct (PCE) to Sacramento Gas Load Center. Supplies West Sacramento and subsystem L108_SGLC_412. The Pmin Design shown is in South Sacramento at the inlet to Florin-Munson 150 psig Primary station supplying DFM 0609-02. |  | 13.81 | PS164 | PCE400, PCE401 | V1-Meets Plng Guide validation criteria | 500 |  | 495 | 495 | 180 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V1 | Y |  | 500 | 180 | 0 | 0 | 114.8897 | 114.8897
213 | MUMY | TP_SACRAMENTO_VALLEY | L172A_N_L169_L167_800 | Hershey Jct North (PCE) to Fell Station and Yuba City Holder. Receives withdrawal gas from Wild Goose Storage Field (PCE) and local California Production in the Willows Field area. The Pmin Design shown is in Grass Valley at the inlet to DR R_SRSTA-112 |  | 142.78 | PS163, PS162, PS157, PS158, PS159, PS160, PS596 | PCE51, PCE54 | V1-Meets Plng Guide validation criteria | 800 | A CROP at 733 psig is currently in place but scheduled to be cleared the week of 4/23. Another CROP at 750 psig is currently in place on 8" L167-1, but may be cleared by records soon. | 798 | 798 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  |  |  |  | A CROP further reducing the MOP to 708 psig due to SSAW seam is pending. | C4-V1 | Y |  | 800 | 90 | 0 | 0 | 101.2818 | 101.2818
214 | MUMY | TP_SACRAMENTO_VALLEY | L172A_S_800 | Hershey Jct (PCE) and Yolo Jct (PCE) to L172-220 Xtie and Swingle Jct. The Pmin Design shown is in Davis at the inlet to Swingle Jct. |  | 42.72 | PS163 | PCE43, PCE44, PCE45, PCE52 | V1-Meets Plng Guide validation criteria | 800 |  | 798 | 798 | 90 |  |  | C4-NOP cannot be lowered now. Investments needed for MOP-20. | [5 empty] | C4-V1 | Y |  | 800 | 90 | 0 | 0 | 101.2818 | 101.2818
215 | MUMY | TP_SACRAMENTO_VALLEY | L195_L196_L200_L210B_800 | Creed Sta (PCE) to Las Vinas Sta. The Pmin Design shown is in South Sacramento at the inlet to DR R_SCSTA-B37 and DR R_SCSTA-B05. |  | 53.35 | PS210, PS214, PS215, PS222, PS235 | PCE56 | V1-Meets Plng Guide validation criteria | 658 | A CROP is in effect reducing the MOP from 800 to 686 psig and is not expected to be cleared before the winter season. | 635 | 632 | 90 |  |  | C2-NOP can be lowered to MOP-20 now |  |  |  |  | A CROP - UP is pending final authorization restoring the MOP to 792 psig. | C2-V1 | Y |  | 658 | 90 | 0 | 0 | 101.9065 | 101.9065
216 | MUMY | TP_SACRAMENTO_VALLEY | L197_1614_TURNER_300 | Las Vinas Sta (PCE) and Turner Rd Sta (PCE) to Lodi, Ione and Valley Springs. The Pmin Design shown is in Ione at the inlet to DR R_LOHP24 and in Sutter at the inlet to DR MARHP-01. General Mills has a Pmin requirement for an elevated delivery service pr |  | 93.36 | PS216, PS217, PS218, PS219, PS220, PS522, PS523 | PCE61, PCE64, DRJ4PCE800 | V2A-Fails validation criteria - results suspect | 300 |  | 295 | 290 | 90 |  |  | C2-NOP can be lowered to MOP-20 now | [5 empty] | C2-V2A | Y |  | 300 | 90 | 0 | 0 | 109.8901 | 109.8901
217 | MUMY | TP_SACRAMENTO_VALLEY | L220_500 | Lines 172 & 220 Crosstie (PCE) to Davis Meter and Reg Sta |  |  | PS243 | PCE386, PCE387 | V1-Meets Plng Guide validation criteria | 500 | A CROP reducing the MOP of L220 from 792 psig to 541 psig is in effect. As a result, L220 north of Rio Vista "Y" is operating at a MOP of 500 psig out of Lines 172 & 220 Crosstie. | 480 | 480 | 188 |  |  | C1-Existing NOP offset is 20 psi or more | [5 empty] | C1-V1 | Y |  | 500 | 188 | 0 | 0 | 116.4654 | 116.4654
218 | LRS3 | TP_SACRAMENTO_VALLEY | South Sutter Co Reg Sta (PCE) to DR R_FM_B-85. South Sutter DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY | South Sutter DFM |  | 17.88 | PS589 | DRJ4PCE816 | V2B-Incomplete validation - results suspect | 234 |  | 230 | 227 | 80 |  | 61 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 80 | 450 ft of 8" pipe south of Hutchinson Rd (from node 214G205F) to reinforce 4". This will extend existing 8" | $283,500 | DRJ4: Modeled by Sie Div as part of Distr Model. OK to use those results. DFM has been reinforced with 8" in past by WRO pipe replacement jobs. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost Guide Rev 4/16 | C4-V2B | Y |  | 234 | 80 | 0 | 61 | 113.2352 | 105.5402
219 | LRS3 | TP_SACRAMENTO_VALLEY | <<Part of L123_L173_500, L119B_L119C_0617_FOLSOM_500>> | District 10 DFM between L-50 tap & Magnolia Rd (no source Reg) Roseville Rd DFM Included in distribution model: MERGE_SacJ11& SierraJ11_APD_BTUopen_45_MOP_MINUS_20_STUDY |  |  | PS93, PS168, PS583, PS586, PS582, PS85, PS85, PS563 | PCE404, DRJ4PCE820 | V2B-Incomplete validation - results suspect | 400 |  | 385 | 385 | 150 |  | 234 | C2-NOP can be lowered to MOP-20 now |  | 199 | none |  | DRJ4: This analysis only looks at a lateral off of the L123_L173_500, and should be treated as part of that analysis. Therefore, the pressure should NOT be reduced until further analysis. Reduced pressure from 385 to 365 at tap. End pressure is inlet to | C2-V2B | Y |  | 400 | 150 | 0 | 234 | 116.3636 | 76.5411
220 | ANY3 | TP_SACRAMENTO_VALLEY | 0600_DIXON_158 | Dixon Reg Sta (PCE) to Dixon at the inlet to DR R_FM_R-22. 0600-05: 158# Included in distribution model:ESDZONE_SA_DIXON_H_W1112_APD_452_(MOP_MINUS_20_STUDY) |  | 2.78 | drj4PS700 | DRJ4PCE805 | V1-Meets Plng Guide validation criteria | 158 |  | 140 | 135 | 90 |  | 124 | C2-NOP can be lowered to MOP-20 now |  |  | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE REG: RR-19 (Dixon Primary) MODELED SETPOINT IS ALREADY 23 psi below MOP. NOP is 140 psig and may be operating as such in the field. | C2-V1 |  |  | 158 | 90 | 0 | 124 | 148.0313 | 56.8548
221 | LRS3 | TP_SACRAMENTO_VALLEY | 0634_COLUSA_GLENN_DRIER_600 | Maxwell Primary Reg Sta (PCE) to Maxwell and Comet Rice Drier. Included in distribution model: -BASE_08-J07maxwellAPD_UTM_452_MOP_MINUS_STUDY.MDB |  | 5.92 | PS595 | DRJ4PCE823 | V2B-Incomplete validation - results suspect | 600 |  | 590 | 570 | 80 |  | 514 | C1-Existing NOP offset is 20 psi or more |  |  | none |  | Already operating at MOP-30 | C1-V2B |  |  | 600 | 80 | 0 | 514 | 101.81 | 27.0939
222 | LRS3 | TP_SACRAMENTO_VALLEY | 0643_ARBUCKLE_150 | Arbuckle DFM Included in distribution model: BASE-07-J07ArbuckleAPD_UTM_452_MOP_MINUS_20_STUDY.MDB |  | 0.79 | drj4PS712 | PCE47, PCE48 | V1-Meets Plng Guide validation criteria | 150 |  | 143 | 133 | 80 |  | 45 | C4-NOP cannot be lowered now. Investments needed for MOP-20. |  | 80 | 1,250 FT OF 6" pipe starting at source | $787,500 | Currently an uprate is planned for 2013, the length of pipe shown would replace the uprate if that decision is made. Construction costs of $630/ft based on highly congested cost provided by Gas Construction Cost Guide Rev 4/16/2012 provided by GPS | C4-V1 |  |  | 150 | 80 | 0 | 45 | 139.7516 | 127.1739
223 | LRS3 | TP_SACRAMENTO_VALLEY | 1514_TOWNSHIP_150 | North Township DFM Included in distribution model: 09-J09YUBACITYaSd_UTM_45_MOP_MINUS_20_STUDY |  | 2.21 | drj4PS714 | DRJ4PCE818 | V3-Insufficient P data to complete validation | 150 |  | 145 | 135 | 80 |  | 133 | C2-NOP can be lowered to MOP-20 now |  | 117 | none |  | Reg set = 120 at MOP-20 | C2-V3 |  |  | 150 | 80 | 0 | 133 | 139.7516 | 29.882
224 | ANY3 | TP_SACRAMENTO_VALLEY | L116_L150_200 | L-150/L-116: 200# Davis Meter and Reg Sta (PCE) to Davis at the inlet to DR R_SCSTA-D08. -included in distribution model: ESDZONE_SA_DAVIS_H_W1112_APD_452_(MOP_MINUS_20_STUDY)_1st_&_A_St_Upgrade) |  | 5.92 | PS69, PS143 | PCE383 | V3-Insufficient P data to complete validation | 200 |  | 200 | 200 | 90 |  | 148 | C2-NOP can be lowered to MOP-20 now |  | 115 | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE DAVIS MTR/REG STA (105R & 106R) Pmin occurs at end of 750', 2" tap to DA- 06 Need charts for inlet to DA-06 | C2-V3 | Y |  | 200 | 90 | 0 | 148 | 125.3918 | 56.7273
225 | ANY3 | TP_SACRAMENTO_VALLEY | L158_L220_500 | D. Q. Scott Reg Sta (PCE) to Clark Pacific Concrete Plant. L-158/L-220 (Woodland?) Included in distribution model: ESDZONE_SA_WOODLAND_HL_W1112_APD_452_(w_Teichert)_(MOP_MINUS_20_STUDY) |  | 2.5 | PS151, PS243 | DRJ4PCE821 | V1-Meets Plng Guide validation criteria | 500 |  | 400 | 320 | 90 |  | 319 | C1-Existing NOP offset is 20 psi or more |  |  | none |  | DRJ4: Modeled by Sac Div as part of Distr Model. OK to use those results. SOURCE REG: D.Q. Scott TS-09; ASD is controlling season NOP (350 psig) is already 150 psig below MOP (500 psig). Need to manually add 20 mcfh load for Clark Pacific to node 460G41 | C1-V1 | Y |  | 500 | 90 | 0 | 319 | 103.3485 | 61.2811

## Reference (hidden)
Monthly Tasks
Check ECTS for OP Events |  | https://catsweb.utility.pge.com/catsweb/main.aspx?WCI=Main&WCE=ViewDashboard&WCU=s%3dOKBSKCNWII1I1N8F2SIGBQO7I2742L34%7c*%7er%3dCorrective%20Action%20Management%7c*%7eq%3d1%7c*%7eg%3d0
Link to ECTS
Link to OPE 2011-2013 MOP Excursion Master (GTCC > Over Pressure Elimination Task Force > SCADA Reports)
Check detail tab that all fields are filled out
On the Pivot Tab
Run pivot tables for month / small-large excursion by trans/LP/HP (A-116)
Run by clicking in the table > right click > refresh
Run pivot tables for month /cause (A-102)
Run by clicking in the table > right click > refresh
Tracking Year by Month Tab
Update monthly # of OP events
Update YTD and EOY for # of OP events (change formulas as applicable)
Check Red-Amber-Green Status is correct for month/ytd/eoy actuals
Green = 0 difference
Amber = 1 difference
Red > 2 difference
On the Charts Tab
Update Bar Chart (and row formulas below for YTD)
Update Pie Chart (on chart tab)
Format MonthlyReportDetail tab for detailed explanations from tracking detail tab
Paste monthly report detail info as picture into Monthly OP report tab
Copy Metric monthly report stats to e-mail and send out to Asset Family Owner metric reporters
Update the GSO Keys to Success Monthly Report | [8 empty] | Currently from Dan
Link to Keys site (GTCC > Documents > GSO Keys to Success Monthly Report)
http://wssuo/gso/gc/GSO%20Keys%20To%20Success%20Monthly%20Report/Forms/AllItems.aspx
Update 2014 KTS Dashboard_GSO_Month (Excel spreadsheet)
Operate the system > Gas Over Pressure Event Frequency > columns D-G
Update Gas System Operations Report Month_Yeardraft (Word Document)
Metrics > Table: Gas Over-Pressure Event Frequency
Metrics > Table: OP Events by Quarter
Metrics > Observations
Primary Drivers, OP events, and their brief descriptions
Monthly OP Events > Table
Paste Pie Charts and Data Tables from Tracking 2013 by Month tab
Enter Corporate Dashboard comment info |  |  | http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx | [5 empty] | Currently from Tim Huckabay
Link to Corporate Dashboard
Gas Data Sheet
http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx
Update Tab: Data
Appropriate information for the Month (Searchable by Gas Metric: Gas Over-Pressure Event Frequency (OPF) Metric Reporter: Kevin Dang/Kevin Singer)
OPE per location detail
Update Tab: Variance Explanation
|  |  |  | Gas Over Pressure Event Frequency (OPF) - Columns F-H |  |  | i.e. | F | G | H
AFO/AFH | [5 empty] | Send monthly updates to Maria Bernal, Tyson Len, Tim Huckabay, Bryan Badgett
CAP updates?
Link to CAP Dashboard (Corrective Action Management)
CAP Updates
https://catsweb.utility.pge.com/catsweb/main.aspx?WCI=Main&WCE=ViewDashboard&WCU=s%3D8YWR64G9BGDM01CDL5PF3OVMC97RTZH4%7C*~r%3DCorrective%2520Action%2520Management%7C*~q%3D1
Update CAP number
2011-2013 Expanded Data tab
Update Cap number in Gas Event ID#/CAP ID #
use link of similar event
If nothing is indicated - Email Todd Novak about entering the OPE into CAP
these
Information that may help
Gas Logs
\\Appgas01\OPC\SHARE\GOCS
TCG(mon,day-year)
Open with notepad
Note on L52: Singer, Kevin D: For November there were 2 transmissions events, 0 HP distribution events and 1 LP distribution event (on par with the expectations for monthly totals). Preliminary root cause: 2 events were human factor error-related and 1 event was equipment-related.
Note on M52: Singer, Kevin D: OP Team reviews root causes of overpressure events. Plan additional training to address human-error related OP events. Detail review of equipment-related events to formulate corrective action plan.
Note on N52: Singer, Kevin D: As process improvement initiatives are implemented, expect this metric to return to green in December

## Tracking2019 by Month (hidden)
2019 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 13 | 16
Amber Goal - Lowest end of range* | 4 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  |  | 20 | 25
Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 33 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8
Actual - HP Distribution Mains | 1 | 1 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 5 | 4 | 2 |  |  | 19 | 20 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | change these colors at End of Month |  |  |  |  | 0
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8 | [9 empty] | 1
Actual - Distribution Main Total | 1 | 1 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 5 | 4 | 2 |  |  | 19 | 20 |  |  |  |  | change these colors at End of Month |  |  |  |  | 2
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8
Actual - Distribution Services Total | 1 | 1 | 0 | 3 | 0 | 0 | 1 | 2 | 0 | 5 | 4 | 2 |  |  | 19 | 20 |  |  |  |  | change these colors at End of Month |  |  |  |  | 3
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 7 | 8
Actual - Transmission | 0 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 |  |  | 11 | 12 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 5 | 6 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 1 |  |  | 8 | 8
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 3 | 3
Actual - Total All Large OP | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 8 | 8
Actual - All Equipment Failure | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 8 | 8
Actual - All Operator Error | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 |  |  | 9 | 9
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 3 | 4 | New for 2018
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 |  |  | 4 | 5 | New for 2018
Goal - All Safety | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 4 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 9 | 10
Actual - Total Small OP | 1 | 2 | 2 | 2 | 0 | 0 | 1 | 2 | 1 | 3 | 4 | 2 |  |  | 20 | 21
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.201, 619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.201, 619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
For July Month-To-Date: 5 transmission events, 3 HP distribution events and 2 LP distribution events (better than month-end goals for HP & Transmission and on par with LP Distribution for YTD). YTD Apparent causes for items were: HP Distribution - liquids, LP Distribution - SP too close between monitor and regulator (too close to MOP), Transmission - HP/WPE as they relate to clearance work, plus manual and gas operations played a role as well.
| Jan: Total OP Events | Large OP Events | [11 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2019 Target |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2019 Target |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2019 Target
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 16 |  |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 6 |  |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 12
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2019 Goal OP events | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2019 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events; Nov: Large OP Events | [9 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual |  |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 2 | 9 |  |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 |  |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 2 | 9 |  |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 3 | 2 |  |  | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 |  |  | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20
[11 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 YTD
[10 empty] | HU | 13 | 4 | 7 | 4 | 5 | 6 | 3 | 0 | 9
[10 empty] | EQ | 8 | 3 | 2 | 3 | 2 | 4 | 8 | 5 | 18
Proposed Scenario | 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, red>2, amber=1, green=0.
Note on A63: Singer, Kevin D: Enter these three cells into the Variance Explaination (F7-H7) http://wss/sites/GasProgramAndPerfMgmt/Gas%20Metrics/Forms/AllItems.aspx

## Tracking2020 by Month (hidden)
2020 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 |  |  | 6 | 16
Amber Goal - Lowest end of range* | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 4 |  |  | 10 | 52
Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 4 | 4 | 3 | 5 | 0 | 3 |  |  | 42 | 43 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 5 | 8
Actual - HP Distribution Mains | 2 | 5 | 2 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 |  |  | 25 | 28 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 1 |  |  |  |  | change these colors at End of Month
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 3 | 8
Actual - Distribution Main Total | 2 | 5 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 |  |  | 26 | 30 |  |  |  |  | change these colors at End of Month
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Services Total | 2 | 5 | 3 | 1 | 2 | 1 | 3 | 1 | 2 | 3 | 0 | 3 |  |  | 26 | 33 |  |  |  |  | change these colors at End of Month
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 3 | 8
Actual - Transmission | 1 | 2 | 2 | 0 | 0 | 3 | 1 | 5 | 1 | 2 | 0 | 1 |  |  | 18 | 23 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 1 | 6 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 1
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 1 | 1 | 0 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 |  |  | 8 | 8
Actual - Total All Large OP | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 0 |  |  | 9 | 13
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 4 | 8
Actual - All Equipment Failure | 2 | 6 | 3 | 1 | 2 | - | - | - | - | - | - | - |  |  | 14 | 18 | [6 empty] | >8
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 1 | 8 | [6 empty] | 8
Actual - All Operator Error | 1 | 1 | 2 | 0 | 0 | - | - | - | - | - | - | - |  |  | 4 | 11 | [6 empty] | 6
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 0 | 4 | New for 2018 | [5 empty] | 4
Actual - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - |  |  | 0 | 4 | New for 2018
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - |  |  | 0 | 0 | New for 2018
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - |  |  | 0 | 0
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 3 | 10
Actual - Total Small OP | 4 | 6 | 4 | 1 | 2 | - | - | - | - | - | - | - |  |  | 17 | 24
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621; Jun: 192.201
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621; Jun: 192.201
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10% or 25 psig
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
| Jan: Total OP Events | Large OP Events | [11 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 YTD |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 YTD |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 YTD
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 |  |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 |  |  | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 33
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2020 Actual - All Events | 3 | 7 | 5 | 1 | 2 | 4 | 4 | 6 | 3 | 5 | 0 | 3 |  |  | 43 | 43
2020 Goal OP events | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 0 |  |  | 9 | 9
2020 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events; Nov: Large OP Events | [9 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 24 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 2 | 9 | 1 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 23
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 1 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 25 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 2 | 9 | 1 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 24
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 18 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 3 | 2 | 8 |  | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 10
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 |  | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 34
| Oct: Large; Nov: 2011; Dec: 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
| Oct: HU; Nov: 13; Dec: 4 | 7 | 4 | 5 | 6 | 3 | 0 | 9
| Oct: EQ; Nov: 8; Dec: 3 | 2 | 3 | 2 | 4 | 8 | 5 | 18
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11
NEW as of December 2020 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: Large OP Events under STIP are reported and forecasted quarterly which may change the projections over a month-to-month basis.

## Tracking2021 by Month (hidden)
2021 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 14 | 16
Amber Goal - Lowest end of range* | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |  |  | 47 | 52
Actual - All Events | 1 | 7 | 1 | 3 | 2 | 1 | 5 | 4 | 1 | 3 | 4 | 2 |  |  | 34 | 36 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 7 | 8
Actual - HP Distribution Mains | 1 | 4 | 1 | 1 | 2 | 1 | 0 | 2 | 0 | 1 | 3 | 0 |  |  | 16 | 17 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | change these colors at End of Month
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Main Total | 1 | 4 | 1 | 1 | 2 | 1 | 0 | 2 | 0 | 1 | 3 | 0 |  |  | 16 | 21 |  |  |  |  | change these colors at End of Month
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Services Total | 1 | 4 | 1 | 1 | 2 | 1 | 0 | 2 | 0 | 1 | 3 | 0 |  |  | 16 | 23 |  |  |  |  | change these colors at End of Month
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 7 | 8
Actual - Transmission | 0 | 3 | 0 | 2 | 0 | 0 | 5 | 2 | 1 | 2 | 1 | 2 |  |  | 18 | 20 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 |  |  | 6 | 7 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  |  | 3 | 3
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  |  | 2 | 2
Actual - Total All Large OP | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  |  | 5 | 6
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 1 | 8
Actual - All Equipment Failure | [14 empty] | 0 | 7 | bar: Jan to Dec
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 0 | 8
Actual - All Operator Error | [14 empty] | 0 | 8 | bar: Jan to Dec
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 0 | 4 | New for 2018
Actual - All Latent Org Weakness | [14 empty] | 0 | 4 | New for 2018 | bar: Jan to Dec
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | [14 empty] | 0 | 0 | New for 2018 | bar: Jan to Dec
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | [14 empty] | 0 | 0 | bar: Jan to Dec
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 1 | 10
Actual - Total Small OP | [14 empty] | 0 | 9 | bar: Jan to Dec
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10%
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
| Jan: Total OP Events | Large OP Events | [10 empty] | Small OP Events
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 YTD |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 YTD | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 9 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 5 | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 33 | 4
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2020 Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 4 | 4 | 3 | 5 | 0 | 3 |  |  | 42 | 42
2021 Actual - All Events | Jan: 1; Feb: 7; Mar: 1; Apr: 3; May: 2 |  |  | 14
2021 Goal OP events | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 0 | 1 | 1 | 0 | 0 |  |  | 9 | 9
2021 Actual - Total All Large Ops | Jan: 0; Feb: 0; Mar: 0; Apr: 0; May: 1 |  |  | 1
2021 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events | Large OP Events | [10 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 24 | 10 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4 | 2 | 3 | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 21 | 9
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 2 | 0 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 2 | 0
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 26 | 10 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 0 | 4 | 2 | 3 | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 23 | 9
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 16 | 4 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 5 | 7 | 6 | 2 | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 12 | 4
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 14 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 8 | 5 | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 35 | 13
[11 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
[10 empty] | HU | 13 | 4 | 7 | 4 | 5 | 6 | 3 | 0
[10 empty] | EQ | 8 | 3 | 2 | 3 | 2 | 4 | 8 | 5
Proposed Scenario | 2015-2020 Performance Outcomes
[12 empty] | Year | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
[12 empty] | LG HPD OP Events | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5
NEW as of December 2019/20 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8*
*Chevron was not an overpressure event based on doucmentation found after the event, but documented by leadership as a large op event
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, wrt metrics

## Pivot (hidden)
OP/Near Hit? | (Multiple Items)
Large/Small OP Event | (Multiple Items)
Count of Month | Column Labels
Row Labels | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Grand Total
2011 | 4 | 3 | 2 |  | 5 | 2 |  | 1 | 1 | 2 |  | 1 | 21
2012 | 2 |  | 1 |  | 1 |  |  |  | 1 |  |  | 2 | 7
2013 | 2 | 1 | 1 | 1 |  |  |  | 2 | 1 |  | 1 |  | 9
2014 | 3 | [6 empty] | 2 |  |  | 2 |  | 7
2015 | 2 |  | 1 |  |  |  | 1 | 3 |  |  |  |  | 7
2016 |  |  |  | 1 |  | 3 | 1 | 1 |  | 2 | 1 | 1 | 10
2017 | 1 |  |  | 2 | 1 |  | 1 | 1 | 1 | 4 |  |  | 11
2018 | [6 empty] | 1 |  |  | 1 | 2 | 1 | 5
2019 | 1 |  |  | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 1 | 11
2020 |  | 1 | 1 |  |  | 2 | 2 | 3 | 1 |  |  |  | 10
2021 |  |  |  |  | 1 |  | 1 |  |  | 1 | 1 |  | 4
Grand Total | 15 | 5 | 6 | 5 | 9 | 8 | 8 | 14 | 5 | 12 | 9 | 6 | 102

## Tracking2023byMonth (hidden)
2023 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | YE-Frcst | [11 empty] | some columns hidden, data below - do not delete
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | 16 | 31
Amber Goal - Lowest end of range* | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  | 28 | 42 | In 2023 - there will be no amber measure - its either green or red > this row will be hidden
Actual - All Events | 1 | 2 | 2 | 2 | 3 | 0 | 0 | 1 | 0 | 3 | 1 | 2 |  | 17 | 19
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  | 8 | 8
Actual - HP Distribution Mains | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 1 |  | 9 | 10
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 1
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  | 8 | 8
Actual - Distribution Main Total | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 2 |  | 10 | 11
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  | 1 | 8
Actual - Distribution Services Total | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 2 |  | 10 | 17
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 8 | 8
Actual - Transmission | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 7 | 8
Goal - All Large OP Events1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 |  | 7 | 7
Actual - Large Excursions - HP Dist | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 3
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 2
Actual - Total All Large OP | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 5
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  | 1 | 8
Actual - All Equipment Failure | [13 empty] | 0 | 7 | bar: Jan to Dec
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  | 0 | 8
Actual - All Operator Error | [13 empty] | 0 | 8 | bar: Jan to Dec
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  | 0 | 4 | New for 2018
Actual - All Latent Org Weakness | [13 empty] | 0 | 4 | New for 2018 | bar: Jan to Dec
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | New for 2018
Actual - All Safety | [13 empty] | 0 | 0 | New for 2018 | bar: Jan to Dec
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Actual - At Compressor Stn or Storage | [13 empty] | 0 | 0 | bar: Jan to Dec
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  | 1 | 10
Actual - Total Small OP | [13 empty] | 0 | 9 | bar: Jan to Dec
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10%
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
Total OP Events
Total | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 | 34 | 27 | 17
Large OP Events
Large | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
T&D Total | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 5 | 9 | 5
Small OP Events
Small | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
T&D Total | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 34 | 29 | 18 | 12
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  | 31 | 31
2020 Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 5 | 4 | 3 | 5 | 0 | 3 |  | 43 | 43
2021 Actual - All Events | 1 | 7 | 1 | 3 | 2 | 1 | 5 | 4 | 1 | 3 | 4 | 2 |  | 34 | 34
2022 Actual - All Events | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 5 | 2 | 2 | 5 | 2 |  | 27 | 27
2023 Actual - All Events | 1 | 2 | 2 | 2 | 3 | 0 | 0 | 1 | 0 | 3 | 1 | 2 |  | 17 | 17
2024 Actual - All Events
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 0 | 0 |  | 9 | 9
2021 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  | 5 | 5
2022 Actual - Total All Large Ops | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 0 |  | 9 | 9
2023 Actual - Total All Large Ops | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 5
2024 Actual - Total All Large Ops
| Jan: Total OP Events |  | Large OP Events | [21 empty] | Small OP Events (2011-2019 data hidden)
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual | 2023 Actual | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual | 2023 Actual |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual | 2023 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 19 | 16 | 13 | 9 | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4 | 2 | 3 | 3 | 3 |  | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 21 | 13 | 10 | 6
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 2 | 0 | 1 | 1 | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 2 | 0 | 1 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 21 | 16 | 2 | 2 | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 0 | 4 | 2 | 3 | 3 | 3 |  | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 23 | 13 | 11 | 7
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 22 | 18 | 13 | 7 | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 5 | 7 | 7 | 6 | 6 | 2 |  | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 12 | 12 | 7 | 5
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 | 34 | 27 | 17 | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 9 | 9 | 5 |  | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 35 | 25 | 18 | 12
Proposed Scenario | Jan: 2015-2020 Performance Outcomes
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5
NEW as of December 2019/20 (STIP 2021) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 9
*Chevron was not an overpressure event based on doucmentation found after the event, but documented by leadership as a large op event
NEW as of 2021 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 34
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 6
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8* | 5
NEW as of 2022 & 2023 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22 | ‘23 | '24
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A | N/A | N/A | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 34 | 27 | 16
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 5 | 7 | 7
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8* | 5 | 9 | 5
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, wrt metrics

## Tracking2022byMonth (hidden)
2022 OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Expected Path: Goal OP events* | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 10 | 33
Amber Goal - Lowest end of range* | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |  |  | 5 | 74
Actual - All Events | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 5 | 2 | 2 | 5 | 2 |  |  | 27 | 33 |  |  |  |  | change these colors at End of Month
Asset Family OP Metrics
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | YE-Frcst
Goal - HP Distribution Mains | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 8 | 8
Actual - HP Distribution Mains | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 4 | 0 | 1 | 4 | 1 |  |  | 14 | 16 |  |  |  |  | change these colors at End of Month
Goal - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - LP Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 1 | 1 |  |  |  |  | change these colors at End of Month
Goal - Distribution Main Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 8 | 8
Actual - Distribution Main Total | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 1 | 4 | 1 |  |  | 15 | 17 |  |  |  |  | change these colors at End of Month
Goal - Distribution Services Total | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  |  | 1 | 8
Actual - Distribution Services Total | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 1 | 4 | 1 |  |  | 15 | 22 |  |  |  |  | change these colors at End of Month
Goal - Transmission | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 8 | 8
Actual - Transmission | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 11 | 15 |  |  |  |  | change these colors at End of Month
Goal - All Large OP Events1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 |  |  | 5 | 5 |  |  |  |  | change these colors at End of Month
Actual - Large Excursions - HP Dist | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 |  |  | 4 | 4
Actual - Large Excursions - LP Dist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - Large Excursions - Trans | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 |  |  | 5 | 5
Actual - Total All Large OP | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 0 |  |  | 9 | 10
Goal - All Equipment Failure | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  |  | 1 | 8
Actual - All Equipment Failure | [14 empty] | 0 | 7 | bar: Jan to Dec
Goal - All Operator Error | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |  |  | 0 | 8
Actual - All Operator Error | [14 empty] | 0 | 8 | bar: Jan to Dec
Goal - All Latent Org Weakness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  |  | 0 | 4 | New for 2018
Actual - All Latent Org Weakness | [14 empty] | 0 | 4 | New for 2018 | bar: Jan to Dec
Goal - All Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | New for 2018
Actual - All Safety | [14 empty] | 0 | 0 | New for 2018 | bar: Jan to Dec
Goal - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Actual - At Compressor Stn or Storage | [14 empty] | 0 | 0 | bar: Jan to Dec
Goal - Small OP Events | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 |  |  | 1 | 10
Actual - Total Small OP | [14 empty] | 0 | 9 | bar: Jan to Dec
1 - Large OP Events are defined as:
HP Distribution (1 psig to 12 psig) = P ≥ MAOP + 50% | Apr: 192.619-621
HP Distribution (12 psig to 60 psig) = P ≥ MAOP + 6 psig | Apr: 192.619-621
LP Distribution = P ≥ 16" H2O | Apr: GO 58A 8.b, 8.f
Transmission = P ≥ MAOP + 10%
Division goals are set at EOY only (it is 0 for each division for each month).
EOY by Division is 1 for Green, 2 for Amber
EOY for total Districts (not broken out by individual Districts in Metric) is 5 for Green, 10 for Amber
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Dashboard Variance Comments:
See JobAid for additional details on Variance and Recovery comments to be added to the monthly report.
Total OP Events
Total | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 | 34 | 27
Large OP Events
Large | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
T&D Total | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 5 | 9
Small OP Events
Small | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
T&D Total | 754 | 302 | 23 | 11 | 22 | 8 | 10 | 13 | 20 | 34 | 29 | 18
| 2015 Total OP - 17 Events | [5 empty] | 2015 Large Excursion OP Events - 0 Events
OP Event Performance
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | YTD | Yr-End
2011 Actual - All Events | 67 | 65 | 88 | 51 | 73 | 71 | 83 | 52 | 62 | 75 | 35 | 53 |  |  | 775 | 775
2012 Actual - All Events | 69 | 68 | 92 | 47 | 13 | 2 | 2 | 2 | 2 | 5 | 1 | 6 |  |  | 309 | 309
2013 Actual - All Events | 8 | 3 | 2 | 4 | 2 | 2 | 0 | 4 | 2 | 1 | 4 | 0 |  |  | 32 | 32
2014 Actual - All Events | 4 | 2 | 0 | 0 | 1 | 3 | 2 | 2 | 0 | 0 | 2 | 2 |  |  | 18 | 18
2015 Actual - All Events | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 4 |  |  | 29 | 29
2016 Actual - All Events | 2 | 0 | 0 | 1 | 0 | 4 | 1 | 3 | 0 | 3 | 2 | 2 |  |  | 18 | 18
2017 Actual - All Events | 1 | 0 | 1 | 2 | 4 | 0 | 1 | 4 | 1 | 5 | 1 | 1 |  |  | 21 | 21
2018 Actual - All Events | 1 | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 4 | 3 |  |  | 18 | 18
2019 Actual - All Events | 2 | 2 | 2 | 3 | 1 | 1 | 2 | 3 | 1 | 5 | 6 | 3 |  |  | 31 | 31
2020 Actual - All Events | 4 | 7 | 5 | 1 | 2 | 4 | 5 | 4 | 3 | 5 | 0 | 3 |  |  | 43 | 43
2021 Actual - All Events | 1 | 7 | 1 | 3 | 2 | 1 | 5 | 4 | 1 | 3 | 4 | 2 |  |  | 34 | 34
2022 Actual - All Events | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 5 | 2 | 2 | 5 | 2 |  |  | 27 | 27
2022 Goal OP events | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 16 | 16
2011 Actual - Total All Large Ops | 4 | 3 | 2 | 0 | 5 | 2 | 0 | 1 | 1 | 2 | 0 | 1 |  |  | 21 | 21
2012 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 |  |  | 7 | 7
2013 Actual - Total All Large Ops | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 |  |  | 9 | 9
2014 Actual - Total All Large Ops | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 |  |  | 7 | 7
2015 Actual - Total All Large Ops | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 |  |  | 7 | 7
2016 Actual - Total All Large Ops | 0 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 0 | 2 | 1 | 1 |  |  | 10 | 10
2017 Actual - Total All Large Ops | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 4 | 0 | 0 |  |  | 11 | 11
2018 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 |  |  | 5 | 5
2019 Actual - Total All Large Ops | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1 |  |  | 11 | 11
2020 Actual - Total All Large Ops | 0 | 1 | 1 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 0 | 0 |  |  | 9 | 9
2021 Actual - Total All Large Ops | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  |  | 5 | 5
2022 Actual - Total All Large Ops | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 0 |  |  | 9 | 9
2022 Goal - All Large OPs1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |  |  | 6 | 6
| Jan: Total OP Events |  | Large OP Events | [11 empty] | Small OP Events
| 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 YTD |  | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual | 2011 Actual | 2012 Actual | 2013 Actual | 2014 Actual | 2015 Actual | 2016 Actual | 2017 Actual | 2018 Actual | 2019 Actual | 2020 Actual | 2021 Actual | 2022 Actual
HP Dist | 39 | 7 | 9 | 6 | 13 | 8 | 6 | 7 | 21 | 19 | 16 | 13 |  | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4 | 2 | 3 | 3 | 29 | 3 | 5 | 2 | 10 | 2 | 2 | 5 | 12 | 21 | 13 | 10
LP Dist | 624 | 228 | 3 | 2 | 3 | 2 | 1 | 2 | 0 | 2 | 0 | 1 |  | 3 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 228 | 2 | 2 | 1 | 2 | 1 | 2 | 0 | 2 | 0 | 1
Dist Total | 663 | 235 | 12 | 8 | 16 | 10 | 7 | 9 | 21 | 21 | 16 | 2 |  | 13 | 4 | 5 | 4 | 5 | 6 | 4 | 0 | 4 | 2 | 3 | 3 | 650 | 231 | 7 | 4 | 11 | 4 | 3 | 7 | 12 | 23 | 13 | 11
Trans | 112 | 74 | 20 | 10 | 13 | 8 | 14 | 9 | 10 | 22 | 18 | 13 |  | 8 | 3 | 4 | 3 | 2 | 4 | 7 | 5 | 7 | 7 | 6 | 6 | 104 | 71 | 16 | 7 | 11 | 4 | 6 | 6 | 8 | 12 | 12 | 7
T&D Total | 775 | 309 | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43 | 34 | 27 |  | 21 | 7 | 9 | 7 | 7 | 10 | 11 | 5 | 11 | 9 | 9 | 9 | 754 | 302 | 23 | 11 | 22 | 8 | 9 | 13 | 20 | 35 | 25 | 18
[11 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
[10 empty] | HU | 13 | 4 | 7 | 4 | 5 | 6 | 3 | 0
[10 empty] | EQ | 8 | 3 | 2 | 3 | 2 | 4 | 8 | 5
Proposed Scenario | 2015-2020 Performance Outcomes
[12 empty] | Year | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
[12 empty] | LG HPD OP Events | 10 | 4 | 4 | 4 | 3 | 6 | 4 | 0 | 4
| ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 9 | 4 | 2 | 1 | 0
Large Overpressure Events | 11 | 9 | 4 | 2 | 1 | 0 | 0 | 0
NEW as of January 2016 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20
Overpressure events | 32 | 24 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of January 2017 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3 | 2
Actual Overpressure Events | ‘13: 32; ‘14: 18; ‘15: 29; ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 2 | 0 | 0 | 0
Actual Large Overpressure Events | ‘13: 10; ‘14: 7; ‘15: 7; ‘16: 10
NEW as of June 2017 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 9 | 4 | 3
Actual Overpressure Events | 10 ‘13: 32; 7 ‘14: 18; 7 ‘15: 29; 10 ‘16: 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3
Actual Large Overpressure Events | 10 ‘13: 10; 7 ‘14: 7; 7 ‘15: 7; 10 ‘16: 10
NEW as of December 2018 (S1) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 4 | 4 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5
NEW as of December 2019/20 (STIP 2021) | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 43
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 4
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 9
*Chevron was not an overpressure event based on doucmentation found after the event, but documented by leadership as a large op event
NEW as of 2021 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 34
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 6
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8* | 5
NEW as of 2022 | ‘13 | ‘14 | ‘15 | ‘16 | ‘17 | ‘18 | ‘19 | ‘20 | ‘21 | ‘22 | ‘23
Overpressure events | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | N/A | N/A | N/A
Actual Overpressure Events | 32 | 18 | 29 | 18 | 21 | 18 | 31 | 42 | 34 | 27
Large Overpressure Events | 11 | 9 | 4 | 4 | 4 | 8 | 6 | 6 | 6 | 5 | 7
Actual Large Overpressure Events | 10 | 7 | 7 | 10 | 11 | 5 | 11 | 8* | 5 | 9
Note on R11: Singer, Kevin D: enter total monthly
Note on R14: Singer, Kevin D: enter total monthly
Note on R23: Singer, Kevin D: enter total monthly, color code accordingly, wrt metrics

## OP & Near Hits Data
Columns Removed due to Confidential Nature - Point Description/Locations, Descriptions
Data can be provided to CPUC upon request.
OP/Near Hit? | CAP# | TELVENT Point Name | Division | Date | Inlet MAOP | Max Value | MAOP Value | Pressure Difference | Percent over MAOP | Primary Event Category | HU / EQ | P | Secondary Event Category | Old Event Category | Apparent Cause | Simplified cause (OP Events) | Constrained system | Clearance | Exposure Rank (High/Low) | Exceeded MOP? | Capture Type | Corrective/Future Planned Actions | Region | Group | LP > 14, Trans>MOP+3, HP>MOP | Gas Log Event | HIS Name | Transmission/ Distribution | Year | Month | Specific OP Metric Group | Large/Small OP Event | Index | Study Group | Avoid by lower setpoints | Quarter | At Compr Stn or Storage | Clearance Time Approval Days | Released to operations (Installed) | Report Final Date | Mooney Regs involved (root or contributing causes)? | HU | Borescope/ Debris | RCE | Slam shut activation? | Tranche | LCC | Runs | FLOC | Operating Diagram | Working Reg Setpoints (psig) | Primary OPP Setpoints (psig) | Secondary OPP Setpoints (psig)
OP | 128045607 | YO_PAT_RN20 | Yosemite | 2024-01-12 14:32 | 890 | 61.88 | 60 | 1.88 | 3.133% | Gas Contaminants – Debris | EQ | P5 |  |  |  | Regulation failed due to debris in the station piping and equipment. Slam shut activated as intended to prevent further pressure exceedance. Slam shut activation | [5 empty] | • Perform internal inspection and shut in the run. • Borescoped and cleaned lead run. • Monitor setpoints were reduced (to 46 psig) which allow more operating room between MAOP and equipment. • Removed strainer gaskets before returning to service. (And submit MPR for damaged strainer gasket.) | [5 empty] | HP Distribution |  |  |  | Small OP Event |  |  | Yes |  | No | [5 empty] | Yes | No | Yes | Distribution - DREG | Yes | H-14 | GD.STAT.DIST.11310 | 0814087 (pge.com) | 40 | 58 | 62
OP | 128078573 | FAI_PT0002 | Stockton | 2024-01-22 | 365 | 107.4 | 90 | 17.4 | 19.33% | Maintenance Operations Quality | HU | P50.2 |  |  |  | Regulation failed to perform as intended - as performing maintenance created a dead end / low flow system that was not gauged. | [5 empty] | • Leak Survey completed on 1/23/24. No leaks found. • Clearance initiated for transmission station (HP-31) outlet pressure reduction to 62 psig (lead) and 58 psig (lag). • GPOM will perform another class A-inspection prior to pressure reduction. • TROP (G4# 80008010) to lower MAOP from 90 psig to 72 psig. | [5 empty] | Transmission |  |  |  | Large OP Event |  |  | Yes |  | No | [5 empty] | No | Yes | No | Transmission - Simple | No | H-14 | GT.STAT.MISC.ACACIASTRG | 082229.pdf
Near Hit | 128171073 | MiniAT | Kern | 2024-02-12 | 465 | 471.1 | 720 | -248.9 | -34.57% | Failure Equipment | EQ | P5 |  |  |  | Meter set backpressure and valve leakage resulted in the pressure increase. Set was originally designed and has an MAOP of 720 psig | [5 empty] | • GPOM reduced pressure to 240 psig. • MAOPE has been engaged to determine of the MAOP is higher than 465 psig on the operating diagram. MAOPE determined the MAOP is 720 psig and will process the paperwork. • FIMP to work with GPOM to lower token relief valve setpoint as needed. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | H-15 | GT.STAT.LVCR.0000000435 | 0812916.pdf (pge.com) |  |  | 390
OP | 128198144 | YO_TUR_RT12 | Yosemite | 2024-02-16 | 890 | 60.458 | 60 | 0.458 | 0.7633% | Gas Contaminants - Sulfur | EQ | P5 |  |  |  | Regulation failed to control pressure due to sulfur in the station equipment. | [5 empty] | GPOM made area safe, completed class inspection B, and returned station to service. Engineering to review maintenance history for additional maintenance recommendations. | [5 empty] | HP Distribution |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Distribution - DREG | No | H-14 | GD.STAT.DIST.00878 |  | 54 | 58
Near Hit | 128221263 | FR_FRE_RGS3 | Fresno | 2024-02-15 17:10 | 650 |  |  | 0 | #DIV/0! | Slam Shut Activation | EQ | P5 |  |  |  | Slam shut activation | [5 empty] | Investigate the spurious activation Engage GSP to load shift so FGLC has more take away than it currently does. | [5 empty] | HP Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Distribution - DREG | No | H-14 | GD.STAT.DIST.11284
OP | 128243445 | S2M_PT0029 ; S2M_PT0031; S2M_PT0032; S2M_PT0033 | Sacramento | 2024-03-05 | 412 | 244.8 | 240 | 4.8 | 2% | Maintenance Operations Quality | HU | P5 |  |  |  | Technician inadvertently placed wrong valve in local control. | [5 empty] | • GPOM technician immediately recognized the issue and made actions to correct the pressure increase. • Station was returned to safe operation. • GPOM to discuss lesson learned and review clearance procedure before continuing work. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - Complex | No | H-19 | GT.STAT.MISC.20THMARTIN | 0800151.pdf
Near Hit | 128352549 | SA_WIN_PT021 | Sacramento | 2024-03-21 | 975 | 111 | 125 | -14 | -11.2% | Slam Shut Activation | EQ | P5 |  |  |  | Slam Shut Activation | [5 empty] | • Slam Shut set points were adjusted 127 psig & 132 psig in compliance with 4125P-07. • Team set out a data recorder and will review information once it is picked up. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - Simple | No | H-14 | GT.STAT.MISC.PLEASANTCK | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083596.pdf | 110 | 120 | 129
Near Hit | 128365291 | MI_ERE_ER11 | Yosemite | 2024-03-23 | 175 |  | 60 | -60 | -100% | Slam Shut Activation | EQ | P5 |  |  |  | Customer Shutdown | [5 empty] | TRVs installed in 2021 Regulation was replaced in 2022, with slam shuts installed Scheduled to be rebuilt in 2025 | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | H-15 | GT.STAT.LVCR.0000000668
Near Hit | 128466871 | ST_TRA_M001 | Stockton | 2024-04-05 10:34 | 890 |  | 60 | -60 | -100% | Slam Shut Activation | EQ | P5 |  |  |  | Customer Shutdown | [5 empty] | mitigation | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | H-15 | GT.STAT.LVCR.0000000141
Near Hit | 128466838 | YO_MAD_RB42 | Yosemite | 2024-04-05 12:01 |  |  |  | 0 | #DIV/0! | Slam Shut Activation | EQ | P5 |  |  |  | Slam shut activation | [11 empty] | HP Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Distribution - DREG | No | H-14 | GD.STAT.LPRS.00249
OP | 128617796 | YO_LBN_M003_PT2 | Yosemite | 2024-04-22 | 890 | 540.6 | 500 | 40.6 | 8.12% | Maintenance Operations Quality | HU | P5 |  |  |  | Regulation failed to control pressure during maintenance. | [5 empty] | Regulation failed to control pressure during maintenance. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | H-15 | GT.STAT.LVCR.0000234
Near Hit | 128716023 | YO_ATW_M001 | Yosemite | 2024-05-04 |  |  |  | 0 | #DIV/0! | Slam Shut Activation | EQ | P5 |  |  |  | Failure - Equipment | [5 empty] | GPOM to investigate and reset SS 7/10/24 CAPS are submitted for tracking and trending purposes for slam shut activations. To a certain extent they document the number of potential overpressure events that were prevented with installing the equipment, and document the potential end of life for the equipment (if these occur with higher frequency, it could be a malfunction of the equipment). Closed for trending. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | N/A |  | No | [5 empty] | N/A | No | Yes | Transmission - LVC | Yes | H-14 | GT.STAT.LVCR.0000000106
Near Hit | 128726729 | DI_ANT_RA05 | Diablo | 2024-05-07 | 573 |  | 58 | -58 | -100% | Slam Shut Activation | EQ | P5 |  |  |  | Moisture identified | [5 empty] | Station was rebuilt, and ss were installed with the new design in 2020. The has requested information about the SS if it was manufactured with the thru hole, and will add to the list if it needs a retrofit. Consider looking at other stations installed/rebuilt in this timeframe to understand if there are more new stations with a similar issue. | [5 empty] | HP Distribution |  |  |  | Near Hit |  |  | N/A |  | No | [5 empty] | N/A | No | Yes | Distribution - DREG | Yes | H-14 | GD.STAT.DIST.11201
Near Hit | 129028216 | ST_ION_M001 | Stockton | 2024-06-05 | 300 |  | 60 | -60 | -100% | Slam Shut Activation | EQ | P5 |  |  |  | Customer Shutdown | [5 empty] | GPOM to investigate and reset SS | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | GT.STAT.LVCR.0000000611 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0812909.pdf
OP | 129054236 | YO_MAD_M003_PT2 | Yosemite | 2024-06-08 | 400 | 418.1 | 400 | 18.1 | 4.525% | Thermal Expansion | EQ | P5 |  |  |  | Thermal expansion | [5 empty] | GPOM relieved high-pressure gas and performed a class A inspection. Regulation Engineering to review equipment modifications. MAOP Engineering to review records for a potential MAOP correction. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | GT.STAT.LVCR.0000000651
Near Hit | 129108449 | N/A | Central Coast | 2024-06-21 | 303 | 60 |  | 60 | #DIV/0! | Failure - Equipment | EQ | P5 |  |  |  | Regulation failed to control pressure - bypass valve tampering, rupture disk. | [5 empty] | We treated the restoration like an OP. We rebuilt the farm tap, removed the hard bypass and created a soft bypass. We restored the line, pressure tested the line and leak surveyed upon completion. M&C will tailboard there teams about what happened and the potential problems. Here is where we can learn from this .. If M&C has a question, please call us, we welcome it. Never feel your alone, if your nervous call and we will help, doesn't have to be an emergency. We are your brothers and sisters . If it is near a GPOM asset, but on a distribution side, Gas Control should call both M&C and GPOM . If you arrive on scene, and find that you are near a GPOM asset, please call for our support. Not only because it is ours, but we may have more information on the site that will be useful . If the situation is safe to do so(read, not life or property threatening), allow a GPOM rep to show up and operate the assets, we are all here for each other . If it is an unsafe situation(very rare life threatening situations) that needs immediate action, then the following steps should be taken (never reg set's) o Call GPOM, if we can't arrive in a safe amount of time, we can walk you through all the steps o Ensure proper oq's o Have gas control give proper instructions if applicable o Gauge up, and document and watch pressure o Close the Outlet valve, downstream valve to isolate o Call GPOM, for follow up response . If it looks like it was tampered with, let us know and we will correct it these are the recommendations we came up with. | [5 empty] | Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | No | Distribution - FTAP | Yes | H-10 | GD.STAT.FTAP.00075
OP | 129167598 | YO_MAD_M003_PT2 | Yosemite | 2024-06-29 | 400 | 403 | 400 | 3 | 0.75% | Thermal Expansion | EQ | P5 |  |  |  | Thermal expansion | [5 empty] | GPOM relieved high-pressure gas and performed a class A inspection. Regulation Engineering to review equipment modifications. MAOP Engineering to review records for a potential MAOP correction. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | GT.STAT.LVCR.0000000651
Note on M3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Tab: OP Event Classification
Note on AT3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Slam shut activation - started in 2023
Note on AV3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low Customer Count - started in 2023
Note on AW3: Singer, Kevin D: N/A - Reg Stations did not contribute to OP Event

## Tracking2013 by Quarter (hidden)
3Q - 2013 OP Event Performance
| Q1 | Q2 | Q3 | Q4 | YTD | Yr-End
Expected Path: Goal OP events | 12 | 6 | 5 | 9 | 32 | 32
Amber Goal - Lowest end of range | 16 | 8 | 6 | 12 | 42 | 42
1Q Actual - All Events | 13 | 8 | 6 | 4 | 31 | 31
Asset Family OP Metrics
| Q1 | Q2 | Q3 | Q4 | YTD | Yr-End
Goal - HP Distribution | 2 | 1 | 1 | 2 | 6 | 6
1Q Actual - HP Distribution | 5 | 3 | 1 | 0 | 9 | 9
Goal - LP Distribution | 2 | 1 | 1 | 2 | 6 | 6
1Q Actual - LP Distribution | 0 | 1 | 1 | 1 | 3 | 3
Goal - Distribution Main Total | 4 | 2 | 2 | 4 | 12 | 12
1Q Actual - Distribution Main Total | 5 | 4 | 2 | 1 | 12 | 12
Goal - Distribution Services Total | 4 | 2 | 2 | 4 | 12 | 12
1Q Actual - Distribution Services Total | 5 | 4 | 2 | 1 | 12 | 12
Goal - Transmission | 8 | 4 | 3 | 5 | 20 | 20
1Q Actual - Transmission | 8 | 4 | 4 | 3 | 19 | 19
Goal - All Large Excursions1 | 3 | 3 | 2 | 3 | 11 | 11
1Q Actual - Large Excursions - HP Distrib | 2 | 1 | 1 | 0 | 4 | 4
1Q Actual - Large Excursions - LP Distrib | 0 | 0 | 1 | 0 | 1 | 1
1Q Actual - Large Excursions - Transmission | 3 | 0 | 1 | 1 | 5 | 5
1Q Actual - Total All Large Excursions | 5 | 1 | 3 | 1 | 10 | 10
Goal - All Equipment Failure | 4 | 3 | 3 | 3 | 13 | 13
1Q Actual - All Equipment Failure | 5 | 5 | 3 | 2 | 15 | 15
Goal - All Operator Error | 5 | 3 | 3 | 3 | 14 | 14
1Q Actual - All Operator Error | 7 | 3 | 2 | 2 | 14 | 14
Goal - At Compressor Stn or Storage | 1 | 1 | 1 | 1 | 4 | 4
1Q Actual - At Compressor Stn or Storage | 0 | 0 | 0 | 0 | 0 | 0
1 - Large Excursions are defined as:
HP Distribution = P ≥ MOP + 10%
LP Distribution = P ≥ 16" H2O
Transmission = P ≥ MOP + 10 psi
All OP events on Distribution Mains assumed to occur also on Distribution Services (no pressure monitoring on distribution services to determine extent of dist main OP event).
Large Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2013 Q3 Goal
HP Distribution |  | 1
LP Distribution |  |  | 1
Transmission | 3 |  | 1
Grand Total | 3 | 1 | 2 | 2
Small Excursion OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2013 Q3 Goal
HP Distribution | 11
LP Distribution | 164
Transmission | 19 | 5 | 3
Grand Total | 194 | 5 | 3 | 3
Total OP Events | 2011 Q3 | 2012 Q3 | 2013 Q3 | 2013 Q3 Goal
HP Distribution | 11 | 1 | 0 | 1
LP Distribution | 164 | 0 | 1 | 1
Transmission | 22 | 5 | 4 | 3
Grand Total | 197 | 6 | 5 | 5
Metric Comparison - Prior Years - 3rd Quarter
OP Events by Apparent Cause - Third Quarter
2013 Total OP- 5 Events as of 9/30/13 |  |  |  |  | 2013 Large Excursion OP Events - 2 Events
Large Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2013 Q2 Goal
HP Distribution | 5 |  | 1
LP Distribution | 1
Transmission | 6 | 2
Grand Total | 12 | 2 | 1 | 3
Small Excursion OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2013 Q2 Goal
HP Distribution | 7 |  | 2
LP Distribution | 147 | 46 | 1
Transmission | 29 | 14 | 4
Grand Total | 183 | 60 | 7 | 3
Total OP Events | 2011 Q2 | 2012 Q2 | 2013 Q2 | 2013 Q2 Goal
HP Distribution | 12 | 0 | 3 | 1
LP Distribution | 148 | 46 | 1 | 1
Transmission | 35 | 16 | 4 | 4
Grand Total | 195 | 62 | 8 | 6
Metric Comparison - Prior Years - 2nd Quarter
OP Events by Apparent Cause - Second Quarter
2013 Total OP- 8 Events as of 7/2/13 |  |  |  |  | 2013 Large Excursion OP Events - 1 Events
Large Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2013 Q1 Goal
HP Distribution | 1 | 2 | 2
LP Distribution | 1 |  | 0
Transmission | 12 | 1 | 3
Grand Total | 14 | 3 | 5 | 3
Small Excursion OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2013 Q1 Goal
HP Distribution | 4 | 2 | 3
LP Distribution | 172 | 179 | 0
Transmission | 29 | 44 | 5
Grand Total | 205 | 225 | 8 | 9
Total OP Events | 2011 Q1 | 2012 Q1 | 2013 Q1 | 2013 Q1 Goal
HP Distribution | 5 | 4 | 5 | 2
LP Distribution | 173 | 179 |  | 2
Transmission | 41 | 45 | 8 | 8
Grand Total | 219 | 228 | 13 | 12
Metric Comparison - Prior Years - First Quarter
OP Events by Apparent Cause - First Quarter
2013 Total OP- 13 Events as of 3/31/13 |  |  |  |  | 2013 Large Excursion OP Events - 5 Events

## Fact Finding (hidden)
Purpose
This document established the fundamental guidelines for questions to investigate to determine the apparent cause of an over pressure event.
The responses to the questions will be incorporated into the over pressure event report, prepared by Gas Control Operations Engineering.
This is an all-encompassing list; some questions may not apply to all over pressure events.
Equipment condition
The following questions are asked to establish the equipment condition and maintenance history of the equipment:
1. Review maintenance Records for the past five (5) years and the latest District Reg Data Sheet
2. When was the station built? To understand the standard design used
3. According to the maintenance records does this station have a history of issues? Sulfur, Water, Lock up?
a. Was there anything discovered in the regulators such as a debris, sulfur, or water?
b. What was the problem with the regulator? Did the monitor catch a potential over pressure?
4. What is the model and manufacturer of the regulator? If Mooney reg, what was the pressure difference across the reg, below 100 psig?
a. Review MPR for equipment type to see if there are known issues
5. When was the gauge last calibrated? What is the gauge serial #?
6. Was the correct spring color installed in reg and monitor?
7. Were there any hard to operate valves involved in the OP event?
8. Is there a history of vault flooding (water lines on vault walls, pumping history)?
a. Are the vents to the top of vault or above ground?
9. Were there any jobs that were recently completed at this location or in the vicinity? If so, what type of work was done?
10. Has hydro testing been completed in the area or upstream piping recently?
a. What were the dew point measurement readings of those projects?
11. When were any ILI activities completed on the upstream piping?
12. Review commissioning documentation or PSSR documentation
13. Was there excessive corrosion on the inside of the piping or equipment?
14. What were the results from MCTL?
15. Is there additional information subsequent to the borescope if completed?
16. Provide necessary pictures.
Overpressure Response
The following questions should be reviewed with the first responder and/or team who responded:
1. What was in control upon arriving to the site - Regulator or Monitor? And what were the As Found set points?
2. How was the station set up upon arrival (as far as valving is concerned in relation to the OP Diagram)?
3. If repairs were done during the incident, what type of repair and/or maintenance was completed?
4. Was the D/S pressure gauged during inspection?
5. How was communication with the control room handed off? Responsible party? GDCC/GTCC?
6. Was the vault flooded when arriving on site?
7. Was there ice formation on the outside of the reg or monitor?
8. Was any ice or debris found inside the reg or monitor?
IF debris was discovered THEN:
a. Can you send it to the Measurement Control Test Lab?
b. Could you take some photos of the debris?
c. Was there any debris found in the monitor and filter? If so, take some photos of the debris?
d. What type of filter was installed at the station? Model and Make?
e. Was a Bore Scope performed? If so, what was the finding?
9. Was the filter properly installed? Seals properly seated?
10. What are the set points of the regulators as found/as left?
a. What valves are being referred to in correlation to the operating diagram?
b. Were the regulators and monitors in good working condition?
11. Was the sensing lines soap tested for leaks? If leak(s) found, where was the leak(s) located?
12. What type of bypass was utilized – hard bypass or temporary bypass? With U/S filter?
13. What time did you arrive on site?
System Operation
The following questions are asked to establish the equipment condition and maintenance history of the equipment:
1. What other regulator station(s) feeds this HIS/System?
2. Which ones were addressed by the field technician (upon their field visit)?
3. What is the MAOP/MOP downstream of the regulator set/customer side?
a. What is the set point of the regulator/monitor/relief valve/over pressure protection?
b. Any indication of internal or external irregularity in the reg set?
c. If a bypass was used, what was the size (diameter) of the bypass?
4. What is the upstream MAOP/MOP?
5. If SCADA is not installed where is the nearest SCADA location?
6. Is there any a paper chart record?
Clearance
The following questions are to be asked to investigate the nature of work being performed:
1. Was there a clearance associated to the event? If so, what is the clearance number?
a. Identify when clearance was written and approved in relation to work being executed, this should not be less than 10 days.
b. Which step did the overpressure occur during?
2. What did the JSSA address prior to starting the work? If so, what was mentioned during the safety tailboard (overpressure)?
a. Obtain a copy of the JSSA
3. When Gas Control Center called regarding the MOP excursion at which step where the crew performing? Simplified question – What was the last clearance step that was completed before the OP excursion?
4. Was a pre-clearance meeting and walk-down done before the work clearance started? Was it a thorough review and discussion?
5. Were the roles and responsibilities clearly defined before the clearance work was started? (Who is the clearance supervisor? Crew member location and responsible clearly defined?)
6. During the clearance work, were there any deviations from the clearance steps? If so, why and was it approved by clearance supervisor/gas control center?
7. Did the clearance have a local approver?
8. Could you anticipate the system response before executing each step? – Did you know what was supposed to happen to the system after executing each step?
Human Performance
The following questions are to be asked to investigate the influence of human performance:
1. What jobs did you have scheduled for the day?
a. Where there time pressures to complete any other work?
b. What day and time did the overpressure occur?
c. How long have people been on the job?
2. Was the field personnel OQ or had validated OQ listed in their record?
3. What documentation were you given prior to arriving on jobsite?
4. What is your familiarity with the job site and the station?
5. Were there traffic, noise, or other environmental issues or concerns?
a. What was the weather like on the day of the incident?
6. Did you call Gas Control and/or Supervisor prior to starting the job?
7. Are the drawings (Operating Diagram, P&ID, Operating Map, etc.) accurate and representative of the facility? (Submit a CAP for corrections)
8. How was your physical condition (Sick, stress, medication, tiredness, alertness and distractions)?
9. Where there other steps besides the normal approved practices used to respond to this issue? (e.g. shop made tools, shortcuts, tasks that have been done in the past but are not routinely done)
10. What do you think would have made this event have a different and positive outcome?

## LRGOP Risk Model Events (hidden)
Count | Year | Date | CAP | Point Name | Location | Summary | Regulator Station Involved? | Rebuild would have prevented? | Secondary OPP would have prevented? | Event accepted in 2024? | Event Category in OP Master | Threat in OP Master | T or D | Transmission Station Name | Transmission Op Diagram | Transmission Station Category | Regulation Type | Max Pressure | MAOP | % over MAOP | P | LOC | FLOC | LRGOP Tranche | LRGOP Assigned Threat | OP Master Threat | Threat Match? | LRGOP Subdriver | LRGOP Rollup Subdriver | OP Master Primary Event Category | Comments
1 | 2014 | 2014-01-07 10:32 | 7001252 | NV_RBL_R125 | DR 125 HOAG ROAD & MARY AVE (Corning) | Slug of pipeline liquids impacted regulation. | Yes | Yes | Yes | Yes | Gas Contaminants - Liquids | EQ | Distribution |  |  |  | Pilot-op | 66.98 | 60 | 11.63% | P5 | No | GD.STAT.DIST.00921 | Distribution - DREG | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Gas Contaminants - Liquids | OD 183968
2 | 2014 | 2014-01-10 17:44 | 7001315; 7003563 | KT2_PT0100B | Topock Compressor Station Topock1 Plant B K Suct Press | Two OP Events: (1) A split station operating mode combined with antiquated equipment resulted in risk of station shutdown and OP, (2) TCS Operator opened valve to reinitiate L-300B flow, however; he/she did not check pressure upstream and downtream as they were trained to do and actions resulted in second OP. | No |  |  | No | Maintenance Operations Quality | HU | Transmission | Topock Compressor Station | 383655 | Compressor (Manned) |  | 699 | 660 | 5.909% | P50.2 | No | GT.STAT.COMP.TOPOCK____ | N/A - C&P | [5 empty] | Maintenance Operations Quality
3 | 2014 | 2014-01-13 07:52 | 7001312 | NV_RBL_R125 | DR 125 HOAG ROAD & MARY AVE (Corning) | Fluids plugged the pilot filter and prevented the regulator from sensing correctly | Yes | Yes | Yes | Yes | Gas Contaminants - Liquids | EQ | Distribution |  |  |  | Pilot-op | 89.68 | 60 | 49.47% | P5 | No | GD.STAT.DIST.00921 | Distribution - DREG | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Gas Contaminants - Liquids | OD 183968
4 | 2014 | 2014-08-04 02:02 | 7005140 | JDL_PT0002 | Dolan Rd L301B | Clearance writers did not take into account that pressure would equalize across regulation when valve V-0.01 was closed; resulted in OP event. | Yes | No | No | Yes | Clearance Preparation | HU | Transmission | Dolan Road Meter Station | 083812 | Category A | Control Valve | 472.6 | 408 | 15.83% | P50.2 | No | GT.STAT.MISC.DOLNRDPLS_ | Transmission - Complex | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation
5 | 2014 | 2014-08-16 08:50 | 7005431; 7005698 | FAI_PT0002 | Acacia Station | Due to poor station design the distance between THYP-31 and THYP-32 was insufficient for the installed equipment to react quickly enough in the event of quick valve closures. | Yes | Yes | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Acacia Street Primary Regulator Station | 082229 | Category B | Pilot-op | 116.424 | 90 | 29.36% | P50.2 | No | GT.STAT.MISC.ACACIASTRG | Transmission - Simple | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
6 | 2014 | 2014-11-08 05:00 | 7008497 | Gauge | Customer - Sunsweet Dryer (Discovered 2015) | Unknown fluids passing the filters and entering the regulator and monitor prevented proper station operation. | Yes | Yes | Yes | Yes | Gas Contaminants - Liquids | EQ | Distribution |  |  |  | Pilot-op | 182 | 60 | 203.3% | P5 | No | GD.STAT.DIST.01482 | Distribution - DREG | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Gas Contaminants - Liquids | OD 0810123; GD.STAT.DIST.01482. Meter not shown on OD - may be downstream. May be low customer count DREG.
7 | 2014 | 2014-11-24 13:30 | 7016776 | Gauge | Customer - Mirassou Dryer (Discovered 2015) | Leaking bypass; HPR set had not been completely removed. | Yes | Yes | N/A | Yes | Clearance Preparation | HU | Distribution |  |  |  | Spring-op | 122 | 60 | 103.3% | P50.2 | No | GD.STAT.FTAP.00847 | Distribution - FTAP | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation
1 | 2015 | 2015-01-03 20:32 | 7008090 | FR_FRE_EX11 | Fresno Junction Distribution | Weld slag in regulator body and ice in pilot. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 70.6 | 60 | 17.67% | P5 | No | GD.STAT.DIST.01424 | Distribution - DREG | EQ | EQ | TRUE | Weld slag | EQ-Contaminants | Failure - Equipment
2 | 2015 | 2015-01-12 11:00 | 7008412 | Gauge | Customer - Alameda Hospital (14th & E 30th St) | Using temporary bypass reg w/no filter or OPP, weld slag failed regulator. | Yes | No | Yes | Yes | Gas Contaminants - Debris | EQ | Distribution |  |  |  | Pilot-op | 22 | 0.43321 | 4978% | P95.8 | No | GD.STAT.LPRS.00076 | Distribution - LP | EQ | EQ | TRUE | Weld slag | EQ-Contaminants | Gas Contaminants - Debris
3 | 2015 | 2015-03-24 10:29 | 7010357 | DI_PIT_S028_PT1 | Pittsburg North HIS | Technicians performed maintenance by opening an incorrect (MAOP separation) valve and did not fully return it to the closed postion. | No |  |  | No | Maintenance Operations Quality | HU | Distribution |  |  |  |  | 24.1 | 17 | 41.76% | P50.2 | No |  | N/A - Pipeline | [5 empty] | Maintenance Operations Quality
4 | 2015 | 2015-07-16 14:10 | 7014357 | SMS_PT0005 | Customer - Morning Star | Failure mode analysis not completed on losing flow signal during engineering review. Software problem in meter controller. | Yes | Yes | Yes | Yes | Design Issue |  | Transmission | Morning Star Meter and Regulator Station | 0807311 | LVC | Pilot-op | 128.7 | 95.4 | 34.91% | P5 | No | GT.STAT.LVCR.0000000523 | Transmission - LVC | IO | EQ | FALSE | Design Issue | IO-Design Issue | Design Issue
5 | 2015 | 2015-08-03 09:00 | 7015601 | BMD_PT0020 | McDonald Island Stn Suction | Improper clearance steps, inadequate review of clearance changes. | No |  |  | No | Maintenance Operations Quality | HU | Transmission | McDonald Island Compressor Station | 385179 | Storage |  | 1211 | 1025 | 18.15% | P50.2 | No | GT.STAT.COMP.MCDONLDISL | N/A - C&P | [5 empty] | Maintenance Operations Quality
6 | 2015 | 2015-08-06 10:49 | 7015706 | Gauge | Dixon Landing & Hwy 880 | Metallic weld slag on both regulator and monitor boots. | Yes | Yes | Yes | Yes | Clearance Preparation | HU | Distribution |  |  |  | Pilot-op | 154 | 38 | 305.3% | P95.8 | No | GD.STAT.DIST.00445 | Distribution - DREG | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation | OD 0808053. Assigned threat of EQ (failure due to weld slag) does not match OP Master (clearance prep).
7 | 2015 | 2015-08-28 11:23 | 7016683 | YO_TUR_S042 | Turlock LP HIS (ORANGE ST S/O W MAIN ST) | Firefighting water runoff filled up the regulating vault and submerged vent lines. Technican did not return vent lines to top of vault. | Yes | No | No | Yes | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 16 | 12 | 33.33% | P50.2 | No | GD.STAT.LPRS.00183 | Distribution - LP | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality | Slam-shut did not activate, possibly due to water intrusion.
1 | 2016 | 2016-04-07 11:53 | 7027290; 7027522 | SSW_PT0007 | Swingle Junction L-172 | Crew failed to secure valve positions during a clearance upon discovering a leak; depressurizing of the sense line caused the monitor valve to swing open. | Yes | No | No | Yes | Clearance Execution | HU | Transmission | Swingle Jct Regulator and Meter Station | 183987 | Category A | Control Valve | 562 | 520 | 8.077% | P50.2 | No | GT.STAT.MISC.SWINGLERMS | Transmission - Complex | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
2 | 2016 | 2016-06-02 13:00 | 7030546 | Gauge | Customer - Olam Spices (47641 West Nees Ave., Firebaugh) | Mainline filter was not installed correctly. Contaminants were discovered in regulator equipment during customer shut-in. | Yes | Yes | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Olam West Coast, Firebaugh | 0809529 | LVC | Pilot-op | 67 | 60 | 11.67% | P50.2 | No | GT.STAT.LVCR.0000000105 | Transmission - LVC | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
3 | 2016 | 2016-06-23 11:35 | 7031602 | JDL_PT0002 | Dolan Rd L301B | Regulated into blocked-in section of piping returning equipment to service at end of clearance. Written clearance had a poor sequence of operations for this activity. | Yes | No | No | Yes | Clearance Preparation | HU | Transmission | Dolan Road Meter Station | 083812 | Category A | Control Valve | 465.9 | 408 | 14.19% | P50.2 | No | GT.STAT.MISC.DOLNRDPLS_ | Transmission - Complex | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation
4 | 2016 | 2016-06-27 09:24 | 7031764 | Gauge | Floral Ave HPR (970 East Floral Ave. Selma) | Leakage through the bypass valve and the relief valve that did not relieve due to wrong spring installation caused a buildup of pressure on a single feed customer during low/no demand. | Yes | Yes | N/A | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Spring-op | 238 | 60 | 296.7% | P95.8 | No | GD.STAT.FTAP.05194 | Distribution - FTAP | EQ | EQ | TRUE | Leaking bypass | EQ-Leaking Valve | Failure - Equipment
5 | 2016 | 2016-07-16 18:18 | 7032831; 7032778 | Gauge | Customer - Kagome Foods (333 Johnson Rd, and Overland Ave Los Banos) - Pipeline Rupture, Gas Release | Regulator boot failed. Oversized equipment that was in service for an extensive period without a full inspection. Obsolete monitor common sense and bleed. TD-4540S does not specify timeframe to perform "B" inspection from the 2014 update. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Kagome Meter and Regulator Station | 0809545 | LVC | Pilot-op | 370 | 60 | 516.7% | P99.1 | Yes | GT.STAT.LVCR.0000000121 | Transmission - LVC | EQ | EQ | TRUE | Inadequate maintenance | EQ-Inadequate Maintenance | Failure - Equipment
6 | 2016 | 2016-08-10 15:00 | 7034290; 7034273 | Gauge | Fresno HPR (7630 S. Leonard Ave.) | Regulator failed to lock up due to equipment contaminants and poor maintenance. Also, vintage relief valve was set above the MAOP limit. | Yes | Yes | N/A | Yes | Gas Contaminants - Debris | EQ | Distribution |  |  |  | Spring-op | 84 | 60 | 40% | P50.7 | No | GD.STAT.FTAP.02254 - No longer found | Distribution - FTAP | EQ | EQ | TRUE | Inadequate maintenance | EQ-Inadequate Maintenance | Gas Contaminants - Debris
7 | 2016 | 2016-10-14 09:40 | 7037549 | SNH_PT0025 | North Sacramento Underground Holder (DFM 0614-04) | Pipe section was blown down in preparation for valve replacement resulting in regulator valve losing power gas and swinging open; caused a rapid increase of pressure. | Yes | No | No | Yes | Design Issue | HU | Transmission | North Sacramento Underground Holder | 382860 | Category A | Control Valve | 239 | 180 | 32.78% | P95.9 | No | GT.STAT.MISC.NSACHOLDER | Transmission - Complex | IO | IO | TRUE | Design Issue | IO-Design Issue | Design Issue
8 | 2016 | 2016-10-30 | 7038541 | Chart Recorder | Customer - Sensient Foods (Cressy Way & Walnut Ave) | Equipment failed to protect to downstream system after the customer went on a hot shutoff (rapid load change) - and the load dropped off almost instantaneously. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Sensient Natural Ingredients Meter and Regulator Station | 0813081 | LVC | Pilot-op | 67 | 60 | 11.67% | P50.7 | No | GT.STAT.LVCR.0000000218 | Transmission - LVC | EQ | EQ | TRUE | Rapid load change | EQ-Rapid Load Change | Failure - Equipment
9 | 2016 | 2016-11-03 15:30 | 7038547 | Gauge | Stanley Blvd & Bernal Ave (Pleasanton HIS) | GC M&C Crew failed to follow special instructions and call for I&R support prior to pinching the 3" plastic main adjacent to a distribution regulator station. | Yes | Yes | No | Yes | Clearance Execution | HU | Distribution |  |  |  | Pilot-op | 66 | 55 | 20% | P50.7 | No | GD.STAT.DIST.11157 | Distribution - DREG | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
10 | 2016 | 2016-12-20 06:03 | 7040178 | Gauge | Customer - Ingomar Packing Plant (Gas Release through Filter) | The clearance to hydrotest upstream inadvertently introduced contaminants into the regulation of the downstream system because steps were written in a manner which blew known downstream contaminants upstream. | Yes | Yes | Yes | Yes | Clearance Preparation | HU | Transmission | Ingomar Packing No. 1 | 0809549 | LVC | Pilot-op | 264 | 125 | 111.2% | P50.7 | No | GT.STAT.LVCR.0000000125 | Transmission - LVC | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation
1 | 2017 | 2017-01-25 | 7041620 | SA_FOL_RA04 | Folsom HIS (Bidwell & Oak) | Contaminants caused failure of station regulation and monitoring equipment contributed by the ILI in prior year. | Yes | Yes | Yes | Yes | Gas Contaminants - Debris | EQ | Distribution |  |  |  | Pilot-op | 114.7 | 60 | 91.17% | P95.9 | No | GD.STAT.DIST.01039 | Distribution - DREG | EQ | EQ | TRUE | Debris | EQ-Contaminants | Gas Contaminants - Debris
2 | 2017 | 2017-04-15 | 112772011 | Gauge | Customer - Monolith Cement | Free liquids, in the pipeline, accumulated in the inlet filter and regulator, reducing loading pressure at the regulator station. PG&E failed to recognize the risk that clearance activities have the potential to move contaminants in the pipeline effecting the operations of metering and regulator equipment. | Yes | Yes | Yes | Yes | Gas Contaminants - Liquids | EQ | Transmission | Monolith Cement Company Meter and Regulator Station | 082609 | LVC | Pilot-op | 663 | 335 | 97.91% | P50.7 | No | GT.STAT.LVCR.0000000711 | Transmission - LVC | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Gas Contaminants - Liquids
3 | 2017 | 2017-04-27 15:39 | 112819827 | BMD_PT2205 | McDonald Island - Gas Release Relief Valve | Layers of protection in the programming logic controller (suction and discharge valves), relief valve and pilot, and impairment process failed to protect piping from the overpressure event. | No |  |  | No | Failure - Equipment | EQ | Transmission | McDonald Island Compressor Station | 385179 | Storage |  | 2314 | 2160 | 7.13% | P95.10 | No | GT.STAT.COMP.MCDONLDISL | N/A - C&P | [5 empty] | Failure - Equipment
4 | 2017 | 2017-05-14 04:45 | 112879269 | KE_THP_I010 | Customer - Monolith Cement | Free liquids, in the pipeline, accumulated in the inlet filter and regulator, reducing loading pressure at the regulator station. PG&E failed to recognize the risk that clearance activities have the potential to move contaminants in the pipeline effecting the operations of metering and regulator equipment. | Yes | Yes | Yes | Yes | Gas Contaminants - Liquids | EQ | Transmission | Monolith Cement Company Meter and Regulator Station | 082609 | LVC | Pilot-op | 662 | 335 | 97.61% | P50.7 | No | GT.STAT.LVCR.0000000711 | Transmission - LVC | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Gas Contaminants - Liquids
5 | 2017 | 2017-07-30 18:00 | 113114495 | Chart Recorder | Beale Air Force Base (Warren Shingle Rd and H St) | Event identified by a chart run, a teardown of the station found debris in various portions of the station. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 73 | 60 | 21.67% | P50.7 | No | GD.STAT.DIST.11162 | Distribution - DREG | EQ | EQ | TRUE | Debris | EQ-Contaminants | Failure - Equipment | Op Diagram 0806087.
6 | 2017 | 2017-08-21 11:38 | 113181647 | Gauge | Customer - Spreckels Sugar (L-307A) | During annual maintenance, technician discovered a 20 ft section of pipe where pressure was 240 psig. By-pass valve (V-1) was leaking into the downstream resulting in an overpressure condition. | Yes | Yes | No | Yes | Failure - Equipment | EQ | Transmission | Spreckels Sugar Regulator Station | 082427 | LVC | Pilot-op | 241.8 | 145 | 66.76% | P50.7 | No | GT.STAT.MISC.SPRCKSUGRS | Transmission - LVC | EQ | EQ | TRUE | Leaking bypass | EQ-Leaking Valve | Failure - Equipment
7 | 2017 | 2017-09-28 13:55 | 113643635 | YO_FRB_I013 | Customer - Olam Spices (47641 West Nees Ave., Firebaugh) | Technicians did not address ongoing overpressure condition during maintenance. | Yes | Unknown | Unknown | Yes | Maintenance Operations Quality | HU | Transmission | Olam West Coast, Firebaugh | 0809529 | LVC | Pilot-op | 66.5 | 60 | 10.83% | P50.2 | No | GT.STAT.LVCR.0000000105 | Transmission - LVC | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
8 | 2017 | 2017-10-13 15:21 | 113738595 | Gauge | Customer - Chevron (GCUST20344) | 16-hour pressure recording not completed after A-inspection. | Yes | Unknown | Unknown | Yes | Maintenance Operations Quality | HU | Transmission | Chevron, Palmer E/O Derrick Meter and Regulator Station | 0810923 | LVC | Pilot-op | 465 | 200 | 132.5% | P50.2 | No | GT.STAT.LVCR.0000000231 | Transmission - LVC | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
9 | 2017 | 2017-10-21 16:34 | 113754369 | Gauge | Durham Ferry (w/o Kasson) T75 (L108) | 3rd Party struck regulator station removing senselines from the equipment. | Yes | No | Yes | Yes | Design Issue | HU | Distribution |  |  |  | Pilot-op | 450 | 60 | 650% | P99.1 | Yes | GD.STAT.DIST.01594 | Distribution - DREG | IO | IO | TRUE | Design Issue | IO-Design Issue | Design Issue | Op Diagram 0804910.
10 | 2017 | 2017-10-26 | 114157455 | Gauge | Customer - Chevron (DCUST1358) Discovered 1/5/18 | Check valve failure. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Coalinga-Chevron Meter and Regulator Station | 0810425 | LVC | Pilot-op | 365 | 175 | 108.6% | P50.7 | No | GT.STAT.LVCR.0000000232 | Transmission - LVC | EQ | EQ | TRUE | Leaking check valve | EQ-Leaking Valve | Failure - Equipment
11 | 2017 | 2017-10-31 07:45 | 113776779; 114049473 | YO_MDA_I017 | Customer - Spreckels Sugar (L-307A) | Leaking by-pass valve. | Yes | Yes | No | Yes | Failure - Equipment | EQ | Transmission | Spreckels Sugar Regulator Station | 082427 | LVC | Pilot-op | 166 | 145 | 14.48% | P50.7 | No | GT.STAT.MISC.SPRCKSUGRS | Transmission - LVC | EQ | EQ | TRUE | Leaking bypass | EQ-Leaking Valve | Failure - Equipment
1 | 2018 | 2018-07-22 08:00 | 114808684 | SBR_PT0002 | Customer - Roseville HPR (9100 Foothills Rd, Roseville), Pipeline Rupture, Gas Release | Weld debris entered the regulating equipment; oversized regulation. Pilot-operated FTAP. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission |  |  |  | Pilot-op | 480 | 60 | 700% | P99.1 | Yes | GD.STAT.FTAP.04054 | Transmission - LVC | EQ | EQ | TRUE | Debris | EQ-Contaminants | Failure - Equipment | Pilot-operated FTAP; considered LVC or FTAP?
2 | 2018 | 2018-10-08 | 115080794 | MiniAT | Customer - Ingomar Packing Plant #1 (Discovered 10/22/18), Los Banos | Sulfur identified between regulator diaphragm and grid. | Yes | Yes | Yes | Yes | Gas Contaminants - Sulfur | EQ | Transmission | Ingomar Packing No. 1 | 0809549 | LVC | Pilot-op | 650 | 125 | 420% | P95.8 | No | GT.STAT.LVCR.0000000125 | Transmission - LVC | EQ | EQ | TRUE | Sulfur | EQ-Contaminants | Gas Contaminants - Sulfur
3 | 2018 | 2018-11-16 21:00 | 115388527 | Gauge | Byron Meganos Regulator Station | Regulator failed to lock up due to the buildup of sulfur and debris in the pilot and on the regulator diaphragm; regulators and monitors were oversized. | Yes | Yes | Yes | Yes | Gas Contaminants - Sulfur | EQ | Transmission | Byron-Meganos Regulator Station | 0811604 | Category B | Pilot-op | 230 | 160 | 43.75% | P50.7 | No | GT.STAT.MISC.BYRONTAPRG | Transmission - Simple | EQ | EQ | TRUE | Sulfur | EQ-Contaminants | Gas Contaminants - Sulfur | Former Op Diagram 083697.
4 | 2018 | 2018-11-20 09:00 | 115413614 | MiniAT | Customer - Diamond Pet (GCUST5848) | Customer went offline with full stop and regulators failed to lock up. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Ripon Cogen Meter and Regulator Station | 0811615 | LVC | Pilot-op | 225 | 175 | 28.57% | P50.5 | No | GT.STAT.MISC.RIPONCOGEN; GT.STAT.LVCR.0000000313 | Transmission - LVC | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Failure - Equipment | Shown on obsolete Op Diagram 089436.
5 | 2018 | 2018-12-15 10:55 | 115524902 | YO_FRB_RC15 | Customer - Olam Spices (GCUST23373 - 47641 West Nees Ave., Firebaugh) | Pressure differential violated; weld slag in reg and monitor; slam-shut engaged but gas continued to leak-by. | Yes | No | No | Yes | Failure - Equipment | EQ | Transmission | Olam West Coast, Firebaugh | 0809529 | LVC | Pilot-op | 92 | 60 | 53.33% | P50.7 | No | GT.STAT.LVCR.0000000105 | Transmission - LVC | EQ | EQ | TRUE | Debris | EQ-Contaminants | Failure - Equipment
1 | 2019 | 2019-01-17 11:44 | 115705607 | FR_FRE_RA17 | Maple & Alluvial (A17) | Downstream fire valve was closed first during clearance; slam shut is not designed to provide overpressure protection in the events where gas flow is suddenly blocked downstream of the regulator station; inlet should have been closed first. | Yes | No | No | Yes | Clearance Preparation | HU | Distribution |  |  |  | Pilot-op | 82 | 60 | 36.67% | P50.2 | No | GD.STAT.DIST.11140 | Distribution - DREG | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation
2 | 2019 | 2019-04-02 11:42 | 116938286 | Gauge | Customer - CalPortland Cement (GCUST24322) - Riverside Cement Meter & Regulation Station (OD 082445) | Leaking bypass valves. | Yes | Yes | No | Yes | Failure - Equipment | EQ | Transmission | Riverside Cement Meter and Regulator Station | 082445 | LVC | Pilot-op | 107 | 60 | 78.33% | P50.7 | No | GT.STAT.LVCR.0000000230 | Transmission - LVC | EQ | EQ | TRUE | Leaking bypass | EQ-Leaking Valve | Failure - Equipment
3 | 2019 | 2019-05-30 | 117345165 | FLP_PT0004 | Customer - Liberty Packing | Customer operated PG&E-owned equipment. Token relief had not yet been installed. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Liberty Packing Meter and Regulator Station | 0806404 | LVC | Pilot-op | 641 | 400 | 60.25% | P50.5 | No | GT.STAT.LVCR.0000000258 | Transmission - LVC | EQ | EQ | TRUE | Rapid load change | EQ-Rapid Load Change | Failure - Equipment | Retrofit in 2019 was not a rebuild, so it did not include changing regulation equipment to comply with H-14, H-15, and H-80.
4 | 2019 | 2019-06-13 | 117445540 | MiniAT | Customer - Frank Toste | Poor condition of service regulator boot/diaphragm. | Yes |  |  | No | Failure - Equipment | EQ | Distribution |  |  |  |  | 80 | 60 | 33.33% | P50.7 | No | GD.SERV.FRES.00657.0001 | N/A - Distribution LVC | [5 empty] | Failure - Equipment | Distribution LVCM?
5 | 2019 | 2019-07-11 20:18 | 117595394 | FLP_PT0004 | Customer - Liberty Packing | Mooney Flowgrid regulator and monitor lacked response time required to lock up when the customer suddenly stopped flow. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Liberty Packing Meter and Regulator Station | 0806404 | LVC | Pilot-op | 470 | 400 | 17.5% | P50.7 | No | GT.STAT.LVCR.0000000258 | Transmission - LVC | EQ | EQ | TRUE | Rapid load change | EQ-Rapid Load Change | Failure - Equipment | Retrofit in 2019 was not a rebuild, so it did not include changing regulation equipment to comply with H-14, H-15, and H-80.
6 | 2019 | 2019-08-09 18:00 | 117753819 | MiniAT | Customer - CalPortland Cement (GCUST24322) - Riverside Cement Meter & Regulation Station (OD 082445) | Reg and monitor failed to lock-up due to wear on diaphragm. TD-4540S only required B inspection for due cause. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Riverside Cement Meter and Regulator Station | 082445 | LVC | Pilot-op | 86 | 60 | 43.33% | P50.7 | No | GT.STAT.LVCR.0000000230 | Transmission - LVC | EQ | EQ | TRUE | Inadequate maintenance | EQ-Inadequate Maintenance | Failure - Equipment | Single run LVCM. Per gas design standard H-80 rev 7 2016, Mooney Flowgrid must not be installed as both the regulator and monitor in a meter set. Application of Mooney Flowgrid regulators is best for installations with a continuous flow of gas.
7 | 2019 | 2019-10-18 10:28 | 118026345 | Gauge | Castroville Rd Farmtap | Temporary bypass during leak repair; expectation to throttle valve for pressure control not made verbally clear to GPOM Supervisor. | Yes | Yes | N/A | Yes | Clearance Execution | HU | Distribution |  |  |  | Spring-op | 80 | 60 | 33.33% | P50.2 | No | GD.STAT.FTAP.00161 | Distribution - FTAP | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
8 | 2019 | 2019-10-30 | 118123950 | Gauge | Sunworld Trailer Park (R-611) | Setpoints of reg and monitor based on obsolete drawing. | Yes | No | N/A | Yes | Clearance Preparation | HU | Distribution |  |  |  | Spring-op | 45 | 32 | 40.62% | P95.9 | No | GD.STAT.HPRS.10195 | Distribution - HPR | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation | New OD 0812037 and new FLOC GD.STAT.HPRS.11177
9 | 2019 | 2019-11-09 | 118197814 | MiniAT | Customer - Mouren Family Farms | Regulation failed to control pressure due to the debris in the regulation. | Yes |  |  | No | Failure - Equipment | EQ | Distribution |  |  |  |  | 79 | 60 | 31.67% | P50.7 | No | GD.SERV.FRES.01536.0001 | N/A - Distribution LVC | [5 empty] | Failure - Equipment
10 | 2019 | 2019-11-20 04:42 | 118190702 | CC_HST_S001 | Best Road, Hollister (H-64) | Work package was prepared with incorrect sense line configuration. | Yes | No | No | Yes | Clearance Preparation | HU | Distribution |  |  |  | Pilot-op | 84 | 60 | 40% | P95.9 | No | GD.STAT.DIST.00397 | Distribution - DREG | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance Preparation | OD 0807396
11 | 2019 | 2019-12-04 01:10 | 118240107 | MiniAT | Customer - Pacific Coast Producer (GCUST5847) | Mooney reg and monitor (oversized regulation) could not respond to customer shut-off. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Pacific Coast, Lodi Meter and Regulator Station | 0812872 | LVC | Pilot-op | 120 | 60 | 100% | P50.7 | No | GT.STAT.LVCR.0000000615 | Transmission - LVC | EQ | EQ | TRUE | Rapid load change | EQ-Rapid Load Change | Failure - Equipment
1 | 2020 | 2020-02-07 | 118505829 | Gauge | Customer - Trillium (DCUST1119) | Leaking check valve (customer owned) backpressurized PG&E equipment. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Trillium CNG, Millbrae Meter and Regulator Station | 0812689 | LVC | Pilot-op | 197 | 175 | 12.57% | P50.7 | No | GT.STAT.LVCR.0000000505 | Transmission - LVC | EQ | EQ | TRUE | Leaking check valve | EQ-Leaking Valve | Failure - Equipment
2 | 2020 | 2020-03-06 10:00 | 118649351 | THM_PT0110 | Hollister Meter Station | Manual clearance operations during sense line leak repair return to service. | Yes | No | No | Yes | Clearance Execution | HU | Transmission | Hollister Meter Station | 282255 | Category A | Control Valve | 569 | 304 | 87.17% | P50.2 | No | GT.STAT.MISC.HLLSTRPLS_ | Transmission - Complex | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
3 | 2020 | 2020-06-10 | 119144634 | FLP_PT0004 | Customer - Liberty Packing | Customer operations including, testing, start up, ramp down and shut down (on/off operations) exceeded the capacity of the PG&E regulation equipment. | Yes | Yes | Yes | Yes | Failure - Equipment | EQ | Transmission | Liberty Packing Meter and Regulator Station | 0806404 | LVC | Pilot-op | 651 | 400 | 62.75% | P50.5 | No | GT.STAT.LVCR.0000000258 | Transmission - LVC | EQ | EQ | TRUE | Rapid load change | EQ-Rapid Load Change | Failure - Equipment
4 | 2020 | 2020-06-25 10:43 | 119295179 | MI_HAY_RH02 | L105N (RH-02, RH-18) | Leaking inlet fire valves off L-105N. (Pressure was increased for ILI.) | Yes | Yes | No | Yes | Clearance Execution | HU | Distribution |  |  |  | Pilot-op | 308.5 | 250 | 23.4% | P50.7 | No | GD.STAT.DIST.00252; GD.STAT.DIST.00241 | Distribution - DREG | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
5 | 2020 | 2020-07-27 | 119518807 | CC_APT_RJ44 | McGregor Dr & New Brighton Rd (RJ44) - Aptos | Slam-shut activation signal had not yet been made live in Telvent; pressure increased while throttling the bypass valve to support dropping pressure in the HIS. | Yes | No | No | Yes | Maintenance Operations Quality; Gas Control Operations; Equipment Failure | HU | Distribution |  |  |  | Pilot-op | 38.9 | 30 | 29.67% | P50.2 | No | GD.STAT.DIST.00520 | Distribution - DREG | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality Gas Control Operations Equipment Failure
6 | 2020 | 2020-07-31 | 119618698 | MiniAT | Customer - Chevron (GCUST31127) | Leaking valve; lack of information on customer's pressure rating. | Yes | No |  | Yes | Failure - Equipment | EQ | Transmission | Chevron Coalinga Field (Sec 25) Meter and Reg Station | 0811830 | LVC | Pilot-op | 459 | 250 | 83.6% | P50.7 | No | GT.STAT.LVCR.0000000251 | Transmission - LVC | IO | EQ | FALSE | Records | IO-Records | Failure - Equipment | Records related. MAOP reassessed to be 498 psig. System of record updated on 9/23/2020.
7 | 2020 | 2020-08-05 11:43 | 119567547 | FFN_PT0002 | Fresno Gas Load Center | Large Mooney regulators are typically oversized and may not provide adequate control in low flow situations. Dead-ended system was created during maintenance. | Yes | Yes | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Fresno Gas Load Center | 3808517 | Category B | Pilot-op | 597.8 | 400 | 49.45% | P50.2 | No | GT.STAT.MISC.FRESNOLOAD | Transmission - Simple | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
8 | 2020 | 2020-08-13 12:00 | 119618698 | MiniAT | Customer - Chevron (GCUST31127) | Leaking valve; lack of information on customer's pressure rating. | Yes | No |  | Yes | Failure - Equipment | EQ | Transmission | Chevron Coalinga Field (Sec 25) Meter and Reg Station | 0811830 | LVC | Pilot-op | 459 | 250 | 83.6% | P50.7 | No | GT.STAT.LVCR.0000000251 | Transmission - LVC | IO | EQ | FALSE | Records | IO-Records | Failure - Equipment | Records related. MAOP reassessed to be 498 psig. System of record updated on 9/23/2020.
9 | 2020 | 2020-09-08 | 119727251 | SJ_SJS_RG55 | Almaden & Redmond | Leaking bypass during clearance; clearance lacked step to open vent valve which caused leaking bpass to go unnoticed. | Yes | Yes | No | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 232 | 60 | 286.7% | P95.8 | No | GD.STAT.DIST.00491 | Distribution - DREG | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance preparation | OD 0809690
1 | 2021 | 2021-05-10 11:31 | 121322720 | YO_PAT_RN13 | S First St & W. Las Palmas (RN13) | Leaking bypass. Sequence of operations did not identify and/or mitigate leaking bypass risk. | Yes | Yes | No | Yes | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 67.5 | 57 | 18.42% | P50.2 | No | GD.STAT.DIST.00687 | Distribution - DREG | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality | OD 0809032; could also be attributed to leaking bypass
2 | 2021 | 2021-07-17 | 121770121 | MiniAT | Customer - Rio Bravo Rocklin | Regulation failed to control pressure due to the debris in the regulation. | Yes | Yes | Yes | Yes | Gas Contaminants - Debris | EQ | Transmission | Rio Bravo, Rocklin Meter and Regulator Station | 0812907 | LVC | Spring-op | 179.11 | 130 | 37.78% | P50.7 | No | GT.STAT.LVCR.0000000603 | Transmission - LVC | EQ | EQ | TRUE | Debris | EQ-Contaminants | Gas Contaminants - Debris
3 | 2021 | 2021-10-19 | 122229820 | Chart Recorder | Avenue 9 and Hwy 99 (RB-19) | Leaking bypass and lack of downstream fire valve. Tech neglected to reopen token relief after maintenance. Station no longer served an active customer. Delayed deployment of pressure recorder enabled discovery of OP. | Yes | Yes | No | Yes | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 73.4 | 60 | 22.33% | P50.2 | No | GD.STAT.DIST.11232 - removed? | Distribution - DREG | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
4 | 2021 | 2021-11-19 10:33 | 122400086 | EB_OAK_RB12 | 86th Ave & International Blvd (RB12) | Clearance execution resulted in the creation of a dead-end system. Slam-shut equipment operated as intended. | Yes | No | No | Yes | Clearance preparation | HU | Distribution |  |  |  | Pilot-op | 33.4 | 25 | 33.6% | P50.7 | No | GD.STAT.DIST.01566 | Distribution - DREG | IO | IO | TRUE | Clearance Preparation | IO-Clearance | Clearance preparation | OD 0812022
5 | 2021 | 2021-12-17 20:15 | 122502982 | Gauge | Customer - SMUD Carosn ICE Cogen (AIS9326) | Documented outlet MAOP was incorrect and did not account for the potential of backpressure by higher-pressure gas from the customer. | Yes | No | No | Yes | Design/Process* | HU | Transmission | SMUD Carson Ice Cogen Meter and Regulator Station | 0813144 | LVC | Pilot-op | 620 | 412 | 50.49% | P50.6 | No | GT.STAT.LVCR.0000000539 | Transmission - LVC | IO | IO | TRUE | Records | IO-Records | Design/Process* | Leaking check valve
1 | 2022 | 2022-01-29 | 122903182 | Gauge | 721 Leveroni Rd (FTAP), Sonoma | Debris due to age and lack of maintenance on unlocatable FTAP. | Yes | Yes | N/A | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Spring-op | 75 | 60 | 25% | P50.2 | No | GD.STAT.FTAP.04934 | Distribution - FTAP | EQ | EQ | TRUE | Inadequate maintenance | EQ-Inadequate Maintenance | Failure - Equipment
2 | 2022 | 2022-03-16 11:00 | 123152084 | MiniAT | Customer - Chemical Lime | Regulation failed to control pressure due to sulfur in the station equipment. | Yes | Yes | Yes | Yes | Gas Contaminants - Sulfur | EQ | Transmission | Chemical Lime Co of Ariz Meter and Regulator Station | 0809592 | LVC | Pilot-op | 89.1 | 75 | 18.8% | P50.7 | No | GT.STAT.LVCR.0000000170 | Transmission - LVC | EQ | EQ | TRUE | Sulfur | EQ-Contaminants | Gas Contaminants - Sulfur
3 | 2022 | 2022-04-19 | 123369541 | Gauge | Tellis Gin Regulator Station | Gas contaminants resulted in regulation failing to control pressure. | Yes | Yes | Yes | Yes | Gas Contaminants - Debris | EQ | Transmission | Tellis Gin Regulator Station | 0806794 | Category B | Pilot-op | 357 | 230 | 55.22% | P50.7 | No | GT.STAT.MISC.TELLISGINR | Transmission - Simple | EQ | EQ | TRUE | Liquids | EQ-Contaminants | Gas Contaminants - Debris | Rebuilt with spring-op equipment.
4 | 2022 | 2022-05-17 | 123621903 | Gauge | Abel Road (WL-05), Williams | Leakage in the bypass and isolation valves resulted in downstream pressure increase. | Yes | Yes | No | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 100.4 | 60 | 67.33% | P50.7 | No | GD.STAT.DIST.01430 | Distribution - DREG | EQ | EQ | TRUE | Leaking bypass | EQ-Leaking Valve | Failure - Equipment | OD 0809421
5 | 2022 | 2022-07-25 10:00 | 124162441 | MI_LVM_RL20 | L-114 (Inlet piping off RL-20) | The MAOP of the bridle was inadvertently understood to be 720 psig during the clearance to transfer distribution regulator stations from L-114 to the adjacent L-303. | No |  |  | No | Design/Process* | TBD | [5 empty] | 706 | 497 | 42.05% | P50.6 | No | GD.STAT.DIST.11205 | N/A - Pipeline | [5 empty] | Design/Process* | OD 0812263
6 | 2022 | 2022-08-04 | 124236113 | PN_SM_RB07 | Pacific Blvd & 39th St, San Mateo | The crew failed to recognize the error-like situation and reseated the inlet fire valve with an open bypass. | Yes | No | Yes | Yes | Clearance Preparation/Execution* | HU | Distribution |  |  |  | Pilot-op | 52.4 | 34 | 54.12% | P50.2 | No | GD.STAT.DIST.00106 | Distribution - DREG | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Preparation/Execution* | OD 0804023
7 | 2022 | 2022-08-29 11:22 | 124391351 | REN_PT0002 | L-138 (Fresno Gas Load Center) | Valve that isolated two pipelines with different MAOPs was mistakenly opened. | Yes | No | No | Yes | Clearance Execution | HU | Transmission | Fresno Gas Load Center | 3808517 | Category B | Pilot-op | 612 | 495 | 23.64% | P95.6 | No | GT.STAT.MISC.FRESNOLOAD | Transmission - Simple | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
8 | 2022 | 2022-09-01 06:55 | 124433893 | HU_EUR_RR30 | Union St (DR-R30) | Vent valve was inadvertently closed creating a bottled section on the station outlet pipe. | Yes | No | Yes | Yes | Clearance Execution | HU | Distribution |  |  |  | Pilot-op | 127.3 | 50 | 154.6% | P50.2 | No | GD.STAT.DIST.01164 | Distribution - DREG | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution | OD 0811598
9 | 2022 | 2022-09-30 | 124600188 | MiniAT | Customer - Chevron San Ardo (highest pressure 8/19/22 - confirmed 9/30) | Possible backpressure from customer. | Yes | Yes | Yes | Yes | Records | TBD | Transmission | Chevron, San Ardo Meter and Regulator Station | 0813193 | LVC | Pilot-op | 184.3 | 125 | 47.44% | P50.6 | No | GT.STAT.LVCR.0000000316 | Transmission - LVC | IO | IO | TRUE | Records | IO-Records | Records
1 | 2023 | 2023-03-15 | 125668382 | KT2_PT0_10D | Topock Compressor Station |  | No |  |  | No | Failure - Equipment | EQ | Transmission | Topock Compressor Station | 383655 | Compressor (Manned) |  | 735.2 | 660 | 11.39% | P95.6 | No | GT.STAT.COMP.TOPOCK____ | N/A - C&P | [5 empty] | Failure - Equipment
2 | 2023 | 2023-03-29 | 125756464 | Gauged Pressure | Antioch Terminal |  | Yes |  |  | Yes | Failure- Equipment | EQ | Transmission | Antioch Terminal | 4807103 | Category A | Control Valve | 645.3 | 468 | 37.88% | P50.4 | No | GT.STAT.MISC.ANTGSTPLS_ | Transmission - Terminals | EQ | EQ | TRUE | Leaking valve | EQ-Leaking Valve | Failure- Equipment
3 | 2023 | 2023-04-12 | 125895048 | KE_EDW_R810_PT3 | Edward AFB Secondary Meter & Regulator Station |  | Yes |  |  | Yes | Clearance Execution | HU | Transmission | Edwards AFB Secondary Meter & Reg Sta (Large Volume Customer) | 087572 | LVC | Pilot-op (assumed) | 40.99 | 25 | 63.96% | P50.2 | No | GT.STAT.LVCR.0000000461 | Transmission - LVC | IO | IO | TRUE | Clearance Execution | IO-Clearance | Clearance Execution
4 | 2023 | 2023-05-15 | 126136492 | CC_LSB_S046_PT1 | Robak Dr. And Mar Monte Ave (J-43) |  | Yes |  |  | Yes | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 66.15 | 50 | 32.3% | P50.2 | No | GD.STAT.DIST.00519 | Distribution - DREG | IO | IO | TRUE | Maintenance | IO-Maintenance Quality | Maintenance Operations Quality
5 | 2023 | 2023-05-17 | 126155328 | MiniAT | Customer - Berkeley Asphalt Virginia St, Berkeley |  | Yes |  |  | Yes | Gas Contaminants - Debris | EQ | Transmission | Berkeley Asphalt Meter & Regulator Station (Large Volume Customer) | 0812805 | LVC | Pilot-op | 132 | 60 | 120% |  | No | GT.STAT.LVCR.0000000365 | Transmission - LVC | EQ | EQ | TRUE | Debris | EQ-Contaminants | Gas Contaminants - Debris

## Large OP Events (hidden)
Count | Year | Date | CAP | Point Name | Location | Summary | Regulator Station Involved? | Secondary OPP installed? | Event accepted in 2023? | Event accepted in 2021? | Event Category in OP Master | Threat in OP Master | T or D | Transmission Station Name | Transmission Op Diagram | Transmission Station Category | Regulation Type | Max Pressure | MAOP | % over MAOP | P | LOC | FLOC | 2023 Tranche | 2021 Tranche | 2023/2021 Tranche Match? | Assigned Threat | OP Master Threat | Threat Match? | Comments
1 | 2014 | 2014-01-07 10:32 | 7001252 | NV_RBL_R125 | DR 125 HOAG ROAD & MARY AVE (Corning) | Slug of pipeline liquids impacted regulation. | Yes |  | Yes | Yes | Gas Contaminants - Liquids | EQ | Distribution |  |  |  | Pilot-op | 66.98 | 60 | 11.63% | P5 | No | GD.STAT.DIST.00921 | Distribution - DREG | Distribution - DREG | TRUE | EQ | EQ | TRUE | OD 183968
2 | 2014 | 2014-01-10 17:44 | 7001315; 7003563 | KT2_PT0100B | Topock Compressor Station Topock1 Plant B K Suct Press | Two OP Events: (1) A split station operating mode combined with antiquated equipment resulted in risk of station shutdown and OP, (2) TCS Operator opened valve to reinitiate L-300B flow, however; he/she did not check pressure upstream and downtream as they were trained to do and actions resulted in second OP. | No |  | No | No | Maintenance Operations Quality | HU | Transmission | Topock Compressor Station | 383655 | Compressor (Manned) |  | 699 | 660 | 5.909% | P50.2 | No | GT.STAT.COMP.TOPOCK____
3 | 2014 | 2014-01-13 07:52 | 7001312 | NV_RBL_R125 | DR 125 HOAG ROAD & MARY AVE (Corning) | Fluids plugged the pilot filter and prevented the regulator from sensing correctly | Yes |  | Yes | Yes | Gas Contaminants - Liquids | EQ | Distribution |  |  |  | Pilot-op | 89.68 | 60 | 49.47% | P5 | No | GD.STAT.DIST.00921 | Distribution - DREG | Distribution - DREG | TRUE | EQ | EQ | TRUE | OD 183968
4 | 2014 | 2014-08-04 02:02 | 7005140 | JDL_PT0002 | Dolan Rd L301B | Clearance writers did not take into account that pressure would equalize across regulation when valve V-0.01 was closed; resulted in OP event. | Yes |  | Yes | Yes | Clearance Preparation | HU | Transmission | Dolan Road Meter Station | 083812 | Category A | Control Valve | 472.6 | 408 | 15.83% | P50.2 | No | GT.STAT.MISC.DOLNRDPLS_ | Transmission - Complex | Transmission - Complex | TRUE | IO | IO | TRUE
5 | 2014 | 2014-08-16 08:50 | 7005431; 7005698 | FAI_PT0002 | Acacia Station | Due to poor station design the distance between THYP-31 and THYP-32 was insufficient for the installed equipment to react quickly enough in the event of quick valve closures. | Yes |  | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Acacia Street Primary Regulator Station | 082229 | Category B | Pilot-op | 116.424 | 90 | 29.36% | P50.2 | No | GT.STAT.MISC.ACACIASTRG | Transmission - Simple | Transmission - Simple | TRUE | IO | IO | TRUE
6 | 2014 | 2014-11-08 05:00 | 7008497 | Gauge | Customer - Sunsweet Dryer (Discovered 2015) | Unknown fluids passing the filters and entering the regulator and monitor prevented proper station operation. | Yes |  | Yes | Yes | Gas Contaminants - Liquids | EQ | Distribution |  |  |  | Pilot-op | 182 | 60 | 203.3% | P5 | No | GD.STAT.DIST.01482 | Distribution - DREG | Transmission - LVC | FALSE | EQ | EQ | TRUE | OD 0810123; GD.STAT.DIST.01482. Meter not shown on OD - may be downstream. May be low customer count DREG.
7 | 2014 | 2014-11-24 13:30 | 7016776 | Gauge | Customer - Mirassou Dryer (Discovered 2015) | Leaking bypass; HPR set had not been completely removed. | Yes |  | Yes | Yes | Clearance Preparation | HU | Distribution |  |  |  | Spring-op | 122 | 60 | 103.3% | P50.2 | No | GD.STAT.FTAP.00847 | Distribution - FTAP | Distribution - FTAP | TRUE | IO | IO | TRUE
1 | 2015 | 2015-01-03 20:32 | 7008090 | FR_FRE_EX11 | Fresno Junction Distribution | Weld slag in regulator body and ice in pilot. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 70.6 | 60 | 17.67% | P5 | No | GD.STAT.DIST.01424 | Distribution - DREG | Distribution - DREG | TRUE | EQ | EQ | TRUE
2 | 2015 | 2015-01-12 11:00 | 7008412 | Gauge | Customer - Alameda Hospital (14th & E 30th St) | Using temporary bypass reg w/no filter or OPP, weld slag failed regulator. | Yes |  | Yes | Yes | Gas Contaminants - Debris | EQ | Distribution |  |  |  | Pilot-op | 22 | 0.43321 | 4978% | P95.8 | No | GD.STAT.LPRS.00076 | Distribution - LP | Distribution - LP | TRUE | EQ | EQ | TRUE
3 | 2015 | 2015-03-24 10:29 | 7010357 | DI_PIT_S028_PT1 | Pittsburg North HIS | Technicians performed maintenance by opening an incorrect (MAOP separation) valve and did not fully return it to the closed postion. | No |  | No | No | Maintenance Operations Quality | HU | Distribution |  |  |  |  | 24.1 | 17 | 41.76% | P50.2 | No
4 | 2015 | 2015-07-16 14:10 | 7014357 | SMS_PT0005 | Customer - Morning Star | Failure mode analysis not completed on losing flow signal during engineering review. Software problem in meter controller. | Yes |  | Yes | Yes | Design Issue |  | Transmission | Morning Star Meter and Regulator Station | 0807311 | LVC | Pilot-op | 128.7 | 95.4 | 34.91% | P5 | No | GT.STAT.LVCR.0000000523 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
5 | 2015 | 2015-08-03 09:00 | 7015601 | BMD_PT0020 | McDonald Island Stn Suction | Improper clearance steps, inadequate review of clearance changes. | No |  | No | No | Maintenance Operations Quality | HU | Transmission | McDonald Island Compressor Station | 385179 | Storage |  | 1211 | 1025 | 18.15% | P50.2 | No | GT.STAT.COMP.MCDONLDISL
6 | 2015 | 2015-08-06 10:49 | 7015706 | Gauge | Dixon Landing & Hwy 880 | Metallic weld slag on both regulator and monitor boots. | Yes |  | Yes | Yes | Clearance Preparation | HU | Distribution |  |  |  | Pilot-op | 154 | 38 | 305.3% | P95.8 | No | GD.STAT.DIST.00445 | Distribution - DREG | Transmission - Simple | FALSE | IO | IO | TRUE | OD 0808053. Assigned threat of EQ (failure due to weld slag) does not match OP Master (clearance prep).
7 | 2015 | 2015-08-28 11:23 | 7016683 | YO_TUR_S042 | Turlock LP HIS (ORANGE ST S/O W MAIN ST) | Firefighting water runoff filled up the regulating vault and submerged vent lines. Technican did not return vent lines to top of vault. | Yes |  | Yes | Yes | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 16 | 12 | 33.33% | P50.2 | No | GD.STAT.LPRS.00183 | Distribution - LP | Distribution - LP | TRUE | IO | IO | TRUE | Slam-shut did not activate, possibly due to water intrusion.
1 | 2016 | 2016-04-07 11:53 | 7027290; 7027522 | SSW_PT0007 | Swingle Junction L-172 | Crew failed to secure valve positions during a clearance upon discovering a leak; depressurizing of the sense line caused the monitor valve to swing open. | Yes |  | Yes | Yes | Clearance Execution | HU | Transmission | Swingle Jct Regulator and Meter Station | 183987 | Category A | Control Valve | 562 | 520 | 8.077% | P50.2 | No | GT.STAT.MISC.SWINGLERMS | Transmission - Complex | Transmission - Complex | TRUE | IO | IO | TRUE
2 | 2016 | 2016-06-02 13:00 | 7030546 | Gauge | Customer - Olam Spices (47641 West Nees Ave., Firebaugh) | Mainline filter was not installed correctly. Contaminants were discovered in regulator equipment during customer shut-in. | Yes |  | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Olam West Coast, Firebaugh | 0809529 | LVC | Pilot-op | 67 | 60 | 11.67% | P50.2 | No | GT.STAT.LVCR.0000000105 | Transmission - LVC | Transmission - LVC | TRUE | IO | IO | TRUE
3 | 2016 | 2016-06-23 11:35 | 7031602 | JDL_PT0002 | Dolan Rd L301B | Regulated into blocked-in section of piping returning equipment to service at end of clearance. Written clearance had a poor sequence of operations for this activity. | Yes |  | Yes | Yes | Clearance Preparation | HU | Transmission | Dolan Road Meter Station | 083812 | Category A | Control Valve | 465.9 | 408 | 14.19% | P50.2 | No | GT.STAT.MISC.DOLNRDPLS_ | Transmission - Complex | Transmission - Complex | TRUE | IO | IO | TRUE
4 | 2016 | 2016-06-27 09:24 | 7031764 | Gauge | Floral Ave HPR (970 East Floral Ave. Selma) | Leakage through the bypass valve and the relief valve that did not relieve due to wrong spring installation caused a buildup of pressure on a single feed customer during low/no demand. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Spring-op | 238 | 60 | 296.7% | P95.8 | No | GD.STAT.FTAP.05194 | Distribution - FTAP | Distribution - HPR | FALSE | EQ | EQ | TRUE
5 | 2016 | 2016-07-16 18:18 | 7032831; 7032778 | Gauge | Customer - Kagome Foods (333 Johnson Rd, and Overland Ave Los Banos) - Pipeline Rupture, Gas Release | Regulator boot failed. Oversized equipment that was in service for an extensive period without a full inspection. Obsolete monitor common sense and bleed. TD-4540S does not specify timeframe to perform "B" inspection from the 2014 update. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Kagome Meter and Regulator Station | 0809545 | LVC | Pilot-op | 370 | 60 | 516.7% | P99.1 | Yes | GT.STAT.LVCR.0000000121 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
6 | 2016 | 2016-08-10 15:00 | 7034290; 7034273 | Gauge | Fresno HPR (7630 S. Leonard Ave.) | Regulator failed to lock up due to equipment contaminants and poor maintenance. Also, vintage relief valve was set above the MAOP limit. | Yes |  | Yes | Yes | Gas Contaminants - Debris | EQ | Distribution |  |  |  | Spring-op | 84 | 60 | 40% | P50.7 | No | GD.STAT.FTAP.02254 - No longer found | Distribution - FTAP | Distribution - FTAP | TRUE | EQ | EQ | TRUE
7 | 2016 | 2016-10-14 09:40 | 7037549 | SNH_PT0025 | North Sacramento Underground Holder (DFM 0614-04) | Pipe section was blown down in preparation for valve replacement resulting in regulator valve losing power gas and swinging open; caused a rapid increase of pressure. | Yes |  | Yes | Yes | Design Issue | HU | Transmission | North Sacramento Underground Holder | 382860 | Category A | Control Valve | 239 | 180 | 32.78% | P95.9 | No | GT.STAT.MISC.NSACHOLDER | Transmission - Complex | Transmission - Complex | TRUE | IO | IO | TRUE
8 | 2016 | 2016-10-30 | 7038541 | Chart Recorder | Customer - Sensient Foods (Cressy Way & Walnut Ave) | Equipment failed to protect to downstream system after the customer went on a hot shutoff (rapid load change) - and the load dropped off almost instantaneously. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Sensient Natural Ingredients Meter and Regulator Station | 0813081 | LVC | Pilot-op | 67 | 60 | 11.67% | P50.7 | No | GT.STAT.LVCR.0000000218 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
9 | 2016 | 2016-11-03 15:30 | 7038547 | Gauge | Stanley Blvd & Bernal Ave (Pleasanton HIS) | GC M&C Crew failed to follow special instructions and call for I&R support prior to pinching the 3" plastic main adjacent to a distribution regulator station. | Yes |  | Yes | Yes | Clearance Execution | HU | Distribution |  |  |  | Pilot-op | 66 | 55 | 20% | P50.7 | No | GD.STAT.DIST.11157 | Distribution - DREG | Distribution - DREG | TRUE | IO | IO | TRUE
10 | 2016 | 2016-12-20 06:03 | 7040178 | Gauge | Customer - Ingomar Packing Plant (Gas Release through Filter) | The clearance to hydrotest upstream inadvertently introduced contaminants into the regulation of the downstream system because steps were written in a manner which blew known downstream contaminants upstream. | Yes |  | Yes | Yes | Clearance Preparation | HU | Transmission | Ingomar Packing No. 1 | 0809549 | LVC | Pilot-op | 264 | 125 | 111.2% | P50.7 | No | GT.STAT.LVCR.0000000125 | Transmission - LVC | Transmission - LVC | TRUE | IO | IO | TRUE
1 | 2017 | 2017-01-25 | 7041620 | SA_FOL_RA04 | Folsom HIS (Bidwell & Oak) | Contaminants caused failure of station regulation and monitoring equipment contributed by the ILI in prior year. | Yes |  | Yes | Yes | Gas Contaminants - Debris | EQ | Distribution |  |  |  | Pilot-op | 114.7 | 60 | 91.17% | P95.9 | No | GD.STAT.DIST.01039 | Distribution - DREG | Distribution - DREG | TRUE | EQ | EQ | TRUE
2 | 2017 | 2017-04-15 | 112772011 | Gauge | Customer - Monolith Cement | Free liquids, in the pipeline, accumulated in the inlet filter and regulator, reducing loading pressure at the regulator station. PG&E failed to recognize the risk that clearance activities have the potential to move contaminants in the pipeline effecting the operations of metering and regulator equipment. | Yes |  | Yes | Yes | Gas Contaminants - Liquids | EQ | Transmission | Monolith Cement Company Meter and Regulator Station | 082609 | LVC | Pilot-op | 663 | 335 | 97.91% | P50.7 | No | GT.STAT.LVCR.0000000711 | Transmission - LVC | Transmission - Simple | FALSE | EQ | EQ | TRUE
3 | 2017 | 2017-04-27 15:39 | 112819827 | BMD_PT2205 | McDonald Island - Gas Release Relief Valve | Layers of protection in the programming logic controller (suction and discharge valves), relief valve and pilot, and impairment process failed to protect piping from the overpressure event. | No |  | No | No | Failure - Equipment | EQ | Transmission | McDonald Island Compressor Station | 385179 | Storage |  | 2314 | 2160 | 7.13% | P95.10 | No | GT.STAT.COMP.MCDONLDISL
4 | 2017 | 2017-05-14 04:45 | 112879269 | KE_THP_I010 | Customer - Monolith Cement | Free liquids, in the pipeline, accumulated in the inlet filter and regulator, reducing loading pressure at the regulator station. PG&E failed to recognize the risk that clearance activities have the potential to move contaminants in the pipeline effecting the operations of metering and regulator equipment. | Yes |  | Yes | Yes | Gas Contaminants - Liquids | EQ | Transmission | Monolith Cement Company Meter and Regulator Station | 082609 | LVC | Pilot-op | 662 | 335 | 97.61% | P50.7 | No | GT.STAT.LVCR.0000000711 | Transmission - LVC | Transmission - Simple | FALSE | EQ | EQ | TRUE
5 | 2017 | 2017-07-30 18:00 | 113114495 | Chart Recorder | Beale Air Force Base (Warren Shingle Rd and H St) | Event identified by a chart run, a teardown of the station found debris in various portions of the station. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 73 | 60 | 21.67% | P50.7 | No | GD.STAT.DIST.11162 | Distribution - DREG | Distribution - DREG | TRUE | EQ | EQ | TRUE | Op Diagram 0806087.
6 | 2017 | 2017-08-21 11:38 | 113181647 | Gauge | Customer - Spreckels Sugar (L-307A) | During annual maintenance, technician discovered a 20 ft section of pipe where pressure was 240 psig. By-pass valve (V-1) was leaking into the downstream resulting in an overpressure condition. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Spreckels Sugar Regulator Station | 082427 | LVC | Pilot-op | 241.8 | 145 | 66.76% | P50.7 | No | GT.STAT.MISC.SPRCKSUGRS | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
7 | 2017 | 2017-09-28 13:55 | 113643635 | YO_FRB_I013 | Customer - Olam Spices (47641 West Nees Ave., Firebaugh) | Technicians did not address ongoing overpressure condition during maintenance. | Yes |  | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Olam West Coast, Firebaugh | 0809529 | LVC | Pilot-op | 66.5 | 60 | 10.83% | P50.2 | No | GT.STAT.LVCR.0000000105 | Transmission - LVC | Transmission - LVC | TRUE | IO | IO | TRUE
8 | 2017 | 2017-10-13 15:21 | 113738595 | Gauge | Customer - Chevron (GCUST20344) | 16-hour pressure recording not completed after A-inspection. | Yes |  | Yes | Yes | Maintenance Operations Quality | HU | Transmission | Chevron, Palmer E/O Derrick Meter and Regulator Station | 0810923 | LVC | Pilot-op | 465 | 200 | 132.5% | P50.2 | No | GT.STAT.LVCR.0000000231 | Transmission - LVC | Transmission - LVC | TRUE | IO | IO | TRUE
9 | 2017 | 2017-10-21 16:34 | 113754369 | Gauge | Durham Ferry (w/o Kasson) T75 (L108) | 3rd Party struck regulator station removing senselines from the equipment. | Yes |  | Yes | Yes | Design Issue | HU | Distribution |  |  |  | Pilot-op | 450 | 60 | 650% | P95.8 | Yes | GD.STAT.DIST.01594 | Distribution - DREG | Distribution - DREG | TRUE | IO | IO | TRUE | Op Diagram 0804910.
10 | 2017 | 2017-10-26 | 114157455 | Gauge | Customer - Chevron (DCUST1358) Discovered 1/5/18 | Check valve failure. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Coalinga-Chevron Meter and Regulator Station | 0810425 | LVC | Pilot-op | 365 | 175 | 108.6% | P50.7 | No | GT.STAT.LVCR.0000000232 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
11 | 2017 | 2017-10-31 07:45 | 113776779; 114049473 | YO_MDA_I017 | Customer - Spreckels Sugar (L-307A) | Leaking by-pass valve. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Spreckels Sugar Regulator Station | 082427 | LVC | Pilot-op | 166 | 145 | 14.48% | P50.7 | No | GT.STAT.MISC.SPRCKSUGRS | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
1 | 2018 | 2018-07-22 08:00 | 114808684 | SBR_PT0002 | Customer - Roseville HPR (9100 Foothills Rd, Roseville), Pipeline Rupture, Gas Release | Weld debris entered the regulating equipment; oversized regulation. Pilot-operated FTAP. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission |  |  |  | Pilot-op | 480 | 60 | 700% | P99.1 | Yes | GD.STAT.FTAP.04054 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE | Pilot-operated FTAP; considered LVC or FTAP?
2 | 2018 | 2018-10-08 | 115080794 | MiniAT | Customer - Ingomar Packing Plant #1 (Discovered 10/22/18), Los Banos | Sulfur identified between regulator diaphragm and grid. | Yes |  | Yes | Yes | Gas Contaminants - Sulfur | EQ | Transmission | Ingomar Packing No. 1 | 0809549 | LVC | Pilot-op | 650 | 125 | 420% | P95.8 | No | GT.STAT.LVCR.0000000125 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
3 | 2018 | 2018-11-16 21:00 | 115388527 | Gauge | Byron Meganos Regulator Station | Regulator failed to lock up due to the buildup of sulfur and debris in the pilot and on the regulator diaphragm; regulators and monitors were oversized. | Yes |  | Yes | Yes | Gas Contaminants - Sulfur | EQ | Transmission | Byron-Meganos Regulator Station | 0811604 | Category B | Pilot-op | 230 | 160 | 43.75% | P50.7 | No | GT.STAT.MISC.BYRONTAPRG | Transmission - Simple | Transmission - Simple | TRUE | EQ | EQ | TRUE | Former Op Diagram 083697.
4 | 2018 | 2018-11-20 09:00 | 115413614 | MiniAT | Customer - Diamond Pet (GCUST5848) | Customer went offline with full stop and regulators failed to lock up. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Ripon Cogen Meter and Regulator Station | 0811615 | LVC | Pilot-op | 225 | 175 | 28.57% | P50.5 | No | GT.STAT.MISC.RIPONCOGEN; GT.STAT.LVCR.0000000313 | Transmission - LVC | Farm Tap | FALSE | EQ | EQ | TRUE | Shown on obsolete Op Diagram 089436.
5 | 2018 | 2018-12-15 10:55 | 115524902 | YO_FRB_RC15 | Customer - Olam Spices (GCUST23373 - 47641 West Nees Ave., Firebaugh) | Pressure differential violated; weld slag in reg and monitor; slam-shut engaged but gas continued to leak-by. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Olam West Coast, Firebaugh | 0809529 | LVC | Pilot-op | 92 | 60 | 53.33% | P50.7 | No | GT.STAT.LVCR.0000000105 | Transmission - LVC | HPR | FALSE | EQ | EQ | TRUE
1 | 2019 | 2019-01-17 11:44 | 115705607 | FR_FRE_RA17 | Maple & Alluvial (A17) | Downstream fire valve was closed first during clearance; slam shut is not designed to provide overpressure protection in the events where gas flow is suddenly blocked downstream of the regulator station; inlet should have been closed first. | Yes |  | Yes | Yes | Clearance Preparation | HU | Distribution |  |  |  | Pilot-op | 82 | 60 | 36.67% | P50.2 | No | GD.STAT.DIST.11140 | Distribution - DREG | Distribution - DREG | TRUE | IO | IO | TRUE
2 | 2019 | 2019-04-02 11:42 | 116938286 | Gauge | Customer - CalPortland Cement (GCUST24322) - Riverside Cement Meter & Regulation Station (OD 082445) | Leaking bypass valves. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Riverside Cement Meter and Regulator Station | 082445 | LVC | Pilot-op | 107 | 60 | 78.33% | P50.7 | No | GT.STAT.LVCR.0000000230 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
3 | 2019 | 2019-05-30 | 117345165 | FLP_PT0004 | Customer - Liberty Packing | Customer operated PG&E-owned equipment. Token relief had not yet been installed. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Liberty Packing Meter and Regulator Station | 0806404 | LVC | Pilot-op | 641 | 400 | 60.25% | P50.5 | No | GT.STAT.LVCR.0000000258 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE | Retrofit in 2019 was not a rebuild, so it did not include changing regulation equipment to comply with H-14, H-15, and H-80.
4 | 2019 | 2019-06-13 | 117445540 | MiniAT | Customer - Frank Toste | Poor condition of service regulator boot/diaphragm. | Yes |  | No | Yes | Failure - Equipment | EQ | Distribution |  |  |  |  | 80 | 60 | 33.33% | P50.7 | No | GD.SERV.FRES.00657.0001 |  | Transmission - LVC |  |  |  |  | Distribution LVCM?
5 | 2019 | 2019-07-11 20:18 | 117595394 | FLP_PT0004 | Customer - Liberty Packing | Mooney Flowgrid regulator and monitor lacked response time required to lock up when the customer suddenly stopped flow. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Liberty Packing Meter and Regulator Station | 0806404 | LVC | Pilot-op | 470 | 400 | 17.5% | P50.7 | No | GT.STAT.LVCR.0000000258 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE | Retrofit in 2019 was not a rebuild, so it did not include changing regulation equipment to comply with H-14, H-15, and H-80.
6 | 2019 | 2019-08-09 18:00 | 117753819 | MiniAT | Customer - CalPortland Cement (GCUST24322) - Riverside Cement Meter & Regulation Station (OD 082445) | Reg and monitor failed to lock-up due to wear on diaphragm. TD-4540S only required B inspection for due cause. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Riverside Cement Meter and Regulator Station | 082445 | LVC | Pilot-op | 86 | 60 | 43.33% | P50.7 | No | GT.STAT.LVCR.0000000230 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE | Single run LVCM. Per gas design standard H-80 rev 7 2016, Mooney Flowgrid must not be installed as both the regulator and monitor in a meter set. Application of Mooney Flowgrid regulators is best for installations with a continuous flow of gas.
7 | 2019 | 2019-10-18 10:28 | 118026345 | Gauge | Castroville Rd Farmtap | Temporary bypass during leak repair; expectation to throttle valve for pressure control not made verbally clear to GPOM Supervisor. | Yes |  | Yes | Yes | Clearance Execution | HU | Distribution |  |  |  | Spring-op | 80 | 60 | 33.33% | P50.2 | No | GD.STAT.FTAP.00161 | Distribution - FTAP | Distribution - FTAP | TRUE | IO | IO | TRUE
8 | 2019 | 2019-10-30 | 118123950 | Gauge | Sunworld Trailer Park (R-611) | Setpoints of reg and monitor based on obsolete drawing. | Yes |  | Yes | Yes | Clearance Preparation | HU | Distribution |  |  |  | Spring-op | 45 | 32 | 40.62% | P95.9 | No | GD.STAT.HPRS.10195 | Distribution - HPR | Distribution - HPR | TRUE | IO | IO | TRUE | New OD 0812037 and new FLOC GD.STAT.HPRS.11177
9 | 2019 | 2019-11-09 | 118197814 | MiniAT | Customer - Mouren Family Farms | Regulation failed to control pressure due to the debris in the regulation. | Yes |  | No | Yes | Failure - Equipment | EQ | Distribution |  |  |  |  | 79 | 60 | 31.67% | P50.7 | No | GD.SERV.FRES.01536.0001 |  | Distribution - FTAP
10 | 2019 | 2019-11-20 04:42 | 118190702 | CC_HST_S001 | Best Road, Hollister (H-64) | Work package was prepared with incorrect sense line configuration. | Yes |  | Yes | Yes | Clearance Preparation | HU | Distribution |  |  |  | Pilot-op | 84 | 60 | 40% | P95.9 | No | GD.STAT.DIST.00397 | Distribution - DREG | Distribution - DREG | TRUE | IO | IO | TRUE | OD 0807396
11 | 2019 | 2019-12-04 01:10 | 118240107 | MiniAT | Customer - Pacific Coast Producer (GCUST5847) | Mooney reg and monitor (oversized regulation) could not respond to customer shut-off. | Yes |  | Yes | Yes | Failure - Equipment | EQ | Transmission | Pacific Coast, Lodi Meter and Regulator Station | 0812872 | LVC | Pilot-op | 120 | 60 | 100% | P50.7 | No | GT.STAT.LVCR.0000000615 | Transmission - LVC | Transmission - LVC | TRUE | EQ | EQ | TRUE
1 | 2020 | 2020-02-07 | 118505829 | Gauge | Customer - Trillium (DCUST1119) | Leaking check valve (customer owned) backpressurized PG&E equipment. | Yes |  | Yes | N/A | Failure - Equipment | EQ | Transmission | Trillium CNG, Millbrae Meter and Regulator Station | 0812689 | LVC | Pilot-op | 197 | 175 | 12.57% | P50.7 | No | GT.STAT.LVCR.0000000505 | Transmission - LVC |  |  | EQ | EQ | TRUE
2 | 2020 | 2020-03-06 10:00 | 118649351 | THM_PT0110 | Hollister Meter Station | Manual clearance operations during sense line leak repair return to service. | Yes |  | Yes | N/A | Clearance Execution | HU | Transmission | Hollister Meter Station | 282255 | Category A | Control Valve | 569 | 304 | 87.17% | P50.2 | No | GT.STAT.MISC.HLLSTRPLS_ | Transmission - Complex |  |  | IO | IO | TRUE
3 | 2020 | 2020-06-10 | 119144634 | FLP_PT0004 | Customer - Liberty Packing | Customer operations including, testing, start up, ramp down and shut down (on/off operations) exceeded the capacity of the PG&E regulation equipment. | Yes |  | Yes | N/A | Failure - Equipment | EQ | Transmission | Liberty Packing Meter and Regulator Station | 0806404 | LVC | Pilot-op | 651 | 400 | 62.75% | P50.5 | No | GT.STAT.LVCR.0000000258 | Transmission - LVC |  |  | EQ | EQ | TRUE
4 | 2020 | 2020-06-25 10:43 | 119295179 | MI_HAY_RH02 | L105N (RH-02, RH-18) | Leaking inlet fire valves off L-105N. (Pressure was increased for ILI.) | Yes |  | Yes | N/A | Clearance Execution | HU | Distribution |  |  |  | Pilot-op | 308.5 | 250 | 23.4% | P50.7 | No | GD.STAT.DIST.00252; GD.STAT.DIST.00241 | Distribution - DREG |  |  | IO | IO | TRUE
5 | 2020 | 2020-07-27 | 119518807 | CC_APT_RJ44 | McGregor Dr & New Brighton Rd (RJ44) - Aptos | Slam-shut activation signal had not yet been made live in Telvent; pressure increased while throttling the bypass valve to support dropping pressure in the HIS. | Yes |  | Yes | N/A | Maintenance Operations Quality; Gas Control Operations; Equipment Failure | HU | Distribution |  |  |  | Pilot-op | 38.9 | 30 | 29.67% | P50.2 | No | GD.STAT.DIST.00520 | Distribution - DREG |  |  | IO | IO | TRUE
6 | 2020 | 2020-07-31 | 119618698 | MiniAT | Customer - Chevron (GCUST31127) | Leaking valve; lack of information on customer's pressure rating. | Yes |  | No | N/A | Failure - Equipment | EQ | Transmission | Chevron Coalinga Field (Sec 25) Meter and Reg Station | 0811830 | LVC | Pilot-op | 459 | 250 | 83.6% | P50.7 | No | GT.STAT.LVCR.0000000251 | [6 empty] | Records related. MAOP reassessed to be 498 psig. System of record updated on 9/23/2020.
7 | 2020 | 2020-08-05 11:43 | 119567547 | FFN_PT0002 | Fresno Gas Load Center | Large Mooney regulators are typically oversized and may not provide adequate control in low flow situations. Dead-ended system was created during maintenance. | Yes |  | Yes | N/A | Maintenance Operations Quality | HU | Transmission | Fresno Gas Load Center | 3808517 | Category B | Pilot-op | 597.8 | 400 | 49.45% | P50.2 | No | GT.STAT.MISC.FRESNOLOAD | Transmission - Simple |  |  | IO | IO | TRUE
8 | 2020 | 2020-08-13 12:00 | 119618698 | MiniAT | Customer - Chevron (GCUST31127) | Leaking valve; lack of information on customer's pressure rating. | Yes |  | No | N/A | Failure - Equipment | EQ | Transmission | Chevron Coalinga Field (Sec 25) Meter and Reg Station | 0811830 | LVC | Pilot-op | 459 | 250 | 83.6% | P50.7 | No | GT.STAT.LVCR.0000000251 | [6 empty] | Records related. MAOP reassessed to be 498 psig. System of record updated on 9/23/2020.
9 | 2020 | 2020-09-08 | 119727251 | SJ_SJS_RG55 | Almaden & Redmond | Leaking bypass during clearance; clearance lacked step to open vent valve which caused leaking bpass to go unnoticed. | Yes |  | Yes | N/A | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 232 | 60 | 286.7% | P95.8 | No | GD.STAT.DIST.00491 | Distribution - DREG |  |  | IO | IO | TRUE | OD 0809690
1 | 2021 | 2021-05-10 11:31 | 121322720 | YO_PAT_RN13 | S First St & W. Las Palmas (RN13) | Leaking bypass. Sequence of operations did not identify and/or mitigate leaking bypass risk. | Yes |  | Yes | N/A | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 67.5 | 57 | 18.42% | P50.2 | No | GD.STAT.DIST.00687 | Distribution - DREG |  |  | IO | IO | TRUE | OD 0809032
2 | 2021 | 2021-07-17 | 121770121 | MiniAT | Customer - Rio Bravo Rocklin | Regulation failed to control pressure due to the debris in the regulation. | Yes |  | Yes | N/A | Gas Contaminants - Debris | EQ | Transmission | Rio Bravo, Rocklin Meter and Regulator Station | 0812907 | LVC | Spring-op | 179.11 | 130 | 37.78% | P50.7 | No | GT.STAT.LVCR.0000000603 | Transmission - LVC |  |  | EQ | EQ | TRUE
3 | 2021 | 2021-10-19 | 122229820 | Chart Recorder | Avenue 9 and Hwy 99 (RB-19) | Leaking bypass and lack of downstream fire valve. Tech neglected to reopen token relief after maintenance. Station no longer served an active customer. Delayed deployment of pressure recorder enabled discovery of OP. | Yes |  | Yes | N/A | Maintenance Operations Quality | HU | Distribution |  |  |  | Pilot-op | 73.4 | 60 | 22.33% | P50.2 | No | GD.STAT.DIST.11232 - removed? | Distribution - DREG |  |  | IO | IO | TRUE
4 | 2021 | 2021-11-19 10:33 | 122400086 | EB_OAK_RB12 | 86th Ave & International Blvd (RB12) | Clearance execution resulted in the creation of a dead-end system. Slam-shut equipment operated as intended. | Yes |  | Yes | N/A | Clearance preparation | HU | Distribution |  |  |  | Pilot-op | 33.4 | 25 | 33.6% | P50.7 | No | GD.STAT.DIST.01566 | Distribution - DREG |  |  | IO | IO | TRUE | OD 0812022
5 | 2021 | 2021-12-17 20:15 | 122502982 | Gauge | Customer - SMUD Carosn ICE Cogen (AIS9326) | Documented outlet MAOP was incorrect and did not account for the potential of backpressure by higher-pressure gas from the customer. | Yes |  | No | N/A | Design/Process* | HU | Transmission | SMUD Carson Ice Cogen Meter and Regulator Station | 0813144 | LVC | Pilot-op | 620 | 412 | 50.49% | P50.6 | No | GT.STAT.LVCR.0000000539
1 | 2022 | 2022-01-29 | 122903182 | Gauge | 721 Leveroni Rd (FTAP), Sonoma | Debris due to age and lack of maintenance on unlocatable FTAP. | Yes |  | Yes | N/A | Failure - Equipment | EQ | Distribution |  |  |  | Spring-op | 75 | 60 | 25% | P50.2 | No | GD.STAT.FTAP.04934 | Distribution - FTAP |  |  | EQ | EQ | TRUE
2 | 2022 | 2022-03-16 11:00 | 123152084 | MiniAT | Customer - Chemical Lime | Regulation failed to control pressure due to sulfur in the station equipment. | Yes |  | Yes | N/A | Gas Contaminants - Sulfur | EQ | Transmission | Chemical Lime Co of Ariz Meter and Regulator Station | 0809592 | LVC | Pilot-op | 89.1 | 75 | 18.8% | P50.7 | No | GT.STAT.LVCR.0000000170 | Transmission - LVC |  |  | EQ | EQ | TRUE
3 | 2022 | 2022-04-19 | 123369541 | Gauge | Tellis Gin Regulator Station | Gas contaminants resulted in regulation failing to control pressure. | Yes |  | Yes | N/A | Gas Contaminants - Debris | EQ | Transmission | Tellis Gin Regulator Station | 0806794 | Category B | Pilot-op | 357 | 230 | 55.22% | P50.7 | No | GT.STAT.MISC.TELLISGINR | Transmission - Simple |  |  | EQ | EQ | TRUE | Rebuilt with spring-op equipment.
4 | 2022 | 2022-05-17 | 123621903 | Gauge | Abel Road (WL-05), Williams | Leakage in the bypass and isolation valves resulted in downstream pressure increase. | Yes |  | Yes | N/A | Failure - Equipment | EQ | Distribution |  |  |  | Pilot-op | 100.4 | 60 | 67.33% | P50.7 | No | GD.STAT.DIST.01430 | Distribution - DREG |  |  | EQ | EQ | TRUE | OD 0809421
5 | 2022 | 2022-07-25 10:00 | 124162441 | MI_LVM_RL20 | L-114 (Inlet piping off RL-20) | The MAOP of the bridle was inadvertently understood to be 720 psig during the clearance to transfer distribution regulator stations from L-114 to the adjacent L-303. | No |  | No | N/A | Design/Process* | TBD | [5 empty] | 706 | 497 | 42.05% | P50.6 | No | GD.STAT.DIST.11205 | [6 empty] | OD 0812263
6 | 2022 | 2022-08-04 | 124236113 | PN_SM_RB07 | Pacific Blvd & 39th St, San Mateo | The crew failed to recognize the error-like situation and reseated the inlet fire valve with an open bypass. | Yes |  | Yes | N/A | Clearance Preparation/Execution* | HU | Distribution |  |  |  | Pilot-op | 52.4 | 34 | 54.12% | P50.2 | No | GD.STAT.DIST.00106 | Distribution - DREG |  |  | IO | IO | TRUE | OD 0804023
7 | 2022 | 2022-08-29 11:22 | 124391351 | REN_PT0002 | L-138 (Fresno Gas Load Center) | Valve that isolated two pipelines with different MAOPs was mistakenly opened. | Yes |  | Yes | N/A | Clearance Execution | HU | Transmission | Fresno Gas Load Center | 3808517 | Category B | Pilot-op | 612 | 495 | 23.64% | P95.6 | No | GT.STAT.MISC.FRESNOLOAD | Transmission - Simple |  |  | IO | IO | TRUE
8 | 2022 | 2022-09-01 06:55 | 124433893 | HU_EUR_RR30 | Union St (DR-R30) | Vent valve was inadvertently closed creating a bottled section on the station outlet pipe. | Yes |  | Yes | N/A | Clearance Execution | HU | Distribution |  |  |  | Pilot-op | 127.3 | 50 | 154.6% | P50.2 | No | GD.STAT.DIST.01164 | Distribution - DREG |  |  | IO | IO | TRUE | OD 0811598
9 | 2022 | 2022-09-30 | 124600188 | MiniAT | Customer - Chevron San Ardo (highest pressure 8/19/22 - confirmed 9/30) | Possible backpressure from customer. | Yes |  | Yes | N/A | Records | TBD | Transmission | Chevron, San Ardo Meter and Regulator Station | 0813193 | LVC | Pilot-op | 184.3 | 125 | 47.44% | P50.6 | No | GT.STAT.LVCR.0000000316 | Transmission - LVC |  |  | IO | IO | TRUE

## Sheet1 (hidden)
Date | Title | System Pressure | Excursion type | Event Brief | Apparent causes | Latest Update
2015-01-12 | Alameda Hospital | LP Distribution | Large | Maintenance during customer on bypass | • Contaminants found in bypass regulation
11/8/14 AF (1/13/15) | Sunsweet Dryer - Orland | HP Distribution | Large | Dead-end customer system | • Mooney low/no flow conditions • Regulator/Monitor failure • Contaminants | • Immediate response to alleviate pressure excursion; leak survey to be conducted, and maintenance on HPR set. • Replacement of main and service piping pending assessment
2015-01-07 | Fresno Junction Station | HP Distribution | Large | Complete reg and monitor failure | • Weld slag/debris contaminants in regulator body • Water & Ice inside the pilot body • Deformation and damage to the pilot seal stem and rubber plug • Sulfur-gon filter restriction and moisture | • Immediate corrective actions were taken to address risks from overpressure event • In the process of reviewing potential future station/and area preventative recurrence • Analyzing system-wide actions
2015-01-04 | Gosford Road Station | Transmission | Small | Clearance procedure not followed during welding operations | • Clearance procedure not followed • Clearance procedure does not specify ‘not to exceed’ MOP pressure | • Field took immediate actions to reduce pressure under MAOP • Event did not require additional mitigative action
2014-12-25 | Amador Station | Transmission | Small | Regulator failed to hold set point | • Contaminants • 5/20 rule not implemented | • Upon arrival field took immediate actions to reduce pressure under MAOP
2015-01-07 | PLS 4B | Transmission | Near Hit | Relief valve activation - unknown cause | • Possibly vibrations impacting pilot operation | • New relief valve have been requested by engineering
1/13/15, 1/6/15, 12/31/14 | Indian Springs PLS L401 | Transmission | Near Hit | Required CROP maintenance has resulted in various events | • Trimmer valve V-12 positioner/3-way failure • Procedure/set-up because of ongoing maintenance work • Inadvert valve operation | • Replaced entire pilot valve assembly of V-12 was completed
1/6/15 9/10/14 | CEMEX (Black Mountain Station) | HP Distribution | Near Hit | Dead-end customer system with equipment issues | • Regulator boot damage • Regulator/monitor equipment design | • Replaced damaged boots, will look to upgrade regulators in 2015 • Current review of similar customer stations by Engineering
1/7/14 1/13/14 | Corning | HP Distribution | Large | Regulator failed to hold set point after liquid surge | • Contaminants • Regulator/Monitor failure | • Establish schedule to monitor the station • Recently installed filter separator
2014-01-10 | Topock Station | Transmission | Large | Atypical operating conditions with split compression and discharge | • System operating mode (Split Station) • Valve Operation to reinitiate L300B flow at the Station | • CAP conducted a Cause Evaluation • Further analysis will be conducted - Process Hazard Analysis
2014-08-04 | Dolan Road | Transmission | Large | Clearance procedure created dead-end system through valving | • Review of Clearance (Closing of isolation valve) • Monitor/Regulator slow reaction time | • A 20% pressure reducation was issued • Crew bleed the pressure down below the MAOP limit
2/14/14 3/5, 8/16, 8/19, 8/20 | Acacia Station | Transmission | Large, Near Hit | Pressure build up on intermediate piping created a dead-end system | • No load demand • Monitor/Regulator set point too close to MOP/HIHI • Station Design | • Reconfiguration of station has been proposed • Regs set points have been adjusted in the 2nd Stage Reg Pit
3/5/14, 3/19, 3/22, 9/26, 11/20, 12/16 | Los Medanos Ryer Island | Transmission | Near Hit | Pressure build up due to automated BTU valve regulating based on % Nitrogen; in addition, power outage causing the regs to fail to its last position | • BTU operated valve shut in due to BTU ratio • Power outage at the station and regs failed to the last position | • New uninterruptible power supply has been submitted for emergent funding • Departmential discussion has been initiated for potential improvements (PLE and Control Engineering)
2/12/14, 2/14, 3/4, 3/5 | Los Banos D/S | Distribution | Near Hit | Reoccurring calibration & communication issues with pressure transducer | • Problematic pressure transducer | • New transducer was order and replaced the existing pressure transducer
1/23/14, 3/12, 11/18, 11/20 | Brentwood Terminal | Transmission | Near Hit | Various work/maintenance contributed to the pressure build up within the station | • Leaking valve • Operator inadvertently entered incorrect pressure • Hand throttling valve | • Lesson Learned were identified and discussed with Control Center Management • Valves were greased to reduce leakage
8/31/14, 11/20 | Kettleman Compressor Station | Transmission | Near Hit | Valve operation during the initial phase of compressing pressure | • Valve reaction time when open/close during compression operation • Valve operation by operator | • Tailboard/Lesson Learned concerning compression process at Kettleman
3/13/14, 4/30 | Redding Tap | Transmission | Near Hit | Low pressure differential across of regulation | • Low flow condition/pressure differential - pressure across the regulator and monitor equalize | • Set point pressure adjusted • Validate regulator differential pressure requirements on manufacturer specs
Common Themes
• There has been a recent rise in equipment failures and contaminants found in regulation potentially due to winter flow patterns (Sunsweet, Fresno Junction, Amador) • Process as it relates to maintenance, construction, and special operations with regard to clearances and pressure limitations have been more frequent (Indian Springs, Fresno Junction, Gosford) • Industrial seasonal customer operations causing increased pressure scenarios (Sunsweet, CEMEX)
cold weather potential causes freezing effects, higher flows move debris and liquidds, larger differential b high and large flows make reg different
Medium/Long Term Corrective Actions
• PHA will be performed on large seasonal distribution customers off transmission lines (optimal use of relief valves) • Validation of current pressures of large seasonal distribution customers off transmission lines - through electronic recording devices • Clearance strategy session to enhance existing guidelines about various clearance issues (local review, best practices, special instructions, control room notification) • Develop further field training for instructions on servicing regulation • Mooney regulator/monitor risk analysis

## OP SAR (hidden)
Q1
OP Events | Jan | Feb | Mar | Q2 | Q3 | Q4 | YTD | Target
[15 empty] | 2014 | 2015 | 2016 | 2017 YTD
Goal - Total Events | 8 | 0 | 0 | 2 | 3 | 3 | 8 | 16 |  |  |  | Total OP Events |  |  | 18 | 29 | 18 | 2
Actual - Total All Events | 0 | 0 | 0 | - | - | - | 0 | 16 |  |  |  | Equipment Failure |  |  | 5 | 5 | 4 | 1
[12 empty] | Contaminants |  |  | 5 | 4 | 3 | 1
Goal - Large Excursions | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  |  |  | Human Performance |  |  | 8 | 20 | 11 | 0
Actual - Total All Large | 0 | 0 | 0 | - | - | - | 0 | 8 |  |  |  | Human Performance Cause Breakdown
[12 empty] | GPOM |  |  | 2 | 10 | 6 | 0
[12 empty] | GC M&C |  |  | 1 | 2 | 1 | 0
Q2 | [11 empty] | Gas Control |  |  | 1 | 0 | 1 | 0
OP Events | Q1 | Apr | May | Jun | Q3 | Q4 | YTD | Target |  |  |  | Clearance Preparation |  |  | 2 | 3 | 2 | 0
[12 empty] | Engineering Design |  |  | 2 | 5 | 1 | 0
Goal - Total Events | 8 | 0 | 1 | 1 | 3 | 3 | 10 | 16
Actual - Total All Events | 2 |  |  |  | - | - | 2 | 10 |  |  |  | Near Hits |  |  | 123 | 199 | 136
[12 empty] | Equipment Failure |  |  | 19 | 35 | 61
Goal - Large OPs | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  |  |  | Human Performance |  |  | 104 | 164 | 75 |  |  | ------->
Actual - Total All Large | 0 |  |  |  | - | - | 0 | 4
3q | [13 empty] | High Exposure Events and Near Hits
OP Events | Q1 | Q2 | Jul | Aug | Sep | Q4 | YTD | Target | [5 empty] | 2013 | 2014 | 2015 | 2016 | 2017 YTD
[14 empty] | 38 | 34 | 25 | 21 | 1
Goal - Total Events | 8 | 2 | 1 | 1 | 1 | 3 | 13 | 16
Actual - Total All Events | 0 |  |  |  | - | - | 0 | 3
Goal - Large OPs | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8
Actual - Total All Large | 0 |  |  |  | - | - | 0 | 8
Indiv
4q | [12 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
[12 empty] | 2015 Actual | 3 | 2 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 5
OP Events | Q1 | Q2 | Q3 | Oct | Nov | Dec | YTD | Target |  |  |  | 2017 Target | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 16
[12 empty] | 2017 Actual | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goal - Total Events | 8 | 2 | 3 | 1 | 1 | 1 | 14 | 16
Actual - Total All Events | 0 |  |  |  | - | - | 0 | 2 |  |  |  | 2015 versus 2016 Comparison
[13 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | ------->
Goal - Large OPs | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  |  |  | 2015 Actual | 3 | 5 | 7 | 8 | 10 | 11 | 14 | 17 | 20 | 23 | 25 | 30
Actual - Total All Large | 0 |  |  |  | - | - | 0 | 8 |  |  |  | 2016 Target | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 16
[12 empty] | 2016 Actual | 2 | 2 | 2 | 3 | 3 | 7 | 8 | 11 | 11 | 14 | 16 | 18
[12 empty] | 2017 Targets | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 16
[12 empty] | 2017 Actual | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OP Events (thru November) | Q1 | Q2 | Q3 | Oct | Nov | Dec | YTD | Target
Goal - Total Events | 5 | 3 | 3 | 1 | 2 | 2 | 14 | 16
Actual - Total All Events | 2 | 5 | 4 | 3 | 2 | - | 16 | 18
Goal - Large OPs | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 4 | Large Excursion Events 2016
Actual - Total All Large | 0 | 4 | 2 | 2 | 1 | - | 9 | 11
[10 empty] | Date | Location |  | 4: Description
[10 empty] | 2016-04-07 11:53 | Swingle Junction L172 |  | 4: No clearance, improper isolation to perform leak repair work
[10 empty] | 2016-06-02 13:00 | Customer - Olam Spices |  | 4: Regulator and monitor failure due to contaminants, filter not installed correctly
[10 empty] | 2016-06-23 11:35 | Dolan Rd L301B |  | 4: Clearance failed to address regulation return to service risk
[10 empty] | 2016-06-27 09:24 | Floral Ave HPR, Selma |  | 4: Leaking bypass on HPR, relief valve did not operate due to wrong spring, not mapped in GT-GIS
[10 empty] | 2016-07-16 18:18 | Customer - Kagome Foods |  | 4: Equipment failure due excessive time in service, and oversized for the application
[10 empty] | 2016-08-10 15:00 | Leonard Ave HPR, Fresno |  | 4: Equipment failure due to contaminants
[10 empty] | 2016-10-14 | North Sac Holder DFM |  | 4: Causal Evaluation not complete
[10 empty] | 2016-10-30 | Customer - Sensient Foods |  | 4: Regulation equipment failed to protect downstream system after hot shut down of customer equipment
[10 empty] | 2016-11-03 | Stanley Blvd & Bernal Ave |  | 4: Crew did not follow special instructions prior to starting clearance, pinched plastic main d/s of regulator station
Note: the list below is associated with YTD OP Events (don’t delete)
Actual
Amber Goal
Monthly OP Goal

## Large_Largest Excursion Events (hidden)
LAST UPDATE 4/4/16
Large OPs
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Transmission | 7 | 2 | 4 | 3 | 2 | 1
HP Distribution | 7 | 1 | 3 | 2 | 2
LP Distribution | 3 | 0 | 0 | 0 | 1
Largest OPs
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Transmission | 1 | 1 | 0 | 0 | 0
HP Distribution | 3 | 3 | 1 | 2 | 1
LP Distribution | 0 | 0 | 1 | 0 | 1
Total Large OPs
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016
Transmission | 8 | 3 | 4 | 3 | 2 | 1
HP Distribution | 10 | 4 | 4 | 4 | 3 | 0
LP Distribution | 3 | 0 | 1 | 0 | 2 | 0

## Monthly Tasks (hidden)
Legend
|  |  |  | D | Day
Monthly |  |  |  | M | Monday
1D | Send out OPE Agenda & Action item List for upcoming OPE meeting |  |  | T | Tuesday
1D | Send out OP Action Items Tracking for status due EOW These are the 10 items OP is responsible for completing by EOY, Frank to review during OPE |  |  | Th | Thursday
1T | Review OP event ACE reports from prior month - and emphasis SMEs to present discussions for the benefit of the group |  |  | F | Friday
1Th | Order lunch for next weeks meeting |  |  | LD | Last Day
1F | Compile metrics from prior month and report to KTS/BPR, this also updates the stats for the OP agenda |  |  | W | Week
1F | Send out 1-pager of OP Events YTD to OPE and Dan
1W | Resolve questions about reports from review meeting (1T)
1W | Session D monthly updates is mainly to discuss progress and any roadblocks you may have in completing the various mitigations within the committed timeframes with Mary & Venetia
1W | Summarize events for the Weekly Items of Interest Bulletin | AMFQ
2T | OPE Meeting to review reports (1T), statistics (1F), and Action items (1W)
2F | Send out OPE Agenda with notes from meeting
2W | Resolve questions about reports from OPE
2W | Input tasks and corrective actions from OPE into CAP
3W | Resolve questions about reports from OP events
3W | Send email to Frank & Dan for approval to close out near hits and event notifications as necessary. | complete versus closure
3W | Perform QA Process: - Are site specific updates complete? - Any system wide C/A moving forward? - Does OP approve report & ACE?
4W | Resolve questions about reports from OP events
4W | Confirm if any reports need to be 'Final' within 60 days of initiation
LD | Pull MTD Dashboard report that shows closed/risk rank CAP
Long Term
2W of 1st, 4th, 7th, and 10th Month | Compile metrics for quarterly report, review past reports, and develop material to deliver - work with OP SAR
OP SAR | April 29th
45D | After events are presented in OPE - focus on report _Final

## Roles (hidden)
GCSS Roles and Responsibilities for OP Events and Transmission Near Hits |  |  | clarity as of 1/8/16
Receive notification of event - epage or other (SRDC email, AIR updates)
Enter the event into excursion master tracking list
Ensure CAP notification is created for event
48-hour report created for event
Quick hit email to notify others of event and provide 48-hour report
This is sent to OPE team, and steering committee to distribute as they see fit
Review OP event report in GCSS event report review meeting
Week prior to OP elimination team meeting
Review OP event report in OP Elimination team meeting
2nd Tuesday of month (See Monthly tasks page)
Finalize OP event report - post to share point using correct file naming convention
within 45 days of presenting at OPE
Enter system wide corrective actions
and event-specific corrective actions into CAP for the event
Perform QA on CAP notification - scope of QA is that the tasks resolve the overpressure event
Close CAP notification upon completion of Quality Assurance in above step
if OP Event, director/steering committee provides QA
if Near Hit, manager provides QA
Request clarification from manager/director steering committee to complete (checkered flag) CAP notification
If CAP notification closed by others, evaluate quality of CAP item contents (see QA step above)
Correct if necessary, and continue through process
Track and trend OP event statistics
Provide monthly updates to the metrics processes as required (Monthly)
Report our on OP event statistics to Gas Operations
Prepare OP SAR meeting materials as directed

## Clearances (hidden)
CLEARANCE COUNTS | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | Total
2014 GT SYSTEM MAINTENANCE | 183 | 203 | 161 | 133 | 204 | 102 | 105 | 152 | 177 | 231 | 197 | 179 | 2027
2014 GT SYSTEM NEW | 37 | 22 | 61 | 65 | 51 | 35 | 48 | 73 | 65 | 99 | 85 | 69 | 710
2015 GT SYSTEM MAINTENANCE | 177 | 221 | 267 | 247 | 275 | 254 | 258 | 248 | 304 | 276 | 251 | 242 | 3020
2015 GT SYSTEM NEW | 40 | 40 | 67 | 43 | 61 | 54 | 73 | 82 | 69 | 91 | 98 | 95 | 813
2016 GT SYSTEM MAINTENANCE | 271 | 278 | 374 | 362 | 316 | 277 | 283 | 325 | 289 | 282 | 369 | 300 | 3726
2016 GT SYSTEM NEW | 96 | 140 | 108 | 159 | 114 | 83 | 131 | 146 | 127 | 114 | 103 | 78 | 1399
2017 GT SYSTEM MAINTENANCE | JAN: 262; FEB: 156; MAR: 423; APR: 385; MAY: 303; JUN: 272; JUL: 285
2017 GT SYSTEM NEW | JAN: 73; FEB: 87; MAR: 115; APR: 92; MAY: 180; JUN: 100; JUL: 137

## Contact List (hidden)
Department | Name | E-mail | Phone | Cell
Asset Knowledge Management - T & D | Cleveland, Nicole | NEB6@pge.com | 925-328-6366 | 925-322-3311
Codes & Standards - T&D | Davidson, Matt | MEDm@pge.com | 925-328-5763 | 925-324-8201
Compliance | Bradley, Mike | M0Bj@pge.com | 925-328-5724 | 925-967-8371
Construction - T&D | Leverett, Ross | RALw@pge.com | 209-576-6586 | 209-608-9276
DIMP | Stockand, Rich | RMSf@pge.com | 925-244-3104 | 415-412-2854
Engineering & Design - T | Chan, Jonathan | J4Cb@pge.com | 925-244-3205 | 925-788-6114
Engineering & Estimating - D | Rouainia, Ghandi | GXRp@pge.com | 925-244-3047 | 510-292-6857
ERX - Evaluate for Installation | Gupta, Nishal | NXGg@pge.com | 925-244-4535 | 415-349-9827
ERX - Connect to Control Room | Sweeney, Jeff | JK10@pge.com | 925-244-4539 | 925-334-0544
FIMP - Initiative Owner | White, Terry | TGW5@pge.com | 925-244-3323 | 925-285-6781
FIMP | Ross, Tim | TRR0@pge.com | 925-244-3344 | 925-817-9441
FIMP | Singer, Kevin | KDSd@pge.com | 925-328-5740 | 925-324-2289
FIMP | Shahab, Rehan | ROS8@pge.com | 925-328-5725 | 925-719-0534
FIMP | Herrmann, Corine | C2Hh@pge.com | 925-244-3797 | 925-222-0442
FIMP | Yee, Gary | GLY1@pge.com | 925-244-3196 | 925-817-0068
FIMP | Morshead, Roger | RKM3@pge.com | 209-932-6558 | 209-608-1049
FIMP - MCTL | Pace, Matt | MBP9@pge.com | 925-674-6738 | 925-586-3985
FIMP - Station Assessment | Rovella, Troy | TMRn@pge.com | 925-974-4023 | 415-666-6086
Gas Systems Operations | Maxwell, Frank | FWM1@pge.com | 925-244-4536 | 415-260-7956
Gas Systems Operations - Clearances | Quijalvo, Roberto | RBQ2@pge.com | 925-244-4572 | 415-314-5730
Gas Planning | Brown, Rick | RCB3@pge.com | 925-244-3102 | 415-264-2122
Gas Stewardship & LCC | N/A
GPOM - Sulfur Filters | Johnson, Lance | LEJ5@pge.com | 925-381-0756 | 925-381-0756
GPOM - Sulfur Filters | Hernandez, Nicolyn | NDH2@pge.com | 925-551-1813 | 925-551-1813
GPOM | Ball, Kelly | KLBp@pge.com | 408-204-5340 | 408-204-5340
GPOM | Tonetti, Curtis | CLTb@pge.com | 530-351-3570 | 530-351-3570
Investment Planning - T&D | Rizo, Hazzel | HMR2@pge.com | 925-244-3117 | 415-244-0963
Mapping
OQ | Bradley, Mike | M0Bj@pge.com | 925-328-5724 | 925-967-8371
Project Management - D | Saffarzadeh, Samira | S8Sb@pge.com | 408-205-8101 | 408-205-8101
Project Management - T | Khairi, Sam | S3Kk@pge.com | 925-244-3932 | 925-404-4067
Safety Quality and Contract Management | Ramirez, James | JAR2@pge.com | 925-328-5796 | 805-441-5444
SCADA Visibility | Gaebler, George | GEG4@pge.com | 925-244-4545 | 510-612-1671
SPEC Services (Supporting Contractor) | Russo, Ed | erusso@specservices.com | 714-415-7002 | 714-914-7895
SPEC Services (Supporting Contractor) | Black, Kevin | kblack@specservices.com | 562-619-5269 | 562-619-5269
TIMP | Liu, Calvin | C1Li@pge.com | 925-244-3353 | 925-719-4293
Training
CRM | Rakin, Dante
Process Safety | Sass, Stephen
Process Safety | Rengifo, Carlos