## Control-Charts
TRANSMISSION WIRE DOWN EVENTS EXCLUDING MEDs, All Cause Categories | [8 empty] | TRANSMISSION WIRE DOWN EVENTS INCLUDING MEDs, All Cause Categories
YEAR | Actuals- Excluding MEDs | Mean, Excluding MEDs | STD DEV, Excluding MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) |  | YEAR | Actuals- Including MEDs | Mean, Including MEDs | STD DEV, Including MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) | Count of MEDs
2011 | 42 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2011 | 68 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 14
2012 | 65 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2012 | 77 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 4
2013 | 43 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2013 | 47 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 4
2014 | 32 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2014 | 42 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 5
2015 | 46 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2015 | 65 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 10
2016 | 44 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2016 | 47 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 3
2017 | 52 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2017 | 96 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 30
2018 | 42 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2018 | 44 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 7
2019 | 40 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2019 | 77 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 31
2020 | 29 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2020 | 44 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 14
2021 | 39 | 40.7778 | 6.9781 | 61.7122 | 19.8434 | 54.7341 | 26.8215 |  | 2021 | 91 | 61.4444 | 21.5819 | 126.1901 | -3.3012 | 104.6082 | 18.2807 | 25
ytd June 2022 | 22 | [7 empty] | ytd June 2022 | 22 | [6 empty] | 0
TRANSMISSION WIRE DOWN EVENTS EXCLUDING MEDs, Equipment Failures | [8 empty] | TRANSMISSION WIRE DOWN EVENTS INCLUDING MEDs, Equipment Failures
YEAR | Actuals- Excluding MEDs | Mean, Excluding MEDs | STD DEV, Excluding MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) |  | YEAR | Actuals- Including MEDs | Mean, Including MEDs | STD DEV, Including MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s)
2011 | 22 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2011 | 39 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2012 | 23 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2012 | 32 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2013 | 26 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2013 | 28 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2014 | 11 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2014 | 18 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2015 | 17 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2015 | 21 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2016 | 19 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2016 | 19 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2017 | 21 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2017 | 33 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2018 | 14 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2018 | 14 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2019 | 15 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2019 | 33 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2020 | 12 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2020 | 20 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
2021 | 18 | 18 | 4.7539 | 32.2618 | 3.7382 | 27.5079 | 8.4921 |  | 2021 | 46 | 27.5455 | 9.9936 | 57.5264 | -2.4354 | 47.5327 | 7.5582
AVE-5 YEAR | 16 | [7 empty] | AVE-5 YEAR | 29.2
TRANSMISSION WIRE DOWN EVENTS EXCLUDING MEDs, Tier 2/3, All Cause Categories | [8 empty] | TRANSMISSION WIRE DOWN EVENTS INCLUDING MEDs, Tier 2/3, All Cause Categories
YEAR | Actuals- Excluding MEDs | Mean, Excluding MEDs | STD DEV, Excluding MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) |  | YEAR | Actuals- Including MEDs | Mean, Including MEDs | STD DEV, Including MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) | Count of MEDs
2011 | 19 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2011 | 37 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 14
2012 | 37 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2012 | 45 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 4
2013 | 13 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2013 | 16 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 4
2014 | 10 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2014 | 15 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 5
2015 | 14 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2015 | 25 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 10
2016 | 19 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2016 | 21 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 3
2017 | 19 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2017 | 40 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 30
2018 | 11 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2018 | 12 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 7
2019 | 14 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2019 | 38 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 31
2020 | 8 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2020 | 19 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 14
2021 | 11 | 15.9091 | 7.9681 | 39.8134 | -7.9953 | 31.8453 | -0.027146 |  | 2021 | 46 | 28.5455 | 12.8169 | 66.9961 | -9.9052 | 54.1792 | 2.9117 | 25
ytd June 2022 | 4 | [7 empty] | Ytd June 2022 | 4
AVE-5 YEAR | 12.6 | [7 empty] | AVE-5 YEAR | 31
DDS
5,525.9 overhead transmission circuit line miles in Tier 2/3 HFTD areas
5525.9
7.2386 | 3 sigma
5.7909 | 2 sigma
4.3432 | 1 sigma
[9 empty] | ELECTRIC TRANSMISSION WIRE DOWN EVENTS/1,000 MILES OCCURRING ON MEDs, Tier 2/3 Only, All Cause Categories | [8 empty] | ELECTRIC TRANSMISSION WIRE DOWN EVENTS/1,000 MILES OCCURRING ON MEDs, Tier 2/3 Only, All Cause Categories
[9 empty] | YEAR | Actuals- During MEDs | Mean, During MEDs | STD DEV, During MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) | Count of MEDs | YEAR | Actuals- During MEDs | Mean, During MEDs | STD DEV, During MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) | Count of MEDs
[9 empty] | 2011 | 3.2574 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 14 | 2013 | 0.5429 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 4
[9 empty] | 2012 | 1.4477 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 4 | 2014 | 0.90483 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 5
[9 empty] | 2013 | 0.5429 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 4 | 2015 | 1.9906 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 10
[9 empty] | 2014 | 0.90483 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 5 | 2016 | 0.36193 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 3
[9 empty] | 2015 | 1.9906 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 10 | 2017 | 3.8003 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 30
[9 empty] | 2016 | 0.36193 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 3 | 2018 | 0.18097 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 7
[9 empty] | 2017 | 3.8003 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 30 | 2019 | 4.3432 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 31
[9 empty] | 2018 | 0.18097 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 7 | 2020 | 1.9906 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 14
[9 empty] | 2019 | 4.3432 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 31 | 2021 | 6.3338 | 2.2721 | 2.1261 | 8.6504 | -4.1061 | 6.5243 | -1.98 | 25
[9 empty] | 2020 | 1.9906 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 14 | AVE 2017-2021 | 3.3298
[9 empty] | 2021 | 6.3338 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 25
[9 empty] | YTD June 2022 | 0 | 2.2868 | 1.9445 | 8.1202 | -3.5467 | 6.1757 | -1.6022 | 0
[9 empty] | AVE 2017-2021 | 3.3298
[12 empty] | 2.1261 | 8.542%
5,525.9 overhead transmission circuit line miles in Tier 2/3 HFTD areas
[9 empty] | 5525.9 | 5.5259
[9 empty] | ELECTRIC TRANSMISSION WIRE DOWN EVENTS/1,000 MILES OCCURRING ON non-MEDs, Tier 2/3 Only, All Cause Categories | [8 empty] | ELECTRIC TRANSMISSION WIRE DOWN EVENTS/1,000 MILES OCCURRING ON non-MEDs, Tier 2/3 Only, All Cause Categories
[9 empty] | YEAR | Actuals- During non-MEDs | Mean, During non-MEDs | STD DEV, During non-MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) | Count of MEDs | YEAR | Actuals- During non-MEDs | Mean, During non-MEDs | STD DEV, During non-MEDs | UCL (3s) | LCL (3s) | UWL (2s) | LWL (2s) | Count of MEDs
[9 empty] | 2011 | 3.4384 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 14 | 2013 | 2.3526 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 4
[9 empty] | 2012 | 6.6957 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 4 | 2014 | 1.8097 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 5
[9 empty] | 2013 | 2.3526 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 4 | 2015 | 2.5335 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 10
[9 empty] | 2014 | 1.8097 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 5 | 2016 | 3.4384 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 3
[9 empty] | 2015 | 2.5335 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 10 | 2017 | 3.4384 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 30
[9 empty] | 2016 | 3.4384 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 3 | 2018 | 1.9906 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 7
[9 empty] | 2017 | 3.4384 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 30 | 2019 | 2.5335 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 31
[9 empty] | 2018 | 1.9906 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 7 | 2020 | 1.4477 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 14
[9 empty] | 2019 | 2.5335 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 31 | 2021 | 1.9906 | 2.3928 | 0.68778 | 4.4561 | 0.32944 | 3.7683 | 1.0172 | 25
[9 empty] | 2020 | 1.4477 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 14 | YTD June 2022 | 0.7239 | [6 empty] | 0
[9 empty] | 2021 | 1.9906 | 2.879 | 1.442 | 7.2049 | -1.4469 | 5.7629 | -0.0049124 | 25
[9 empty] | YTD June 2022 | 0.7239 | [6 empty] | 0
[9 empty] | AVE 2017-2021 | 2.2802
2011-2021 Standard Deviation =1.944
Control Charts to be used for target-setting purposes and will be updated EOY 2022

## Pivot-EFs
|  | YEAR | Equip Fails (including MEDs) | Equip Fails (excluding MEDs)
Row Labels | Count of Comments | 2011 | 39 | 22
2011 | 68 | 2012 | 32 | 23
Animal | 1 | 2013 | 28 | 26
No | 1 | 2014 | 18 | 11
Disaster | 2 | 2015 | 21 | 17
No | 2 | 2016 | 19 | 19
Equipment failure | 39 | 2017 | 33 | 21
No | 22 | 2018 | 14 | 14
YES | 17 | 2019 | 33 | 15
External contact | 9 | 2020 | 20 | 12
No | 9 | 2021 | 46 | 18
Tree | 14 | 5 Year Average | 29.2 | 16
No | 6
YES | 8
Weather | 2
No | 1
YES | 1
Work Procedure Error | 1
No | 1
2012 | 77
Disaster | 8
No | 8
Equipment failure | 32
No | 23
YES | 9
External contact | 12
No | 12
Other | 3
No | 3
Tree | 20
No | 17
YES | 3
Weather | 1
No | 1
Work Procedure Error | 1
No | 1
2013 | 47
Contamination | 1
No | 1
Disaster | 2
No | 2
Equipment failure | 28
No | 26
YES | 2
External contact | 8
No | 8
Other | 1
No | 1
Tree | 4
No | 2
YES | 2
Weather | 1
No | 1
Work Procedure Error | 2
No | 2
2014 | 42
Animal | 1
No | 1
Contamination | 1
No | 1
Disaster | 3
No | 3
Equipment failure | 18
No | 11
YES | 7
External contact | 11
No | 11
Tree | 7
No | 4
YES | 3
Weather | 1
No | 1
2015 | 65
Animal | 1
No | 1
Contamination | 2
No | 2
Disaster | 5
No | 5
Equipment failure | 21
No | 17
YES | 4
External contact | 14
No | 13
YES | 1
Tree | 20
No | 7
YES | 13
Weather | 1
No | 1
Work Procedure Error | 1
No | 1
2016 | 47
Disaster | 2
No | 2
Equipment failure | 19
No | 19
External contact | 11
No | 11
Tree | 13
No | 10
YES | 3
Weather | 2
No | 2
2017 | 96
Contamination | 1
YES | 1
Disaster | 9
No | 7
YES | 2
Equipment failure | 33
No | 21
YES | 12
External contact | 15
No | 11
YES | 4
Tree | 35
No | 12
YES | 23
Weather | 2
YES | 2
Work Procedure Error | 1
No | 1
2018 | 44
Contamination | 1
No | 1
Disaster | 7
No | 6
YES | 1
Equipment failure | 14
No | 14
External contact | 16
No | 15
YES | 1
Tree | 6
No | 6
2019 | 77
Contamination | 2
No | 2
Equipment failure | 33
No | 15
YES | 18
External contact | 14
No | 12
YES | 2
Other | 4
No | 2
YES | 2
Tree | 18
No | 6
YES | 12
Weather | 4
No | 1
YES | 3
Work Procedure Error | 2
No | 2
2020 | 44
Contamination | 1
No | 1
Disaster | 4
No | 4
Equipment failure | 20
No | 12
YES | 8
External contact | 11
No | 9
YES | 2
Tree | 6
No | 3
YES | 3
Weather | 2
YES | 2
2021 | 91
Disaster | 3
No | 2
YES | 1
Equipment failure | 46
No | 18
YES | 28
External contact | 13
No | 13
Tree | 28
No | 6
YES | 22
Weather | 1
No | 1
Grand Total | 698

## Sheet2
Row Labels | Count of Date Out
2011 | 68
No | 42
Non-HFTD | 23
Tier 2 - Elevated | 15
Tier 3 - Extreme | 4
YES | 26
Non-HFTD | 8
Tier 2 - Elevated | 10
Tier 3 - Extreme | 8
2012 | 77
No | 65
Non-HFTD | 28
Tier 2 - Elevated | 34
Tier 3 - Extreme | 3
YES | 12
Non-HFTD | 4
Tier 2 - Elevated | 6
Tier 3 - Extreme | 2
2013 | 47
No | 43
Non-HFTD | 30
Tier 2 - Elevated | 12
Tier 3 - Extreme | 1
YES | 4
Non-HFTD | 1
Tier 2 - Elevated | 1
Tier 3 - Extreme | 2
2014 | 42
No | 32
Non-HFTD | 22
Tier 2 - Elevated | 5
Tier 3 - Extreme | 5
YES | 10
Non-HFTD | 5
Tier 2 - Elevated | 5
2015 | 65
No | 47
Non-HFTD | 33
Tier 2 - Elevated | 14
YES | 18
Non-HFTD | 7
Tier 2 - Elevated | 8
Tier 3 - Extreme | 3
2016 | 47
No | 44
Non-HFTD | 25
Tier 2 - Elevated | 12
Tier 3 - Extreme | 7
YES | 3
Non-HFTD | 1
Tier 2 - Elevated | 1
Tier 3 - Extreme | 1
2017 | 96
No | 52
Non-HFTD | 33
Tier 2 - Elevated | 12
Tier 3 - Extreme | 7
YES | 44
Non-HFTD | 23
Tier 2 - Elevated | 11
Tier 3 - Extreme | 10
2018 | 44
No | 42
Non-HFTD | 31
Tier 2 - Elevated | 9
Tier 3 - Extreme | 2
YES | 2
Non-HFTD | 1
Tier 2 - Elevated | 1
2019 | 77
No | 40
Non-HFTD | 26
Tier 2 - Elevated | 11
Tier 3 - Extreme | 3
YES | 37
Non-HFTD | 13
Tier 2 - Elevated | 13
Tier 3 - Extreme | 11
2020 | 44
No | 29
Non-HFTD | 21
Tier 2 - Elevated | 6
Tier 3 - Extreme | 2
YES | 15
Non-HFTD | 4
Tier 2 - Elevated | 4
Tier 3 - Extreme | 7
2021 | 91
No | 40
Non-HFTD | 28
Tier 2 - Elevated | 6
Tier 3 - Extreme | 6
YES | 51
Non-HFTD | 17
Tier 2 - Elevated | 21
Tier 3 - Extreme | 13
Grand Total | 698
|  | 2011 | 68
|  | No | 42
|  | Non-HFTD | 23
|  | Tier 2 - Elevated | 15
|  | Tier 3 - Extreme | 4
|  | YES | 26
|  | Non-HFTD | 8
|  | Tier 2 - Elevated | 10
|  | Tier 3 - Extreme | 8
|  | 2012 | 77
|  | No | 65
|  | Non-HFTD | 28
|  | Tier 2 - Elevated | 34
|  | Tier 3 - Extreme | 3
|  | YES | 12
|  | Non-HFTD | 4
|  | Tier 2 - Elevated | 6
|  | Tier 3 - Extreme | 2
|  | 2013 | 47
|  | No | 43
|  | Non-HFTD | 30
|  | Tier 2 - Elevated | 12
|  | Tier 3 - Extreme | 1
|  | YES | 4
|  | Non-HFTD | 1
|  | Tier 2 - Elevated | 1
|  | Tier 3 - Extreme | 2
|  | 2014 | 42
|  | No | 32
|  | Non-HFTD | 22
|  | Tier 2 - Elevated | 5
|  | Tier 3 - Extreme | 5
|  | YES | 10
|  | Non-HFTD | 5
|  | Tier 2 - Elevated | 5
|  | 2015 | 65
|  | No | 47
|  | Non-HFTD | 33
|  | Tier 2 - Elevated | 14
|  | YES | 18
|  | Non-HFTD | 7
|  | Tier 2 - Elevated | 8
|  | Tier 3 - Extreme | 3
|  | 2016 | 47
|  | No | 44
|  | Non-HFTD | 25
|  | Tier 2 - Elevated | 12
|  | Tier 3 - Extreme | 7
|  | YES | 3
|  | Non-HFTD | 1
|  | Tier 2 - Elevated | 1
|  | Tier 3 - Extreme | 1
|  | 2017 | 96
|  | No | 52
|  | Non-HFTD | 33
|  | Tier 2 - Elevated | 12
|  | Tier 3 - Extreme | 7
|  | YES | 44
|  | Non-HFTD | 23
|  | Tier 2 - Elevated | 11
|  | Tier 3 - Extreme | 10
|  | 2018 | 44
|  | No | 42
|  | Non-HFTD | 31
|  | Tier 2 - Elevated | 9
|  | Tier 3 - Extreme | 2
|  | YES | 2
|  | Non-HFTD | 1
|  | Tier 2 - Elevated | 1
|  | 2019 | 77
|  | No | 40
|  | Non-HFTD | 26
|  | Tier 2 - Elevated | 11
|  | Tier 3 - Extreme | 3
|  | YES | 37
|  | Non-HFTD | 13
|  | Tier 2 - Elevated | 13
|  | Tier 3 - Extreme | 11
|  | 2020 | 44
|  | No | 29
|  | Non-HFTD | 21
|  | Tier 2 - Elevated | 6
|  | Tier 3 - Extreme | 2
|  | YES | 15
|  | Non-HFTD | 4
|  | Tier 2 - Elevated | 4
|  | Tier 3 - Extreme | 7
|  | 2021 | 91
|  | No | 40
|  | Non-HFTD | 28
|  | Tier 2 - Elevated | 6
|  | Tier 3 - Extreme | 6
|  | YES | 51
|  | Non-HFTD | 17
|  | Tier 2 - Elevated | 21
|  | Tier 3 - Extreme | 13
|  | Grand Total | 698
ET WIRE DOWN COUNTS TIER 2/3
[5 empty] | non-MED | MED
|  |  |  | 2011 | 19 | 18
|  |  |  | 2012 | 37 | 8
|  |  |  | 2013 | 13 | 3
|  |  |  | 2014 | 10 | 5
|  |  |  | 2015 | 14 | 11
|  |  |  | 2016 | 19 | 2
|  |  |  | 2017 | 19 | 21
|  |  |  | 2018 | 11 | 1
|  |  |  | 2019 | 14 | 24
|  |  |  | 2020 | 8 | 11
|  |  |  | 2021 | 11 | 35

## Historical-by-Month
Row Labels | Count of T-LINE
2011 | 68
2012 | 77
2013 | 47
2014 | 42
2015 | 65
2016 | 47
2017 | 96
2018 | 44
2019 | 77
2020 | 44
2021 | 91
Grand Total | 698
MONTHLY ET WIRE DOWN EVENTS, INCLUDING MAJOR EVENT DAYS
|  | YEAR | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | TOTAL
|  | 2011 | 2 | 10 | 15 | 2 | 5 | 3 | 4 | 4 | 4 | 5 | 5 | 9 | 68
|  | 2012 | 5 | 5 | 10 | 3 | 2 | 5 | 2 | 8 | 6 | 5 | 5 | 21 | 77
|  | 2013 | 1 | 2 | 4 | 3 | 6 | 1 | 0 | 5 | 4 | 10 | 6 | 5 | 47
|  | 2014 | 5 | 2 | 2 | 0 | 3 | 0 | 6 | 4 | 3 | 2 | 0 | 15 | 42
|  | 2015 | 1 | 17 | 4 | 3 | 3 | 2 | 2 | 8 | 4 | 7 | 4 | 10 | 65
|  | 2016 | 5 | 6 | 9 | 4 | 3 | 2 | 5 | 2 | 1 | 7 | 1 | 2 | 47
|  | 2017 | 17 | 22 | 3 | 4 | 5 | 1 | 7 | 4 | 12 | 11 | 5 | 5 | 96
|  | 2018 | 3 | 5 | 4 | 3 | 4 | 3 | 8 | 0 | 5 | 4 | 2 | 3 | 44
|  | 2019 | 8 | 27 | 5 | 5 | 4 | 0 | 3 | 6 | 2 | 6 | 8 | 3 | 77
|  | 2020 | 12 | 4 | 4 | 2 | 3 | 2 | 4 | 4 | 2 | 4 | 3 | 0 | 44
|  | 2021 | 27 | 6 | 9 | 2 | 3 | 1 | 1 | 4 | 4 | 5 | 3 | 26 | 91
|  | TOTALS | 86 | 106 | 69 | 31 | 41 | 20 | 42 | 49 | 47 | 66 | 42 | 99 | 698
MONTHLY ET WIRE DOWN EVENTS, INCLUDING MAJOR EVENT DAYS, EFOs
|  | YEAR | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | EoY
|  | 2015 | 0% | 0% | 0% | 33.33% | 0% | 0% | 0% | 25% | 0% | 28.57% | 0% | 0% | 7.692%
|  | 2016 | 0% | 16.67% | 0% | 25% | 0% | 0% | 0% | 50% | 0% | 0% | 0% | 0% | 6.383%
|  | 2017 | 5.882% | 13.64% | 0% | 0% | 0% | 0% | 14.29% | 0% | 0% | 9.091% | 0% | 0% | 6.25%
|  | 2018 | 0% | 0% | 0% | 0% | 0% | 0% | 12.5% | 0% | 0% | 0% | 0% | 0% | 2.273%
|  | 2019 | 12.5% | 3.704% | 0% | 20% | 0% | 0% | 0% | 0% | 0% | 66.67% | 0% | 0% | 9.091%
|  | 2020 | 8.333% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 33.33% | 0% | 4.545%
|  | 2021 | 3.704% | 33.33% | 11.11% | 0% | 0% | 0% | 100% | 25% | 0% | 20% | 0% | 3.846% | 8.791%
[16 empty] | 7 Year Average = | 6.432%

## REGIONS
Bay Area |  | Central Valley |  | North Coast |  | North Valley and Sierra |  | South Bay and Central Coast
County | City | County | City | County | City | County | City | County | City
Alameda | Alameda | Alpine |  | Del Norte |  | Butte | Biggs | Monterey | Carmel-by-the-Sea | BAY AREA
Alameda | Albany | Amador | Amador City | Humboldt | Arcata | Butte | Chico | Monterey | Del Rey Oaks | CENTRAL VALLEY
Alameda | Berkeley | Amador | Ione | Humboldt | Blue Lake | Butte | Gridley | Monterey | Gonzales | NORTH COAST
Alameda | Dublin | Amador | Jackson | Humboldt | Eureka | Butte | Oroville | Monterey | Greenfield | NORTH VALLEY AND SIERRA
Alameda | Emeryville | Amador | Plymouth | Humboldt | Ferndale | Butte | Paradise | Monterey | King City | SOUTH BAY AND CENTRAL COAST
Alameda | Fremont | Amador | Sutter Creek | Humboldt | Fortuna | Colusa | Colusa | Monterey | Marina
Alameda | Hayward | Calaveras | Angels | Humboldt | Rio Dell | Colusa | Williams | Monterey | Monterey
Alameda | Livermore | Fresno | Clovis | Humboldt | Trinidad | El Dorado | Placerville | Monterey | Pacific Grove
Alameda | Newark | Fresno | Coalinga | Lake | Clearlake | Glenn | Orland | Monterey | Salinas
Alameda | Oakland | Fresno | Firebaugh | Lake | Lakeport | Glenn | Willows | Monterey | Sand City
Alameda | Piedmont | Fresno | Fowler | Marin | Belvedere | Lassen |  | Monterey | Seaside
Alameda | Pleasanton | Fresno | Fresno | Marin | Corte Madera | Nevada | Grass Valley | Monterey | Soledad
Alameda | San Leandro | Fresno | Huron | Marin | Fairfax | Nevada | Nevada City | San Benito | Hollister
Alameda | Union City | Fresno | Kerman | Marin | Larkspur | Placer | Auburn | San Benito | San Juan Bautista
Contra Costa | Antioch | Fresno | Kingsburg | Marin | Mill Valley | Placer | Colfax | San Luis Obispo | Arroyo Grande
Contra Costa | Brentwood | Fresno | Mendota | Marin | Novato | Placer | Lincoln | San Luis Obispo | Atascadero
Contra Costa | Clayton | Fresno | Orange Cove | Marin | Ross | Placer | Loomis | San Luis Obispo | El Paso de Robles
Contra Costa | Concord | Fresno | Parlier | Marin | San Anselmo | Placer | Rocklin | San Luis Obispo | Grover Beach
Contra Costa | Danville | Fresno | Reedley | Marin | San Rafael | Placer | Roseville | San Luis Obispo | Morro Bay
Contra Costa | El Cerrito | Fresno | San Joaquin | Marin | Sausalito | Plumas |  | San Luis Obispo | Pismo Beach
Contra Costa | Hercules | Fresno | Sanger | Marin | Tiburon | Sacramento | Citrus Heights | San Luis Obispo | San Luis Obispo
Contra Costa | Lafayette | Fresno | Selma | Mendocino | Fort Bragg | Sacramento | Elk Grove | Santa Barbara | Buellton
Contra Costa | Martinez | Inyo |  | Mendocino | Point Arena | Sacramento | Folsom | Santa Barbara | Guadalupe
Contra Costa | Moraga | Kern | Arvin | Mendocino | Ukiah | Sacramento | Galt | Santa Barbara | Lompoc
Contra Costa | Oakley | Kern | Bakersfield | Mendocino | Willits | Sacramento | Isleton | Santa Barbara | Santa Maria
Contra Costa | Orinda | Kern | California City | Modoc |  | Sacramento | Rancho Cordova | Santa Barbara | Solvang
Contra Costa | Pinole | Kern | Delano | Napa | American Canyon | Sacramento | Sacramento | Santa Clara | Campbell
Contra Costa | Pittsburg | Kern | Maricopa | Napa | Calistoga | Shasta | Anderson | Santa Clara | Cupertino
Contra Costa | Pleasant Hill | Kern | McFarland | Napa | Napa | Shasta | Redding | Santa Clara | Gilroy
Contra Costa | Richmond | Kern | Ridgecrest | Napa | Saint Helena | Shasta | Shasta Lake | Santa Clara | Los Altos
Contra Costa | San Pablo | Kern | Shafter | Napa | Yountville | Sierra |  | Santa Clara | Los Altos Hills
Contra Costa | San Ramon | Kern | Taft | Siskiyou |  | Solano | Benicia | Santa Clara | Los Gatos
Contra Costa | Walnut Creek | Kern | Tehachapi | Sonoma | Cloverdale | Solano | Dixon | Santa Clara | Milpitas
San Francisco | San Francisco | Kern | Wasco | Sonoma | Cotati | Solano | Fairfield | Santa Clara | Monte Sereno
San Mateo | Atherton | Kings | Avenal | Sonoma | Healdsburg | Solano | Rio Vista | Santa Clara | Morgan Hill
San Mateo | Belmont | Kings | Corcoran | Sonoma | Petaluma | Solano | Suisun City | Santa Clara | Mountain View
San Mateo | Brisbane | Kings | Hanford | Sonoma | Rohnert Park | Solano | Vacaville | Santa Clara | Palo Alto
San Mateo | Burlingame | Kings | Lemoore | Sonoma | Santa Rosa | Solano | Vallejo | Santa Clara | San Jose
San Mateo | Colma | Madera | Chowchilla | Sonoma | Sebastopol | Sutter | Live Oak | Santa Clara | Santa Clara
San Mateo | Daly City | Madera | Madera | Sonoma | Sonoma | Sutter | Yuba City | Santa Clara | Saratoga
San Mateo | East Palo Alto | Mariposa |  | Sonoma | Windsor | Tehama | Corning | Santa Clara | Sunnyvale
San Mateo | Foster City | Merced | Atwater | Trinity |  | Tehama | Red Bluff | Santa Cruz | Capitola
San Mateo | Half Moon Bay | Merced | Dos Palos |  |  | Tehama | Tehama | Santa Cruz | Santa Cruz
San Mateo | Hillsborough | Merced | Gustine |  |  | Yolo | Davis | Santa Cruz | Scotts Valley
San Mateo | Menlo Park | Merced | Livingston |  |  | Yolo | West Sacramento | Santa Cruz | Watsonville
San Mateo | Millbrae | Merced | Los Banos |  |  | Yolo | Winters
San Mateo | Pacifica | Merced | Merced |  |  | Yolo | Woodland
San Mateo | Portola Valley | San Bernardino |  |  |  | Yuba | Marysville
San Mateo | Redwood City | San Joaquin | Escalon |  |  | Yuba | Wheatland
San Mateo | San Bruno | San Joaquin | Lathrop
San Mateo | San Carlos | San Joaquin | Lodi
San Mateo | San Mateo | San Joaquin | Manteca
San Mateo | South San Francisco | San Joaquin | Ripon
San Mateo | Woodside | San Joaquin | Stockton
|  | San Joaquin | Tracy
|  | Stanislaus | Ceres
|  | Stanislaus | Hughson
|  | Stanislaus | Modesto
|  | Stanislaus | Newman
|  | Stanislaus | Oakdale
|  | Stanislaus | Patterson
|  | Stanislaus | Riverbank
|  | Stanislaus | Turlock
|  | Stanislaus | Waterford
|  | Tulare | Dinuba
|  | Tulare | Woodlake
|  | Tuolumne | Sonora

## ET-WD-Details_2011-2022YTD
REGION | TL Area | kV Cls | kV | YEAR | Date Out | Time Out | MED | ET WD | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | CAP | RGN | TOTL Ref | Cust Afftd | CESO/ Event | CMIN/ Event | SAIFI Contr | SAIDI Contr | CAIDI | System Cust Count | Fault Type | Fault Location | AUTO / EFO / SCHD | Outage Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-01-10 04:54 | 40553.2042 | No | YES | No | 0.41319 | 595 | 2011-01-10 14:49 | 40553.6174 | F | Equipment failure | Connector/ hardware | COND | 7597 | CV-S | MD-2011-002 | 290 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-01-17 16:50 | 40560.7014 | No | YES | No | 0.77986 | 1123 | 2011-01-18 11:33 | 40561.4812 | F | External contact | Foreign object | COND | 7668 | NO-W | HM-2011-001 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-02-16 01:59 | 40590.0826 | YES | YES | No | 0.77847 | 1121 | 2011-02-16 20:40 | 40590.8611 | F | Tree | Tree failure | STRU | 7633 | NO-E | TM-2011-014 | 1680 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-02-16 03:18 | 40590.1375 | YES | YES | No | 1900-01-03 14:28 | 6628 | 2011-02-20 17:46 | 40594.7403 | F | Equipment failure | Structure-line | COND | NONE | NO-E | TM-2011-017 | 1500 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-02-17 14:37 | 40591.609 | YES | YES | No | 1900-01-02 05:27 | 4647 | 2011-02-20 20:04 | 40594.8361 | F | Equipment failure | Conductor | COND | NONE | NO-E | VD-2011-014 | 3641 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2011 | 2011-02-17 19:38 | 40591.8181 | YES | YES | No | 1900-01-01 20:17 | 4097 | 2011-02-20 15:55 | 40594.6632 | F | Equipment failure | Conductor | COND | NONE | CV-N | TE-2011-014 | 1 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2011 | 2011-02-18 06:26 | 40592.2681 | YES | YES | No | 1899-12-31 03:22 | 1642 | 2011-02-19 09:48 | 40593.4083 | F | Tree | Tree failure | STRU | NONE | CV-N | TE-2011-019 | 13543 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-02-18 11:30 | 40592.4792 | YES | YES | No | 1900-01-02 22:11 | 5651 | 2011-02-22 09:41 | 40596.4035 | C | Tree | Tree failure | COND | NONE | NO-E | VD-2011-017 | 2 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-02-24 23:58 | 40598.9986 | YES | YES | No | 1900-01-01 15:20 | 3800 | 2011-02-27 15:18 | 40601.6375 | F | Tree | Tree failure | COND | NONE | NO-E | VD-2011-023 | 3650 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2011 | 2011-02-25 01:52 | 40599.0778 | YES | YES | No | 0.57361 | 826 | 2011-02-25 15:38 | 40599.6514 | F | Equipment failure | Insulator-line | INSL | NONE | CV-N | TE-2011-020 | 13949 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-02-25 03:40 | 40599.1528 | YES | YES | No | 1899-12-31 14:16 | 2296 | 2011-02-26 17:56 | 40600.7472 | F | Equipment failure | Conductor | COND | NONE | NO-E | RM-2011-005 | 2422 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2011 | 2011-02-28 07:32 | 40602.3139 | No | YES | No | 0.54375 | 783 | 2011-02-28 20:35 | 40602.8576 | F | Equipment failure | Conductor | COND | NONE | CV-N | TE-2011-022 | 8505 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2011 | 2011-03-01 22:23 | 40603.9326 | No | YES | No | 0.44514 | 641 | 2011-03-02 09:04 | 40603.3778 | F | External contact | Car pole | STRU | NONE | CV-N | TE-2011-023 | 11802 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-03-02 00:30 | 40604.0208 | No | YES | No | 0.48889 | 704 | 2011-03-02 12:14 | 40604.5097 | F | Tree | Tree failure | INSL | 7673 | NO-E | HM-2011-007 | 2055 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2011 | 2011-03-10 16:55 | 40612.7049 | No | YES | No | 0.45208 | 651 | 2011-03-11 03:46 | 40613.1569 | F | Equipment failure | Conductor | RELY | 7690 | CC-S | DW-2011-004 | 5799 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2011 | 2011-03-17 11:06 | 40619.4625 | No | YES | No | 0.28681 | 413 | 2011-03-17 17:59 | 40619.7493 | F | Animal | Bird | GUYS | NONE | CV-N | TE-2011-024 | 5583 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2011 | 2011-03-18 19:58 | 40620.8319 | No | YES | No | 0.87431 | 1259 | 2011-03-19 16:57 | 40621.7063 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | TE-2011-029 | 5583 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2011 | 2011-03-19 07:38 | 40621.3181 | YES | YES | No | 1900-01-02 10:28 | 4948 | 2011-03-22 18:06 | 40624.7542 | C | Equipment failure | Structure-line | STRU | NONE | NO-E | VD-2011-042 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-03-20 02:56 | 40622.1222 | YES | YES | No | 0.52361 | 754 | 2011-03-20 15:30 | 40622.6458 | F | Equipment failure | Conductor | COND | NONE | NO-E | VD-2011-053 | 4350 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-03-20 08:31 | 40622.3549 | YES | YES | No | 1899-12-31 02:21 | 1581 | 2011-03-21 10:52 | 40623.4528 | F | Equipment failure | Connector/ hardware | COND | 7718 | NO-E | RM-2011-015 | 342 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-03-21 06:41 | 40623.2785 | YES | YES | No | 1899-12-31 05:22 | 1762 | 2011-03-22 12:03 | 40624.5021 | F | Tree | Tree failure | COND | 7753 | CV-S | FR-2011-019 | 3500 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-03-22 14:12 | 40624.5917 | No | YES | No | 1900-01-03 05:18 | 6078 | 2011-03-26 19:30 | 40628.8125 | C | Disaster | Other | STRU | 7751 | CV-S | LB-2011-0224 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | EFO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-03-23 14:33 | 40625.6062 | No | YES | No | 0.9625 | 1386 | 2011-03-24 13:39 | 40626.5687 | F | Tree | Tree failure | COND | 7731 | NO-W | FU-2011-050 | 2425 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-03-24 09:31 | 40626.3965 | YES | YES | No | 1899-12-31 04:54 | 1734 | 2011-03-25 14:25 | 40627.6007 | F | Equipment failure | Structure-line | COND | 7724 | NO-E | TM-2011-057 | 2665 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
BAY AREA | NORTH | 230 | 230 | 2011 | 2011-03-24 10:05 | 40626.4201 | YES | YES | No | 0.45972 | 662 | 2011-03-24 21:07 | 40626.8799 | F | Equipment failure | Connector/ hardware | COND | 7728 | BA | NE-2011-008 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-03-26 06:20 | 40628.2639 | No | YES | No | 1899-12-31 08:28 | 1948 | 2011-03-27 14:48 | 40629.6167 | F | Equipment failure | Conductor | COND | 7754 | CV-N | LB-2011-013 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-03-26 16:41 | 40628.6951 | No | YES | No | 1899-12-31 02:19 | 1579 | 2011-03-27 19:00 | 40629.7917 | F | Tree | Tree failure | COND | NONE | NO-E | TM-2011-079 | 2807 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-04-22 00:56 | 40655.0389 | No | YES | No | 0.66528 | 958 | 2011-04-22 16:54 | 40655.7042 | F | External contact | Car pole | STRU | NONE | CV-N | LB-2011-016 | 4677 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2011 | 2011-04-30 09:59 | 40663.416 | No | YES | No | 0.30486 | 439 | 2011-04-30 17:18 | 40663.7208 | F | External contact | Vandalism | COND | NONE | CV-N | TE-2011-048 | 1358 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-05-07 00:42 | 40670.0292 | No | YES | No | 0.51667 | 744 | 2011-05-07 13:06 | 40670.5458 | F | Equipment failure | Conductor | COND | 7807 | NO-E | RM-2011-028 | 1855 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-05-08 23:02 | 40671.9597 | No | YES | No | 0.47083 | 678 | 2011-05-09 10:20 | 40672.4306 | F | Weather | Lightning | COND | 7810 | NO-E | TM-2011-092 | 743 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2011 | 2011-05-08 23:03 | 40671.9604 | No | YES | No | 0.65139 | 938 | 2011-05-09 14:41 | 40672.6118 | F | Equipment failure | Conductor | COND | 7813 | CV-N | TE-2011-050 | 13949 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2011 | 2011-05-09 03:47 | 40672.1576 | No | YES | No | 0.64931 | 935 | 2011-05-09 19:22 | 40672.8069 | F | Equipment failure | Connector/ hardware | COND | NONE | CC-S | DW-2011-011 | 18227 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2011 | 2011-05-17 16:19 | 40680.6799 | No | YES | No | 1899-12-31 03:46 | 1666 | 2011-05-18 20:05 | 40681.8368 | F | Equipment failure | Connector/ hardware | COND | NONE | CC-S | ML-2011-022 | 1135 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-06-09 20:23 | 40703.8493 | No | YES | No | 0.70903 | 1021 | 2011-06-10 13:24 | 40704.5583 | F | Tree | Tree failure | COND | 7847 | NO-W | FU-2011-067 | 8130 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-06-17 09:42 | 40711.4042 | No | YES | No | 0.32083 | 462 | 2011-06-17 17:24 | 40711.725 | F | Equipment failure | Connector/ hardware | COND | NONE | NO-E | TM-2011-111 | 2 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | EFO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-06-20 15:10 | 40714.6319 | No | YES | No | 1900-01-02 03:24 | 4524 | 2011-06-23 18:34 | 40717.7736 | C | Equipment failure | Insulator-line | STRU | 7862 | NO-W | RM-2011-035 | 4 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2011 | 2011-07-02 20:18 | 40726.8458 | No | YES | No | 0.6875 | 990 | 2011-07-03 12:48 | 40727.5333 | F | External contact | Car pole | STRU | NONE | CV-S | MD-2011-046 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-07-09 16:02 | 40733.6681 | No | YES | No | 1899-12-31 08:51 | 1971 | 2011-07-11 00:53 | 40735.0368 | F | Equipment failure | Structure-line | STRU | NONE | NO-E | TM-2011-126 | 3912 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2011 | 2011-07-11 15:53 | 40735.6618 | No | YES | No | 0.54861 | 790 | 2011-07-12 05:03 | 40736.2104 | F | Equipment failure | Insulator-line | COND | NONE | CV-N | TE-2011-063 | 3 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-07-29 09:13 | 40753.384 | No | YES | No | 0.31597 | 455 | 2011-07-29 16:48 | 40753.7 | F | External contact | Aircraft | COND | 7908 | NO-E | VD-2011-124 | 4866 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-08-03 11:21 | 40758.4729 | No | YES | No | 0.32917 | 474 | 2011-08-03 19:15 | 40758.8021 | F | External contact | Car pole | STRU | 7912 | CV-N | LB-2011-031 | 1 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-08-04 18:37 | 40759.7757 | No | YES | No | 0.64167 | 924 | 2011-08-05 10:01 | 40760.4174 | F | External contact | Car pole | STRU | 7913 | CV-S | FR-2011-089 | 2730 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-08-28 01:35 | 40783.066 | No | YES | No | 0.53125 | 765 | 2011-08-28 14:20 | 40783.5972 | F | Equipment failure | Conductor | COND | 7952 | CV-N | LB-2011-038 | 1 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-08-29 10:12 | 40784.425 | No | YES | No | 0.35833 | 516 | 2011-08-29 18:48 | 40784.7833 | F | Equipment failure | Conductor | COND | NONE | NO-W | FU-2011-078 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-09-09 11:32 | 40795.4806 | No | YES | No | 1899-12-31 12:31 | 2191 | 2011-09-11 00:03 | 40797.0021 | F | Equipment failure | Connector/ hardware | GUYS | 7968 | CV-S | FR-2011-100 | 349 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-09-12 09:17 | 40798.3868 | No | YES | No | 0.50417 | 726 | 2011-09-12 21:23 | 40798.891 | F | Equipment failure | Conductor | INSL | 7978 | NO-E | RM-2011-039 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2011 | 2011-09-13 09:03 | 40799.3771 | No | YES | No | 0.46389 | 668 | 2011-09-13 20:11 | 40799.841 | F | Work Procedure Error | Not following prescribed procedures | COND | 7976 | CC-S | DW-2011-024 | 28359 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2011 | 2011-09-23 21:02 | 40809.8764 | No | YES | No | 0.64931 | 935 | 2011-09-24 12:37 | 40810.5257 | F | Equipment failure | Structure-line | STRU | 7984 | CV-S | MD-2011-091 | 116 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-10-05 16:51 | 40821.7021 | YES | YES | No | 0.17639 | 254 | 2011-10-05 21:05 | 40821.8785 | F | Weather | Lightning | COND | NONE | NO-E | RM-2011-044 | 11323 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-10-09 00:39 | 40825.0271 | No | YES | No | 0.44236 | 637 | 2011-10-09 11:16 | 40825.4694 | F | External contact | Vandalism | COND | 8007 | CV-S | FR-2011-119 | 2324 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-10-09 19:34 | 40825.8153 | No | YES | No | 1900-01-03 02:37 | 5917 | 2011-10-13 22:11 | 40829.9243 | C | Disaster | Other | STRU | NONE | NO-E | TM-2011-153 | 1906 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
BAY AREA | NORTH | 230 | 230 | 2011 | 2011-10-19 01:22 | 40835.0569 | No | YES | No | 1899-12-31 14:12 | 2292 | 2011-10-20 15:34 | 40836.6486 | F | Equipment failure | Connector/ hardware | COND | 8068 | CV-S | VD-2011-134 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-10-28 06:54 | 40844.2875 | No | YES | No | 0.44306 | 638 | 2011-10-28 17:32 | 40844.7306 | F | Tree | Tree failure | COND | 8034 | NO-W | FU-2011-087 | 5430 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2011 | 2011-11-17 01:41 | 40864.0701 | No | YES | No | 0.41319 | 595 | 2011-11-17 11:36 | 40864.4833 | F | Equipment failure | Structure-line | STRU | NONE | CV-S | FR-2011-128 | 1897 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-11-29 11:37 | 40876.484 | No | YES | No | 0.2625 | 378 | 2011-11-29 17:55 | 40876.7465 | F | Equipment failure | Connector/ hardware | COND | NONE | NO-E | TM-2011-156 | 2593 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 230 | 230 | 2011 | 2011-11-30 13:36 | 40877.5667 | YES | YES | No | 0.28958 | 417 | 2011-11-30 20:33 | 40877.8562 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | LB-2011-056 | 0 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-11-30 19:21 | 40877.8063 | YES | YES | No | 0.55208 | 795 | 2011-12-01 08:36 | 40878.3583 | F | Tree | Tree failure | COND | 8114 | NO-W | FU-2011-095 |  | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-11-30 23:55 | 40877.9965 | YES | YES | No | 0.77292 | 1113 | 2011-12-01 18:28 | 40878.7694 | F | Equipment failure | Structure-line | STRU | NONE | CV-S | FR-2011-133 | 1 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2011 | 2011-12-01 02:50 | 40878.1181 | YES | YES | No | 1900-01-01 18:40 | 4000 | 2011-12-03 21:30 | 40880.8958 | F | Equipment failure | Conductor | COND | NONE | CV-N | TE-2011-084 | 2362 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2011 | 2011-12-01 04:09 | 40878.1729 | YES | YES | No | 0.77917 | 1122 | 2011-12-01 22:51 | 40878.9521 | F | Equipment failure | Structure-line | STRU | NONE | CV-S | FR-2011-136 | 905 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-12-01 06:21 | 40878.2646 | YES | YES | No | 1899-12-31 05:05 | 1745 | 2011-12-02 11:26 | 40879.4764 | F | Tree | Tree failure | COND | 8070 | NO-E | VD-2011-142 | 3651 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 230 | 230 | 2011 | 2011-12-01 06:57 | 40878.2896 | YES | YES | No | 1899-12-31 07:38 | 1898 | 2011-12-02 14:35 | 40879.6076 | F | Tree | Tree failure | COND | 8071 | NO-E | VD-2011-143 | 2 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2011 | 2011-12-01 09:54 | 40878.4125 | YES | YES | No | 0.85694 | 1234 | 2011-12-02 06:28 | 40879.2694 | F | Equipment failure | Structure-line | STRU | 8083 | CV-S | LB-2011-057 | 1768 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2011 | 2011-12-01 12:14 | 40878.5097 | YES | YES | No | 1899-12-31 00:50 | 1490 | 2011-12-02 13:04 | 40879.5444 | F | Equipment failure | Structure-line | COND | 8081 | CV-S | FR-2011-143 | 4 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2011 | 2011-12-01 23:16 | 40878.9694 | YES | YES | No | 0.45833 | 660 | 2011-12-02 10:16 | 40879.4278 | F | Equipment failure | Conductor | COND | 8076 | NO-W | FU-2011-097 | 7848 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2011 | 2011-12-02 04:20 | 40879.1806 | No | YES | No | 0.62361 | 898 | 2011-12-02 19:18 | 40879.8042 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | TE-2011-087 | 9025 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2011 | 2011-12-03 08:50 | 40880.3681 | No | YES | No | 0.71111 | 1024 | 2011-12-04 01:54 | 40881.0792 | F | Tree | Tree failure | COND | 8072 | NO-E | TM-2011-159 | 2803 | TBD | TBD | TBD | TBD | TBD | 5411331 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-01-01 04:52 | 40909.2028 | No | YES | No | 0.55139 | 794 | 2012-01-01 18:06 | 40909.7542 | F | External contact | Car pole | STRU | 8207 | NO-E | RM-2012-001 | 1879 | 1879 | 108982 | 0.00034723 | 0.02014 | 58 | 5353272 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | CENTRAL | 115 | 115 | 2012 | 2012-01-12 21:22 | 40920.8903 | No | YES | No | 1899-12-31 00:27 | 1467 | 2012-01-13 21:49 | 40921.909 | F | External contact | Vandalism | COND | 8252 | BA | ME-2012-002 | 372 | 372 | 59374 | 6.8745e-05 | 0.010972 | 159.6075 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-01-19 05:22 | 40927.2236 | No | YES | No | 0.34861 | 502 | 2012-01-19 13:44 | 40927.5722 | F | Tree | Tree failure | COND | 8221 | NO-W | HM-2012-001 | 1999 | 1999 | 845766 | 0.00036941 | 0.1563 | 423.0945 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2012 | 2012-01-21 12:53 | 40929.5368 | No | YES | No | 0.15486 | 223 | 2012-01-21 16:36 | 40929.6917 | F | Equipment failure | Conductor | COND | 8239 | CV-N | TE-2012-005 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-01-23 10:21 | 40931.4313 | No | YES | No | 1899-12-31 06:32 | 1832 | 2012-01-24 16:53 | 40932.7035 | F | Equipment failure | Conductor | COND | NONE | NO-E | VD-2012-0063 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-02-13 03:02 | 40952.1264 | No | YES | No | 1899-12-31 12:17 | 2177 | 2012-02-14 15:19 | 40953.6382 | F | Tree | Tree failure | COND | 8275 | NO-W | HM-2012-006 | 2037 | 2037 | 523076 | 0.00037643 | 0.096663 | 256.7874 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-02-13 04:52 | 40952.2028 | No | YES | No | 0.74583 | 1074 | 2012-02-13 22:46 | 40952.9486 | F | Tree | Tree failure | COND | 8276 | NO-W | HM-2012-007 | 1747 | 1747 | 249879 | 0.00032284 | 0.046177 | 143.0332 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-02-13 08:44 | 40952.3639 | No | YES | No | 0.36389 | 524 | 2012-02-13 17:28 | 40952.7278 | F | Equipment failure | Conductor | COND | NONE | NO-E | TM-2012-017 | 2537 | 2537 | 646987 | 0.00046883 | 0.11956 | 255.0205 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 230 | 230 | 2012 | 2012-02-28 21:35 | 40967.8993 | No | YES | No | 1900-01-01 00:27 | 2907 | 2012-03-01 22:02 | 40969.9181 | F | Equipment failure | Structure-line | COND | NONE | NO-E | RM-2012-012 | 2 | 2 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 115 | 115 | 2012 | 2012-02-29 08:34 | 40968.3569 | No | YES | No | 0.87361 | 1258 | 2012-03-01 05:32 | 40969.2306 | F | Tree | Tree failure | COND | 8292 | BA | PS-2012-006 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-03-01 06:00 | 40969.25 | No | YES | No | 1899-12-31 13:38 | 2258 | 2012-03-02 19:38 | 40970.8181 | F | Tree | Tree failure | COND | 8295 | NO-W | RM-2012-017 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | NORTH | 69 | 60 | 2012 | 2012-03-06 09:45 | 40974.4062 | No | YES | No | 0.42847 | 617 | 2012-03-06 20:02 | 40974.8347 | F | Equipment failure | Structure-line | COND | 8300 | NO-E | TM-2012-019 | 882 | 882 | 51156 | 0.00016299 | 0.0094535 | 58 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-03-07 15:48 | 40975.6583 | No | YES | No | 0.91319 | 1315 | 2012-03-08 13:43 | 40976.5715 | F | Tree | Tree failure | COND | 8304 | CV-S | FR-2012-012 | 70 | 70 | 2340 | 1.2936e-05 | 0.00043243 | 33.4286 | 5353272 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2012 | 2012-03-10 03:42 | 40978.1542 | No | YES | No | 0.45694 | 658 | 2012-03-10 14:40 | 40978.6111 | F | Equipment failure | Connector/ hardware | COND | 8307 | CC-S | MD-2012-016 | 343 | 343 | 225008 | 6.3386e-05 | 0.041581 | 656 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 230 | 230 | 2012 | 2012-03-16 00:29 | 40984.0201 | No | YES | No | 0.66736 | 961 | 2012-03-16 16:30 | 40984.6875 | F | Tree | Tree failure | COND | NONE | NO-E | RM-2012-021 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-03-16 13:58 | 40984.5819 | No | YES | No | 1899-12-31 03:50 | 1670 | 2012-03-17 17:48 | 40985.7417 | F | Tree | Tree failure | COND | 8335 | NO-E | TM-2012-020 | 2627 | 2627 | 1271489 | 0.00048546 | 0.23497 | 484.008 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-03-23 21:49 | 40991.909 | No | YES | No | 0.67986 | 979 | 2012-03-24 14:08 | 40992.5889 | F | Tree | Tree failure | COND | 8334 | NO-W | FU-2012-015 | 2724 | 2724 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-03-24 01:40 | 40992.0694 | No | YES | No | 0.90278 | 1300 | 2012-03-24 23:20 | 40992.9722 | F | Tree | Tree failure | COND | 8333 | NO-W | HM-2012-012 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-03-27 13:10 | 40995.5486 | No | YES | No | 0.60972 | 878 | 2012-03-28 03:48 | 40996.1583 | F | Tree | Tree failure | COND | 8337 | NO-W | FU-2012-018 | 233 | 233 | 10485 | 4.3058e-05 | 0.0019376 | 45 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-03-31 03:49 | 40999.159 | No | YES | No | 0.57569 | 829 | 2012-03-31 17:38 | 40999.7347 | F | Tree | Tree failure | COND | 8341 | NO-W | HM-2012-015 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2012 | 2012-04-09 04:49 | 41008.2007 | No | YES | No | 0.36042 | 519 | 2012-04-09 13:28 | 41008.5611 | F | Equipment failure | Conductor | COND | 8391 | CV-N | TE-2012-015 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-04-13 16:56 | 41012.7056 | No | YES | No | 0.36597 | 527 | 2012-04-14 01:43 | 41013.0715 | F | Equipment failure | Conductor | COND | 8375 | CV-S | FR-2012-030 | 23 | 23 | 4351 | 4.2503e-06 | 0.00080405 | 197 | 5353272 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-04-27 06:13 | 41026.259 | No | YES | No | 0.59722 | 860 | 2012-04-27 20:33 | 41026.8562 | F | External contact | Car pole | STRU | 8396 | CV-S | MD-2012-026 | 594 | 594 | 60026 | 0.00010977 | 0.011093 | 101.0539 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2012 | 2012-05-26 22:44 | 41055.9472 | No | YES | No | 0.67639 | 974 | 2012-05-27 14:58 | 41056.6236 | F | External contact | Foreign object | INSL | NONE | CV-N | TE-2012-030 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 230 | 230 | 2012 | 2012-05-31 11:23 | 41060.4743 | No | YES | No | 0.85833 | 1236 | 2012-06-01 07:59 | 41061.3326 | F | Equipment failure | Conductor | COND | 8451 | CV-N | LB-2012-022 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2012 | 2012-06-12 06:04 | 41072.2528 | No | YES | No | 0.45347 | 653 | 2012-06-12 16:57 | 41072.7063 | F | Work Procedure Error | Not following prescribed procedures | COND | 8466 | CC-S | ML-2012-022 | 11904 | 11904 | 1213993 | 0.0021998 | 0.22434 | 101.9819 | 5353272 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2012 | 2012-06-14 06:09 | 41074.2562 | No | YES | No | 0.57222 | 824 | 2012-06-14 19:53 | 41074.8285 | F | Equipment failure | Conductor | COND | 8472 | CC-S | DW-2012-022 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-06-22 22:46 | 41082.9486 | No | YES | No | 0.52778 | 760 | 2012-06-23 11:26 | 41083.4764 | F | External contact | Car pole | STRU | 8624 | CV-N | LB-2012-027 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-06-26 19:14 | 41086.8014 | No | YES | No | 0.49236 | 709 | 2012-06-27 07:03 | 41087.2937 | F | External contact | Vandalism | COND | NONE | NO-W | FU-2012-040 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-06-28 09:25 | 41088.3924 | No | YES | No | 0.57153 | 823 | 2012-06-28 23:08 | 41088.9639 | F | Equipment failure | Structure-line | COND | NONE | NO-W | FU-2012-041 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 70 | 2012 | 2012-07-17 13:15 | 41107.5521 | No | YES | No | 0.44583 | 642 | 2012-07-17 23:57 | 41107.9979 | F | External contact | Car pole | STRU | 8686 | CV-N | LB-2012-028 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-07-29 19:28 | 41119.8111 | No | YES | No | 0.75972 | 1094 | 2012-07-30 13:42 | 41120.5708 | F | External contact | Car pole | STRU | 8705 | CV-N | LB-2012-029 | 10270 | 10270 | 1329351 | 0.0018979 | 0.24566 | 129.4402 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2012 | 2012-08-01 14:29 | 41122.6035 | No | YES | No | 1900-01-02 22:10 | 5650 | 2012-08-05 12:39 | 41126.5271 | C | Disaster | Fire | STRU | NONE | NO-E | RM-2012-049 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-08-01 15:24 | 41122.6417 | No | YES | No | 1900-01-02 22:11 | 5651 | 2012-08-05 13:35 | 41126.566 | C | Disaster | Fire | STRU | NONE | NO-E | RM-2012-050 | 968 | 968 | 1208796 | 0.00017888 | 0.22338 | 1248.7562 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2012 | 2012-08-04 03:55 | 41125.1632 | No | YES | No | 0.91389 | 1316 | 2012-08-05 01:51 | 41126.0771 | F | Equipment failure | Structure-line | COND | NONE | CV-S | MD-2012-038 | 128 | 128 | 13440 | 2.3654e-05 | 0.0024837 | 105 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-08-08 14:21 | 41129.5979 | No | YES | No | 0.50903 | 733 | 2012-08-09 02:34 | 41130.1069 | F | External contact | Car pole | COND | 8741 | NO-W | FU-2012-050 | 1256 | 1256 | 33912 | 0.00023211 | 0.0062669 | 27 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-08-14 05:19 | 41135.2215 | No | YES | No | 0.34444 | 496 | 2012-08-14 13:35 | 41135.566 | F | Tree | Tree failure | COND | 8744 | NO-W | FU-2012-055 | 2194 | 2194 | 256698 | 0.00040545 | 0.047437 | 117 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-08-16 17:53 | 41137.7451 | No | YES | No | 1900-01-13 18:04 | 21244 | 2012-08-31 11:57 | 41152.4979 | C | Disaster | Fire | STRU | NONE | NO-E | TM-2012-081 | 7534 | 7534 | 178694 | 0.0013923 | 0.033022 | 23.7183 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-08-26 15:27 | 41147.6438 | No | YES | No | 1900-01-01 11:58 | 3598 | 2012-08-29 03:25 | 41150.1424 | F | Disaster | Fire | STRU | NONE | NO-E | TM-2012-1380 | 5346 | 5346 | 171072 | 0.00098793 | 0.031614 | 32 | 5353272 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-08-29 01:08 | 41150.0472 | No | YES | No | 1900-01-02 16:07 | 5287 | 2012-09-01 17:15 | 41153.7188 | C | Disaster | Fire | STRU | NONE | NO-E | TM-2012-088 | 5346 | 5346 | 630918 | 0.00098793 | 0.11659 | 118.0168 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2012 | 2012-09-16 11:01 | 41168.459 | No | YES | No | 0.21806 | 314 | 2012-09-16 16:15 | 41168.6771 | F | Equipment failure | Conductor | COND | NONE | CV-N | TE-2012-047 | 10876 | 10876 | 510287 | 0.0020099 | 0.0943 | 46.9186 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-09-17 22:46 | 41169.9486 | No | YES | No | 0.36875 | 531 | 2012-09-18 07:37 | 41170.3174 | F | External contact | Vandalism | COND | 8812 | NO-E | TM-2012-091 | 1679 | 1679 | 906660 | 0.00031027 | 0.16755 | 540 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-09-18 06:11 | 41170.2576 | No | YES | No | 0.72083 | 1038 | 2012-09-18 23:29 | 41170.9785 | F | Equipment failure | Connector/ hardware | CB | NONE | CV-S | MD-2012-043 | 173 | 173 | 23355 | 3.197e-05 | 0.0043159 | 135 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2012 | 2012-09-21 15:33 | 41173.6479 | No | YES | No | 1900-01-03 00:10 | 5770 | 2012-09-25 15:43 | 41177.6549 | C | Disaster | Fire | STRU | NONE | NO-E | RM-2012-056 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-09-21 16:14 | 41173.6764 | No | YES | No | 1900-01-03 00:19 | 5773 | 2012-09-25 16:33 | 41177.6896 | C | Disaster | Fire | STRU | NONE | NO-E | RM-2012-057 | 968 | 968 | 792017 | 0.00017888 | 0.14636 | 818.1994 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2012 | 2012-09-21 17:36 | 41173.7333 | No | YES | No | 1899-12-31 23:06 | 2826 | 2012-09-23 16:42 | 41175.6958 | F | External contact | Aircraft | COND | 8822 | CV-N | LB-2012-038 | 409 | 409 | 57669 | 7.5582e-05 | 0.010657 | 141 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2012 | 2012-10-07 17:59 | 41189.7493 | No | YES | No | 0.62222 | 896 | 2012-10-08 08:55 | 41190.3715 | F | External contact | Car pole | STRU | 8858 | CV-S | MD-2012-049 | 498 | 498 | 71974 | 9.2029e-05 | 0.013301 | 144.5261 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2012 | 2012-10-14 10:36 | 41196.4417 | No | YES | No | 0.3375 | 486 | 2012-10-14 18:42 | 41196.7792 | F | Equipment failure | Connector/ hardware | CB | 8875 | NO-W | HM-2012-030 | 1497 | 1497 | 264433 | 0.00027664 | 0.048867 | 176.642 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2012 | 2012-10-19 18:23 | 41201.766 | No | YES | No | 0.40764 | 587 | 2012-10-20 04:10 | 41202.1736 | F | Disaster | Fire | STRU | 8907 | NO-E | RM-2012-060 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-10-22 04:40 | 41204.1944 | No | YES | No | 0.60417 | 870 | 2012-10-22 19:10 | 41204.7986 | F | Other | Distribution caused | STRU | 8892 | CV-N | LB-2012-039 | 3968 | 3968 | 395127 | 0.00073328 | 0.073018 | 99.5784 | 5353272 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2012 | 2012-10-22 09:02 | 41204.3764 | No | YES | No | 0.45556 | 656 | 2012-10-22 19:58 | 41204.8319 | F | Equipment failure | Connector/ hardware | COND | 8894 | CV-N | LB-2012-039 | 14847 | 14847 | 445410 | 0.0027437 | 0.082311 | 30 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2012 | 2012-11-01 12:16 | 41214.5111 | No | YES | No | 0.37292 | 537 | 2012-11-01 21:13 | 41214.884 | F | Other | Distribution caused | STRU | 8921 | CV-N | TE-2012-054 | 1593 | 1593 | 135329 | 0.00029438 | 0.025008 | 84.9523 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 500 | 500 | 2012 | 2012-11-21 08:07 | 41234.3382 | No | YES | No | 0.58889 | 848 | 2012-11-21 22:15 | 41234.9271 | F | Equipment failure | Insulator-line | COND | 8952 | NO-E | RM-2012-067 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-11-29 21:37 | 41242.9007 | No | YES | No | 0.72361 | 1042 | 2012-11-30 14:59 | 41243.6243 | F | Tree | Tree failure | COND | 8962 | NO-W | FU-2012-083 | 235 | 235 | 34310 | 4.3427e-05 | 0.0063404 | 146 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-11-29 23:57 | 41242.9979 | No | YES | No | 0.93472 | 1346 | 2012-11-30 22:23 | 41243.9326 | F | Tree | Tree failure | COND | 8960 | NO-E | TM-2012-113 | 4335 | 4335 | 897345 | 0.0008011 | 0.16583 | 207 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 230 | 230 | 2012 | 2012-11-30 01:21 | 41243.0563 | No | YES | No | 1900-03-03 22:38 | 92078 | 2013-02-01 23:59 | 41306.9993 | F | Tree | Tree failure | COND | 8959 | NO-E | RM-2012-069 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2012 | 2012-12-01 21:07 | 41244.8799 | No | YES | No | 0.82569 | 1189 | 2012-12-02 16:56 | 41245.7056 | F | Equipment failure | Conductor | COND | 8976 | NO-W | RM-2012-071 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-12-02 00:07 | 41245.0049 | YES | YES | No | 0.73542 | 1059 | 2012-12-02 17:46 | 41245.7403 | F | Tree | Tree failure | COND | 8968 | NO-W | FU-2012-084 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-12-02 01:07 | 41245.0465 | YES | YES | No | 0.7125 | 1026 | 2012-12-02 18:13 | 41245.759 | F | Equipment failure | Structure-line | COND | 8971 | NO-E | RM-2012-072 | 2005 | 2005 | 300750 | 0.00037052 | 0.055578 | 150 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2012 | 2012-12-02 03:08 | 41245.1306 | YES | YES | No | 0.90833 | 1308 | 2012-12-03 00:56 | 41246.0389 | F | Equipment failure | Structure-line | COND | 8973 | NO-E | TM-2012-119 | 8741 | 8741 | 1335197 | 0.0016153 | 0.24674 | 152.7511 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 115 | 115 | 2012 | 2012-12-02 03:41 | 41245.1535 | YES | YES | No | 0.88194 | 1270 | 2012-12-03 00:51 | 41246.0354 | F | Equipment failure | Structure-line | STRU | 8970 | NO-W | FU-2012-092 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-12-02 07:21 | 41245.3063 | YES | YES | No | 0.48889 | 704 | 2012-12-02 19:05 | 41245.7951 | F | Tree | Tree failure | COND | NONE | NO-W | TM-2012-128 | 1040 | 1040 | 454426 | 0.00019219 | 0.083977 | 436.9481 | 5353272 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2012 | 2012-12-03 10:00 | 41246.4167 | No | YES | No | 0.30972 | 446 | 2012-12-03 17:26 | 41246.7264 | F | Equipment failure | Insulator-line | COND | 9001 | CC-S | DW-2012-034 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-12-07 15:12 | 41250.6333 | No | YES | No | 1899-12-31 05:04 | 1744 | 2012-12-08 20:16 | 41251.8444 | F | Equipment failure | Conductor | COND | 8993 | CV-S | LB-2012-045 | 3124 | 3124 | 353012 | 0.00057731 | 0.065236 | 113 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2012 | 2012-12-19 06:06 | 41262.2542 | No | YES | No | 0.4 | 576 | 2012-12-19 15:42 | 41262.6542 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | TE-2012-1230 | 406 | 406 | 39556 | 7.5028e-05 | 0.0073098 | 97.4286 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-12-20 07:25 | 41263.309 | No | YES | No | 0.50347 | 725 | 2012-12-20 19:30 | 41263.8125 | F | Tree | Tree failure | COND | NONE | NO-W | FU-2012-097 | 235 | 235 | 21385 | 4.3427e-05 | 0.0039519 | 91 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2012 | 2012-12-20 23:43 | 41263.9882 | No | YES | No | 1900-01-07 11:31 | 12211 | 2012-12-29 11:14 | 41272.4681 | C | Equipment failure | Structure-line | COND | 9027 | NO-W | RM-2012-084 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2012 | 2012-12-20 23:47 | 41263.991 | No | YES | No | 0.79653 | 1147 | 2012-12-21 18:54 | 41264.7875 | F | Weather | Snow/ ice | COND | 9014 | NO-E | RM-2012-085 | 608 | 608 | 543856 | 0.00011236 | 0.1005 | 894.5 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2012 | 2012-12-21 05:06 | 41264.2125 | YES | YES | No | 1900-01-05 14:17 | 9497 | 2012-12-27 19:23 | 41270.8076 | C | Equipment failure | Structure-line | COND | 9026 | NO-W | RM-2012-086 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-12-21 06:50 | 41264.2847 | YES | YES | No | 1899-12-31 10:49 | 2089 | 2012-12-22 17:39 | 41265.7354 | F | Tree | Tree failure | COND | 9015 | NO-E | RM-2012-090 | 249 | 249 | 48555 | 4.6015e-05 | 0.0089728 | 195 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2012 | 2012-12-21 07:00 | 41264.2917 | YES | YES | No | 1900-01-02 05:11 | 4631 | 2012-12-24 12:11 | 41267.5076 | C | Equipment failure | Structure-line | COND | NONE | NO-E | RM-2012-NA | 801 | 801 | 2548655 | 0.00014802 | 0.47098 | 3181.8414 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2012 | 2012-12-21 10:51 | 41264.4521 | YES | YES | No | 1900-02-09 05:45 | 59385 | 2013-01-31 16:36 | 41305.6917 | F | Equipment failure | Structure-line | COND | NONE | NO-E | TM-2012-133 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2012 | 2012-12-23 10:11 | 41266.4243 | YES | YES | No | 0.3375 | 486 | 2012-12-23 18:17 | 41266.7618 | F | Equipment failure | Conductor | COND | NONE | NO-W | FU-2012-100 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2012 | 2012-12-23 15:00 | 41266.625 | YES | YES | No | 1899-12-31 04:43 | 1723 | 2012-12-24 19:43 | 41267.8215 | F | Equipment failure | Conductor | COND | NONE | CV-N | TE-2012-060 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2012 | 2012-12-23 16:37 | 41266.6924 | YES | YES | No | 1899-12-31 02:44 | 1604 | 2012-12-24 19:21 | 41267.8063 | F | Equipment failure | Conductor | COND | NONE | CC-N | NE-2012-014 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2012 | 2012-12-24 09:56 | 41267.4139 | No | YES | No | 0.049306 | 71 | 2012-12-24 11:07 | 41267.4632 | F | Other | Distribution caused | COND | NONE | CV-S | MD-2012-068 | 178 | 178 | 12638 | 3.2894e-05 | 0.0023355 | 71 | 5353272 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2012 | 2012-12-26 10:11 | 41269.4243 | No | YES | No | 0.15694 | 226 | 2012-12-26 13:57 | 41269.5813 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | TE-2012-063 | 0 | 0 | 0 | 0 | 0 | 0 | 5353272 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2013 | 2013-01-02 18:06 | 41276.7542 | No | YES | No | 0.4 | 576 | 2013-01-03 03:42 | 41277.1542 | F | External contact | Car pole | STRU | 9050 | CV-N | TE-2013-001 | 1712 | 1712 | 246277 | 0.00031478 | 0.045283 | 143.8534 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2013 | 2013-02-07 09:03 | 41312.3771 | No | YES | No | 0.27986 | 403 | 2013-02-07 15:46 | 41312.6569 | F | Equipment failure | Connector/ hardware | STRU | 9095 | CV-S | FR-2013-006 | 3 | 3 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2013 | 2013-02-19 16:01 | 41324.6674 | No | YES | No | 1899-12-31 01:42 | 1542 | 2013-02-20 17:43 | 41325.7382 | F | Equipment failure | Conductor | COND | 9173 | CV-N | TE-2013-007 | 8285 | 8285 | 240376 | 0.0015477 | 0.044903 | 29.0134 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2013 | 2013-03-03 21:09 | 41336.8812 | No | YES | No | 0.39583 | 570 | 2013-03-04 06:39 | 41337.2771 | F | Equipment failure | Connector/ hardware | COND | 9212 | NO-W | FU-2013-007 | 213 | 213 | 15549 | 3.9789e-05 | 0.0029046 | 73 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2013 | 2013-03-04 20:36 | 41337.8583 | No | YES | No | 0.50069 | 721 | 2013-03-05 08:37 | 41338.359 | F | External contact | Car pole | STRU | 9268 | CV-N | TE-2013-009 | 1609 | 1609 | 328833 | 0.00030056 | 0.061427 | 204.371 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2013 | 2013-03-08 03:54 | 41341.1625 | No | YES | No | 0.53264 | 767 | 2013-03-08 16:41 | 41341.6951 | F | Contamination | Animal waste | COND | 9215 | CV-S | FR-2013-017 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2013 | 2013-03-11 13:43 | 41344.5715 | No | YES | No | 0.52292 | 753 | 2013-03-12 02:16 | 41345.0944 | F | External contact | Vandalism | COND | 9219 | CV-S | LB-2013-010 | 3062 | 3062 | 264551 | 0.00057199 | 0.049419 | 86.3981 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2013 | 2013-04-08 08:13 | 41372.3424 | YES | YES | No | 0.75486 | 1087 | 2013-04-09 02:20 | 41373.0972 | F | Equipment failure | Structure-line | COND | 9288 | NO-E | VD-2013-010 | 1 | 1 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2013 | 2013-04-14 10:22 | 41378.4319 | No | YES | No | 0.73264 | 1055 | 2013-04-15 03:57 | 41379.1646 | F | Equipment failure | Conductor | COND | 9309 | NO-E | VD-2013-013 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 230 | 230 | 2013 | 2013-04-23 00:50 | 41387.0347 | No | YES | No | 0.80972 | 1166 | 2013-04-23 20:16 | 41387.8444 | F | Equipment failure | Connector/ hardware | COND | 9350 | BA | FU-2013-013 | 8868 | 8868 | 739458 | 0.0016566 | 0.13813 | 83.385 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-05-01 10:22 | 41395.4319 | No | YES | No | 0.78889 | 549 | 2013-05-02 05:18 | 41396.2208 | F | Equipment failure | Connector/ hardware | STRU | 9387 | NO-E | VD-2013-0410 | 2 | 2 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-05-02 10:22 | 41396.4319 | No | YES | No | 0.045833 | 260 | 2013-05-02 11:28 | 41396.4778 | F | Equipment failure | Conductor | COND | 9388 | NO-E | VD-2013-0410 | 2 | 2 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2013 | 2013-05-19 09:00 | 41413.375 | No | YES | No | 0.66389 | 956 | 2013-05-20 00:56 | 41414.0389 | F | Equipment failure | Conductor | COND | 9534 | NO-E | VD-2013-024 | 1319 | 1319 | 179774 | 0.00024639 | 0.033582 | 136.2957 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2013 | 2013-05-21 10:18 | 41415.4292 | No | YES | No | 0.65347 | 941 | 2013-05-22 01:59 | 41416.0826 | F | Equipment failure | Conductor | COND | 9453 | NO-W | RM-2013-023 | 4 | 4 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2013 | 2013-05-22 21:07 | 41416.8799 | No | YES | No | 0.50556 | 728 | 2013-05-23 09:15 | 41417.3854 | F | Tree | Tree failure | COND | 9449 | NO-W | FU-2013-020 | 2683 | 2683 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-05-31 16:37 | 41425.6924 | No | YES | No | 0.48194 | 694 | 2013-06-01 04:11 | 41426.1743 | F | External contact | Car pole | STRU | 9459 | NO-E | RM-2013-025 | 1813 | 1813 | 279041 | 0.00033867 | 0.052125 | 153.9112 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-06-09 14:59 | 41434.6243 | No | YES | No | 0.33611 | 484 | 2013-06-09 23:03 | 41434.9604 | F | Equipment failure | Conductor | COND | 9486 | NO-E | TM-2013-023 | 906 | 906 | 244968 | 0.00016924 | 0.04576 | 270.3841 | 5380759 | NA | NA | EFO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2013 | 2013-08-09 18:00 | 41495.75 | No | YES | No | 0.35139 | 506 | 2013-08-10 02:26 | 41496.1014 | F | Weather | Lightning | COND | 9645 | NO-W | HM-2013-016 | 3183 | 3183 | 1659342 | 0.00059459 | 0.30997 | 521.3139 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2013 | 2013-08-11 14:48 | 41497.6167 | No | YES | No | 0.78611 | 1132 | 2013-08-12 09:40 | 41498.4028 | F | External contact | Vandalism | COND | 9644 | CC-S | MD-2013-040 | 330 | 330 | 51480 | 6.1645e-05 | 0.0096165 | 156 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2013 | 2013-08-18 16:28 | 41504.6861 | No | YES | No | 1900-01-04 23:50 | 8630 | 2013-08-24 16:18 | 41510.6792 | C | Tree | Tree failure | COND | 9661 | CV-N | TE-2013-032 | 11038 | 11038 | 1202244 | 0.0020619 | 0.22458 | 108.9186 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2013 | 2013-08-24 12:11 | 41510.5076 | No | YES | No | 0.64514 | 929 | 2013-08-25 03:40 | 41511.1528 | F | External contact | Aircraft | COND | 9736 | CV-S | MD-2013-042 | 95 | 95 | 8550 | 1.7746e-05 | 0.0015972 | 90 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2013 | 2013-08-27 10:30 | 41513.4375 | No | YES | No | 0 | 0 | 2013-08-27 10:30 | 41513.4375 | F | Equipment failure | Conductor | NONE | 9686 | CC-S | DW-2013-NA | 2775 | 2775 | 305594 | 0.00051837 | 0.057085 | 110.124 | 5380759 | NA | NA | SCHD | Single Mode
NORTH COAST | CENTRAL | 230 | 230 | 2013 | 2013-09-08 15:41 | 41525.6535 | No | YES | No | 1899-12-31 02:29 | 1589 | 2013-09-09 18:10 | 41526.7569 | F | Disaster | Fire | COND | 9716 | NO-W | FU-2013-074 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 115 | 115 | 2013 | 2013-09-23 18:56 | 41540.7889 | No | YES | No | 1899-12-31 00:08 | 1448 | 2013-09-24 19:04 | 41541.7944 | F | External contact | Aircraft | COND | NONE | NO-W | FU-2013-079 | 7669 | 7669 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2013 | 2013-09-24 02:57 | 41541.1229 | No | YES | No | 0.50694 | 730 | 2013-09-24 15:07 | 41541.6299 | F | Equipment failure | Connector/ hardware | COND | NONE | CC-S | DW-2013-028 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 500 | 500 | 2013 | 2013-09-24 17:54 | 41541.7458 | No | YES | No | 0.75278 | 1084 | 2013-09-25 11:58 | 41542.4986 | F | External contact | Aircraft | COND | NONE | NO-E | TM-2013-067 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 230 | 230 | 2013 | 2013-10-03 04:57 | 41550.2063 | No | YES | No | 0.060417 | 87 | 2013-10-03 06:24 | 41550.2667 | F | Work Procedure Error | Not following prescribed procedures | COND | 9791 | BA | PS-2013-0001 | 24256 | 24256 | 2107304 | 0.0045311 | 0.39365 | 86.8776 | 5380759 | NA | NA | SCHD | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2013 | 2013-10-09 07:39 | 41556.3187 | No | YES | No | 1899-12-31 11:29 | 2129 | 2013-10-10 19:08 | 41557.7972 | F | Equipment failure | Structure-line | COND | NONE | CV-S | MD-2013-045 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2013 | 2013-10-09 08:26 | 41556.3514 | No | YES | No | 0.55278 | 796 | 2013-10-09 21:42 | 41556.9042 | F | Equipment failure | Structure-line | COND | NONE | CV-S | MD-2013-046 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-10-21 03:17 | 41568.1368 | No | YES | No | 0.38333 | 552 | 2013-10-21 12:29 | 41568.5201 | F | Equipment failure | Conductor | COND | 9826 | NO-E | VD-2013-067 | 2606 | 2606 | 956799 | 0.00048681 | 0.17873 | 367.1523 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2013 | 2013-10-27 19:30 | 41574.8125 | No | YES | No | 0.68264 | 983 | 2013-10-28 11:53 | 41575.4951 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | TE-2013-046 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2013 | 2013-10-27 19:41 | 41574.8201 | No | YES | No | 1899-12-31 23:59 | 2879 | 2013-10-29 19:40 | 41576.8194 | F | Equipment failure | Structure-line | STRU | NONE | CV-N | TE-2013-047 | 3 | 3 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2013 | 2013-10-27 23:44 | 41574.9889 | No | YES | No | 0.77778 | 1120 | 2013-10-28 18:24 | 41575.7667 | F | Equipment failure | Structure-line | STRU | NONE | CV-S | FR-2013-067 | 1 | 1 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2013 | 2013-10-28 15:42 | 41575.6542 | No | YES | No | 0.34653 | 499 | 2013-10-29 00:01 | 41576.0007 | F | Other | Distribution caused | STRU | NONE | CV-S | FR-2013-068 | 1914 | 1914 | 326001 | 0.00035754 | 0.060898 | 170.3245 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2013 | 2013-10-29 07:42 | 41576.3208 | No | YES | No | 0.2375 | 342 | 2013-10-29 13:24 | 41576.5583 | F | Equipment failure | Connector/ hardware | COND | NONE | CC-S | ML-2013-021 | 1467 | 1467 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2013 | 2013-10-31 06:07 | 41578.2549 | No | YES | No | 0.45417 | 654 | 2013-10-31 17:01 | 41578.709 | F | Equipment failure | Connector/ hardware | COND | NONE | BA | TE-2013-049 | 319 | 319 | 103383 | 5.959e-05 | 0.019312 | 324.0846 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2013 | 2013-11-02 18:31 | 41580.7715 | No | YES | No | 0.29514 | 425 | 2013-11-03 01:36 | 41581.0667 | F | Equipment failure | Conductor | COND | 9849 | CC-S | ML-2013-024 | 4517 | 4517 | 1222178 | 0.00084378 | 0.2283 | 270.5729 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2013 | 2013-11-09 15:54 | 41587.6625 | No | YES | No | 0.975 | 1404 | 2013-11-10 15:18 | 41588.6375 | F | Disaster | Fire | STRU | 9876 | NO-W | HM-2013-027 | 1462 | 1462 | 24854 | 0.0002731 | 0.0046428 | 17 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2013 | 2013-11-21 19:03 | 41599.7937 | YES | YES | No | 1899-12-31 21:03 | 2703 | 2013-11-23 16:06 | 41601.6708 | F | Tree | Tree failure | COND | 9896 | NO-W | FU-2013-090 | 15282 | 15282 | 4273884 | 0.0028547 | 0.79837 | 279.6678 | 5380759 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2013 | 2013-11-22 00:50 | 41600.0347 | YES | YES | No | 0.58889 | 848 | 2013-11-22 14:58 | 41600.6236 | F | Equipment failure | Conductor | COND | 9897 | NO-W | FU-2013-093 | 199 | 199 | 35014 | 3.7174e-05 | 0.0065407 | 175.9497 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-11-22 02:55 | 41600.1215 | YES | YES | No | 0.76944 | 1108 | 2013-11-22 21:23 | 41600.891 | F | Tree | Tree failure | COND | 9900 | NO-E | RM-2013-054 | 785 | 785 | 321065 | 0.00014664 | 0.059975 | 409 | 5380759 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2013 | 2013-11-25 04:22 | 41603.1819 | No | YES | No | 0.20556 | 296 | 2013-11-25 09:18 | 41602.3875 | F | Equipment failure | Conductor | COND | 9939 | BA | VD-2013-NA | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2013 | 2013-12-06 22:12 | 41614.925 | No | YES | No | 0.60208 | 867 | 2013-12-07 12:39 | 41615.5271 | F | Equipment failure | Insulator-line | STRU | 9947 | BA | TE-2013-065 | 55 | 55 | 30745 | 1.0274e-05 | 0.0057432 | 559 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2013 | 2013-12-08 23:41 | 41616.9868 | No | YES | No | 0.71944 | 1036 | 2013-12-09 16:57 | 41617.7063 | F | Equipment failure | Connector/ hardware | COND | 9948 | CV-N | LB-2013-0836 | 0 | 0 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2013 | 2013-12-13 00:17 | 41621.0118 | No | YES | No | 0.76458 | 1101 | 2013-12-13 18:38 | 41621.7764 | F | Equipment failure | Connector/ hardware | COND | 9997 | CC-S | DW-2013-031 | 1 | 1 | 0 | 0 | 0 | 0 | 5380759 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2013 | 2013-12-16 20:07 | 41624.8382 | No | YES | No | 0.59236 | 853 | 2013-12-17 10:20 | 41625.4306 | F | Equipment failure | Structure-line | COND | 9981 | NO-E | TM-2013-083 | 2745 | 2745 | 234666 | 0.00051277 | 0.043836 | 85.4885 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2013 | 2013-12-19 15:21 | 41627.6396 | No | YES | No | 0.42014 | 605 | 2013-12-20 01:26 | 41628.0597 | F | Work Procedure Error | Not following prescribed procedures | PROC | 9982 | CV-S | MD-2013-061 | 30607 | 30607 | 2188819 | 0.0057174 | 0.40887 | 71.5137 | 5380759 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2014 | 2014-01-01 18:40 | 41640.7778 | No | YES | No | 0.83264 | 1199 | 2014-01-02 14:39 | 41641.6104 | F | External contact | Foreign object | COND | 10042 | CV-N | TE-2014-001 | 2 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-01-14 07:24 | 41653.3083 | No | YES | No | 0.37222 | 536 | 2014-01-14 16:20 | 41653.6806 | F | Equipment failure | Conductor | COND | 10029 | CV-N | LB-2014-004 | 0 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-01-15 16:14 | 41654.6764 | No | YES | No | 0.20278 | 292 | 2014-01-15 21:06 | 41654.8792 | F | External contact | Foreign object | STRU | 10037 | NO-E | TM-2014-0373 | 896 | 896 | 216886 | 0.00016652 | 0.040308 | 242.0603 | 5412924 | NA | NA | EFO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2014 | 2014-01-18 01:18 | 41657.0542 | No | YES | No | 0.40208 | 579 | 2014-01-18 10:57 | 41657.4563 | F | Equipment failure | Insulator-line | COND | 10046 | CC-S | ML-2014-001 | 208 | 208 | 17595 | 3.8656e-05 | 0.00327 | 84.5913 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2014 | 2014-01-21 05:58 | 41660.2486 | No | YES | No | 1899-12-31 08:29 | 1949 | 2014-01-22 14:27 | 41661.6021 | F | Equipment failure | Conductor | COND | 10043 | CV-N | TE-2014-004 | 0 | 2 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2014 | 2014-02-24 07:00 | 41694.2917 | No | YES | No | 0.50903 | 733 | 2014-02-24 19:13 | 41694.8007 | F | Equipment failure | Insulator-line | COND | 10120 | CC-S | MD-2014-009 | 327 | 327 | 47088 | 6.0772e-05 | 0.0087512 | 144 | 5412924 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2014 | 2014-02-28 09:03 | 41698.3771 | No | YES | No | 0.35208 | 507 | 2014-02-28 17:30 | 41698.7292 | F | Tree | Tree failure | INSL | 10128 | NO-W | FU-2014-009 | 14335 | 14335 | 1300990 | 0.0026641 | 0.24179 | 90.7562 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2014 | 2014-03-08 04:00 | 41706.1667 | No | YES | No | 0.30278 | 436 | 2014-03-08 11:16 | 41706.4694 | F | External contact | Car pole | STRU | 10148 | CV-S | MD-2014-012 | 3 | 3 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2014 | 2014-03-26 12:42 | 41724.5292 | No | YES | No | 1899-12-31 01:46 | 1546 | 2014-03-27 14:28 | 41725.6028 | F | External contact | Vandalism | COND | 10180 | CV-N | TE-2014-016 | 4354 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-05-13 08:40 | 41772.3611 | No | YES | No | 0.25764 | 371 | 2014-05-13 14:51 | 41772.6188 | F | Equipment failure | Conductor | COND | 10277 | NO-E | RM-2014-019 | 783 | 783 | 82215 | 0.00014552 | 0.015279 | 105 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2014 | 2014-05-14 11:56 | 41773.4972 | No | YES | No | 0.69375 | 999 | 2014-05-15 04:35 | 41774.191 | F | Equipment failure | Insulator-line | STRU | 10287 | NO-E | TM-2014-029 | 726 | 726 | 54072 | 0.00013493 | 0.010049 | 74.4793 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-05-27 12:46 | 41786.5319 | No | YES | No | 0.63264 | 911 | 2014-05-28 03:57 | 41787.1646 | F | Contamination | Animal waste | STRU | 10301 | CV-S | FR-2014-032 | 688 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-07-04 01:40 | 41824.0694 | No | YES | No | 0.43889 | 632 | 2014-07-04 12:12 | 41824.5083 | F | Tree | Tree failure | COND | 10395 | NO-E | TM-2014-042 | 2798 | 2798 | 1719539 | 0.00052 | 0.31957 | 614.56 | 5412924 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2014 | 2014-07-07 19:09 | 41827.7979 | No | YES | No | 0.28333 | 408 | 2014-07-08 01:57 | 41828.0813 | F | Equipment failure | Connector/ hardware | PROC | 10408 | NO-W | HM-2014-013 | 9399 | 9399 | 1319955 | 0.0017468 | 0.24531 | 140.4357 | 5412924 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2014 | 2014-07-14 17:06 | 41834.7125 | No | YES | No | 0.57083 | 822 | 2014-07-15 06:48 | 41835.2833 | F | External contact | Car pole | STRU | 10424 | CC-S | ML-2014-012 | 3104 | 3104 | 448312 | 0.00057687 | 0.083318 | 144.4304 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-07-18 07:42 | 41838.3208 | No | YES | No | 0.43056 | 620 | 2014-07-18 18:02 | 41838.7514 | F | External contact | Foreign object | COND | 10438 | NO-E | RM-2014-027 | 783 | 783 | 100224 | 0.00014552 | 0.018626 | 128 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-07-20 12:23 | 41840.516 | No | YES | No | 1899-12-31 04:19 | 1699 | 2014-07-21 16:42 | 41841.6958 | F | Weather | Lightning | COND | 10436 | CV-S | LB-2014-030 | 3077 | 3077 | 388076 | 0.00057185 | 0.072123 | 126.1215 | 5412924 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | 2014 | 2014-07-24 15:26 | 41844.6431 | No | YES | No | 0.75417 | 1086 | 2014-07-25 09:32 | 41845.3972 | F | Tree | Tree failure | COND | 10456 | BA | SA-2014-0655 | 11839 | 7330 | 1085259 | 0.0013623 | 0.20169 | 148.0572 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 500 | 500 | 2014 | 2014-08-03 06:41 | 41854.2785 | No | YES | No | 1900-01-02 07:11 | 4751 | 2014-08-06 13:52 | 41857.5778 | C | Disaster | Fire | COND | 10465 | CV-S | MD-2014-033 | 0 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2014 | 2014-08-14 20:24 | 41865.85 | No | YES | No | 0.46458 | 669 | 2014-08-15 07:33 | 41866.3146 | F | External contact | Car pole | COND | 10486 | CV-S | FR-2014-046 | 1814 | 1692 | 212550 | 0.00031445 | 0.039502 | 125.6206 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-08-21 09:11 | 41872.3826 | No | YES | No | 0.32639 | 470 | 2014-08-21 17:01 | 41872.709 | F | Animal | Bird | COND | 10499 | NO-E | TM-2014-052 | 3419 | 3418 | 381757 | 0.00063523 | 0.070949 | 111.6902 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2014 | 2014-08-27 03:34 | 41878.1486 | No | YES | No | 1899-12-31 03:00 | 1620 | 2014-08-28 06:34 | 41879.2736 | F | External contact | Car pole | STRU | 10518 | CV-S | MD-2014-036 | 3124 | 3124 | 452034 | 0.00058059 | 0.084009 | 144.6972 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-09-03 16:22 | 41885.6819 | No | YES | No | 0.43264 | 623 | 2014-09-04 02:45 | 41886.1146 | F | Disaster | Fire | INSL | 10527 | NO-E | RM-2014-044 | 6396 | 6396 | 415511 | 0.0011887 | 0.077222 | 64.9642 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-09-12 05:55 | 41894.2465 | No | YES | No | 0.31875 | 459 | 2014-09-12 13:34 | 41894.5653 | F | External contact | Car pole | STRU | 10562 | NO-E | TM-2014-059 | 4044 | 4044 | 501456 | 0.00075157 | 0.093194 | 124 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-09-17 19:53 | 41899.8285 | No | YES | No | 1900-01-14 02:01 | 21721 | 2014-10-02 21:54 | 41914.9125 | C | Disaster | Fire | COND | 10607 | NO-E | VD-2014-051 | 0 | 0 |  |  |  |  | 5412924 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2014 | 2014-10-25 03:17 | 41937.1368 | No | YES | No | 0.44167 | 636 | 2014-10-25 13:53 | 41937.5785 | F | Tree | Tree failure | COND | 10697 | NO-W | HM-2014-021 | 1170 | 1170 | 66690 | 0.00021744 | 0.012394 | 57 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-10-31 22:23 | 41943.9326 | No | YES | No | 0.70347 | 1013 | 2014-11-01 15:16 | 41944.6361 | F | Equipment failure | Conductor | COND | 10674 | CV-S | MD-2014-052 | 156 | 156 | 49608 | 2.8992e-05 | 0.0092195 | 318 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2014 | 2014-12-03 11:13 | 41976.4674 | YES | YES | No | 0.24444 | 352 | 2014-12-03 17:05 | 41976.7118 | F | Equipment failure | Connector/ hardware | COND | 10737 | CV-N | TE-2014-047 | 0 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-03 11:33 | 41976.4812 | YES | YES | No | 0.51667 | 744 | 2014-12-03 23:57 | 41976.9979 | F | Equipment failure | Structure-line | COND | NONE | NO-E | TM-2014-075 | 1 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2014 | 2014-12-11 06:20 | 41984.2639 | YES | YES | No | 1899-12-31 09:39 | 2019 | 2014-12-12 15:59 | 41985.666 | F | Tree | Tree failure | COND | 10770 | NO-W | FU-2014-062 | 2699 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-11 09:07 | 41984.3799 | YES | YES | No | 0.45347 | 653 | 2014-12-11 20:00 | 41984.8333 | F | Tree | Tree failure | COND | 10774 | NO-E | TM-2014-086 | 1546 | 1546 | TBD | TBD | TBD | TBD | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-12-11 21:54 | 41984.9125 | YES | YES | No | 1899-12-31 00:41 | 1481 | 2014-12-12 22:35 | 41985.941 | F | Equipment failure | Structure-line | COND | 10762 | CV-S | MD-2014-057 | 292 | 292 | TBD | TBD | TBD | TBD | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2014 | 2014-12-12 00:03 | 41985.0021 | YES | YES | No | 0.54444 | 784 | 2014-12-12 13:07 | 41985.5465 | F | Equipment failure | Conductor | COND | 10764 | CV-S | MD-2014-058 | 160 | 160 | TBD | TBD | TBD | TBD | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-12 01:29 | 41985.0618 | YES | YES | No | 1899-12-31 14:28 | 2308 | 2014-12-13 15:57 | 41986.6646 | F | Equipment failure | Conductor | COND | 10775 | NO-E | TM-2014-087 | 2204 | 2204 | TBD | TBD | TBD | TBD | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-12 09:44 | 41985.4056 | YES | YES | No | 1899-12-31 06:13 | 1813 | 2014-12-13 15:57 | 41986.6646 | F | Equipment failure | Conductor | COND | 10776 | NO-E | TM-2014-096 | 2847 | 2847 | TBD | TBD | TBD | TBD | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-12-13 22:16 | 41986.9278 | No | YES | No | 0.50347 | 725 | 2014-12-14 10:21 | 41987.0958 | F | Equipment failure | Connector/ hardware | COND | 10760 | CV-S | FR-2014-073 | 0 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-16 03:39 | 41989.1521 | No | YES | No | 0.80694 | 1162 | 2014-12-16 23:01 | 41989.959 | F | External contact | Car pole | COND | NONE | NO-E | TM-2014-097 | TBD | TBD | TBD | TBD | TBD | TBD | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2014 | 2014-12-21 05:07 | 41994.2132 | No | YES | No | 0.45903 | 661 | 2014-12-21 16:08 | 41994.6722 | F | Equipment failure | Connector/ hardware | COND | 10793 | CV-S | FR-2014-074 | 0 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2014 | 2014-12-30 11:02 | 42003.4597 | YES | YES | No | 0.26181 | 377 | 2014-12-30 17:19 | 42003.7215 | F | Tree | Tree failure | COND | 10805 | BA | NE-2014-010 | 1 | 0 | 0 | 0 | 0 | 0 | 5412924 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-30 23:25 | 42003.9757 | YES | YES | No | 1900-01-01 20:09 | 4089 | 2015-01-02 19:34 | 42006.8153 | F | Equipment failure | Structure-line | COND | NONE | NO-E | VD-2014-085 | 1840 | 1840 | 515260 | 0.00034196 | 0.09576 | 280.0326 | 5412924 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2014 | 2014-12-31 06:46 | 42004.2819 | No | YES | No | 0.33611 | 484 | 2014-12-31 14:50 | 42004.6181 | F | External contact | Car pole | COND | 10810 | CV-N | TE-2014-052 | 3372 | 3372 | 727670 | 0.00062668 | 0.13524 | 215.7977 | 5412924 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2014 | 2014-12-31 12:08 | 42004.5056 | No | YES | No | 0.29653 | 427 | 2014-12-31 19:15 | 42004.8021 | F | Equipment failure | Conductor | COND | 10813 | NO-E | TM-2014-101 | 1736 | 1736 | 313166 | 0.00032263 | 0.058201 | 180.3952 | 5412924 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-01-12 11:55 | 42016.4965 | No | YES | No | 0.47639 | 686 | 2015-01-12 23:21 | 42016.9729 | F | External contact | Car pole | COND | 10835 | NO-E | TM-2015-002 | 2138 | 2138 | 142453 | 0.00039254 | 0.026154 | 66.6291 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-02-06 00:24 | 42041.0167 | YES | YES | No | 1900-01-03 22:04 | 7084 | 2015-02-10 22:28 | 42045.9361 | C | Tree | Tree failure | STRU | 10912 | NO-E | RM-2015-006 | 9 | 9 | 52209 | 1.6524e-06 | 0.0095856 | 5801 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-02-06 08:14 | 42041.3431 | YES | YES | No | 0.45139 | 650 | 2015-02-06 19:04 | 42041.7944 | F | Tree | Tree failure | COND | 10877 | NO-W | FU-2015-005 | 6297 | 216 | 81216 | 3.9658e-05 | 0.014911 | 376 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 500 | 500 | 2015 | 2015-02-06 08:57 | 42041.3729 | YES | YES | No | 0.71458 | 1029 | 2015-02-07 02:06 | 42042.0875 | F | Equipment failure | Insulator-line | COND | 10888 | NO-E | VD-2015-011 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-02-06 09:18 | 42041.3875 | YES | YES | No | 1900-01-03 02:23 | 5903 | 2015-02-10 11:41 | 42045.4868 | C | Tree | Tree failure | STRU | 11045 | NO-E | TM-2015-007 | 5753 | 5753 | 23442069 | 0.0010562 | 4.304 | 4074.7556 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-02-06 11:55 | 42041.4965 | YES | YES | No | 1899-12-31 12:53 | 2213 | 2015-02-08 00:48 | 42043.0333 | F | Tree | Tree failure | COND | 10886 | NO-E | TM-2015-011 | 3369 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-02-06 12:34 | 42041.5236 | YES | YES | No | 0.51528 | 742 | 2015-02-07 00:56 | 42042.0389 | F | Tree | Tree failure | COND | 10885 | NO-E | TM-2015-013 | 1655 | 1655 | 1913907 | 0.00030386 | 0.35139 | 1156.4393 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-02-06 16:06 | 42041.6708 | YES | YES | No | 1899-12-31 05:41 | 1781 | 2015-02-07 21:47 | 42042.9076 | F | Tree | Tree failure | COND | 10878 | NO-W | FU-2015-007 | 2163 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2015 | 2015-02-06 21:55 | 42041.9132 | YES | YES | No | 0.39375 | 567 | 2015-02-07 07:22 | 42042.3069 | F | Tree | Tree failure | COND | 10879 | NO-W | FU-2015-008 | 7502 | 7502 | 4253634 | 0.0013774 | 0.78097 | 567 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-02-07 11:18 | 42042.4708 | YES | YES | No | 0.50069 | 721 | 2015-02-07 23:19 | 42042.9715 | F | Equipment failure | Connector/ hardware | STRU | 10883 | NO-E | TM-2015-019 | 2798 | 1230 | TBD | TBD | TBD | TBD | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-02-08 21:00 | 42043.875 | YES | YES | No | 0.50694 | 730 | 2015-02-09 09:10 | 42044.3819 | F | Tree | Tree failure | COND | 10909 | NO-W | FU-2015-016 | 2163 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2015 | 2015-02-08 21:18 | 42043.8875 | YES | YES | No | 1899-12-31 19:36 | 2616 | 2015-02-10 16:54 | 42045.7042 | F | Tree | Tree failure | COND | 10901 | NO-W | FU-2015-013 | 6971 | 6971 | 8623205 | 0.0012799 | 1.5832 | 1237.0112 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2015 | 2015-02-08 22:51 | 42043.9521 | YES | YES | No | 0.87778 | 1264 | 2015-02-09 19:55 | 42044.8299 | F | Equipment failure | Structure-line | COND | 10903 | CV-N | TE-2015-008 | 1 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-02-09 14:24 | 42044.6 | No | YES | No | 0.44306 | 638 | 2015-02-10 01:02 | 42045.0431 | F | Tree | Tree failure | COND | 10910 | NO-W | FU-2015-018 | 5788 | 5788 | 4281786 | 0.0010627 | 0.78614 | 739.7695 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2015 | 2015-02-10 04:02 | 42045.1681 | No | YES | No | 0.62431 | 899 | 2015-02-10 19:01 | 42045.7924 | F | Equipment failure | Insulator-line | RELY | 10902 | CV-S | MD-2015-004 | 4 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-02-15 17:37 | 42050.734 | No | YES | No | 1899-12-31 07:58 | 1918 | 2015-02-17 01:35 | 42052.066 | F | Tree | Tree failure | COND | 10927 | NO-E | TM-2015-021 | 2745 | 2745 | 242141 | 0.00050398 | 0.044457 | 88.2117 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-02-23 07:19 | 42058.3049 | No | YES | No | 0.45833 | 660 | 2015-02-23 18:19 | 42058.7632 | F | Tree | Tree failure | COND | 10926 | NO-W | HM-2015-006 | 1126 | 1126 | 115978 | 0.00020673 | 0.021294 | 103 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2015 | 2015-02-28 06:13 | 42063.259 | No | YES | No | 0.61458 | 885 | 2015-02-28 20:58 | 42063.8736 | F | External contact | Foreign object | COND | 10941 | NO-E | VD-2015-018 | 4111 | 4111 | 408928 | 0.00075478 | 0.075079 | 99.4717 | 5446629 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2015 | 2015-03-07 09:11 | 42070.3826 | No | YES | No | 0.36181 | 521 | 2015-03-07 17:52 | 42070.7444 | F | Equipment failure | Conductor | COND | 10969 | CC-S | DW-2015-005 | 42 | 42 | 10332 | 7.7112e-06 | 0.001897 | 246 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-03-14 05:26 | 42077.2264 | No | YES | No | 0.34514 | 497 | 2015-03-14 13:43 | 42077.5715 | F | Tree | Tree failure | STRU | 10974 | NO-E | TM-2015-024 | 2746 | 2746 | 267499 | 0.00050417 | 0.049113 | 97.4141 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2015 | 2015-03-29 10:28 | 42092.4361 | No | YES | No | 0.42083 | 606 | 2015-03-29 20:34 | 42092.8569 | F | Tree | Tree failure | COND | 11017 | NO-E | VD-2015-022 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-03-30 08:28 | 42093.3528 | No | YES | No | 0.88333 | 1272 | 2015-03-31 05:40 | 42094.2361 | F | External contact | Car pole | CB | 11014 | CV-N | TE-2015-012 | 4234 | 2022 | TBD | TBD | TBD | TBD | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-04-07 16:38 | 42101.6931 | No | YES | No | 0.47917 | 690 | 2015-04-08 04:08 | 42102.1722 | F | Equipment failure | Structure-line | COND | 11063 | CV-S | MD-2015-017 | 619 | 619 | 22346 | 0.00011365 | 0.0041027 | 36.1002 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2015 | 2015-04-12 09:31 | 42106.3965 | No | YES | No | 0.44514 | 641 | 2015-04-12 20:12 | 42106.8417 | F | Equipment failure | Conductor | COND | 11037 | CV-S | FR-2015-017 | 338 | 338 | 3718 | 6.2057e-05 | 0.00068262 | 11 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-04-21 12:39 | 42115.5271 | No | YES | No | 0.35069 | 505 | 2015-04-21 21:04 | 42115.8778 | F | Equipment failure | Connector/ hardware | COND | 11061 | CV-N | TE-2015-021 | 1593 | 1593 | 184381 | 0.00029247 | 0.033852 | 115.7445 | 5446629 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-05-07 03:25 | 42131.1424 | No | YES | No | 0.27431 | 395 | 2015-05-07 10:00 | 42131.4167 | F | Equipment failure | Connector/ hardware | COND | 11098 | NO-E | TM-2015-041 | 908 | 908 | 366832 | 0.00016671 | 0.06735 | 404 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-05-07 23:50 | 42131.9931 | No | YES | No | 0.51736 | 745 | 2015-05-08 12:15 | 42132.5104 | F | Equipment failure | Conductor | STRU | 11101 | CV-S | MD-2015-022 | 153 | 153 | 14841 | 2.8091e-05 | 0.0027248 | 97 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2015 | 2015-05-27 21:34 | 42151.8986 | No | YES | No | 0.76597 | 1103 | 2015-05-28 15:57 | 42152.6646 | F | External contact | Car pole | STRU | 11147 | CV-S | MD-2015-0427 | 615 | 615 | 36900 | 0.00011291 | 0.0067748 | 60 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2015 | 2015-06-05 19:38 | 42160.8181 | No | YES | No | 0.93056 | 1340 | 2015-06-06 17:58 | 42161.2486 | F | Weather | Lightning | COND | 11176 | NO-E | VD-2015-057 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-06-18 20:48 | 42173.8667 | No | YES | No | 1900-01-01 19:42 | 4062 | 2015-06-21 16:30 | 42176.6875 | F | Disaster | Fire | STRU | 11198 | NO-E | FR-2015-034 | 2907 | 2907 | 537088 | 0.00053372 | 0.098609 | 184.7568 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-07-05 12:28 | 42190.5194 | No | YES | No | 0.68333 | 984 | 2015-07-06 04:52 | 42191.2028 | F | External contact | Car pole | COND | 11233 | CV-S | FR-2015-043 | 1913 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 115 | 115 | 2015 | 2015-07-29 21:52 | 42214.9111 | No | YES | No | 1900-01-05 03:33 | 8853 | 2015-08-05 01:25 | 42221.059 | C | Disaster | Fire | COND | NONE | NO-W | FU-2015-037 | 1 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 70 | 2015 | 2015-08-01 05:27 | 42217.2271 | No | YES | No | 0.70139 | 1010 | 2015-08-01 22:17 | 42217.9285 | F | Disaster | Fire | STRU | 11314 | CV-N | LB-2015-025 | 1 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-08-02 08:08 | 42218.3389 | No | YES | No | 0.48542 | 699 | 2015-08-02 19:47 | 42218.8243 | F | Animal | Bird | COND | 11315 | CV-N | LB-2015-027 | 2321 | 2321 | 1072946 | 0.00042614 | 0.19699 | 462.2775 | 5446629 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2015 | 2015-08-14 06:39 | 42230.2771 | No | YES | No | 0.48403 | 697 | 2015-08-14 18:16 | 42230.7611 | F | External contact | Foreign object | COND | 11403 | BA | NE-2015-1028 | 2 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2015 | 2015-08-21 16:58 | 42237.7069 | No | YES | No | 1900-01-06 01:45 | 10185 | 2015-08-28 18:43 | 42244.7799 | C | Disaster | Fire | ENCR | 11445 | CV-S | FR-2015-077 | 25 | 25 | 188125 | 4.59e-06 | 0.03454 | 7525 | 5446629 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2015 | 2015-08-27 08:16 | 42243.3444 | No | YES | No | 0.48542 | 699 | 2015-08-27 19:55 | 42243.8299 | F | External contact | Foreign object | COND | 11457 | CV-N | TE-2015-050 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-08-28 03:14 | 42244.1347 | No | YES | No | 0.55556 | 800 | 2015-08-28 16:34 | 42244.6903 | F | External contact | Car pole | COND | 11448 | CV-S | FR-2015-079 | 2993 | 2993 | 122314 | 0.00054951 | 0.022457 | 40.8667 | 5446629 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2015 | 2015-08-28 21:29 | 42244.8951 | No | YES | No | 1899-12-31 01:35 | 1535 | 2015-08-29 23:04 | 42245.9611 | F | External contact | Foreign object | STRU | 11443 | BA | SA-2015-010 | 7746 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-08-31 16:59 | 42247.7076 | No | YES | No | 0.38889 | 560 | 2015-09-01 02:19 | 42248.0965 | F | External contact | Foreign object | GUYS | 11451 | CV-S | FR-2015-080 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-09-09 17:43 | 42256.7382 | No | YES | No | 1900-01-06 23:55 | 11515 | 2015-09-17 17:38 | 42264.7347 | C | Disaster | Fire | ENCR | 11580 | CV-N | TE-2015-053 | 14255 | 14255 | 118581 | 0.0026172 | 0.021771 | 8.3186 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-09-10 09:09 | 42257.3812 | No | YES | No | 0.53958 | 777 | 2015-09-10 22:06 | 42257.9208 | F | Tree | Tree failure | COND | 11486 | NO-W | HM-2015-0295 | 1979 | 441 | 249684 | 8.0968e-05 | 0.045842 | 566.1769 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2015 | 2015-09-10 16:11 | 42257.6743 | No | YES | No | 0.42222 | 608 | 2015-09-11 02:19 | 42258.0965 | F | Work Procedure Error | Not following prescribed procedures | COND | 11483 | NO-W | RM-2015-062a | 7930 | 7930 | 1133371 | 0.0014559 | 0.20809 | 142.9219 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2015 | 2015-09-24 04:30 | 42271.1875 | No | YES | No | 0.375 | 540 | 2015-09-24 13:30 | 42271.5625 | F | Equipment failure | Connector/ hardware | COND | NONE | NO-W | FU-2015-057 | 3944 | 230 | 22680 | 4.2228e-05 | 0.004164 | 98.6087 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-10-01 13:37 | 42278.5674 | No | YES | No | 0.53819 | 775 | 2015-10-02 02:32 | 42279.1056 | F | Contamination | Environmental | COND | 11556 | CV-N | LB-2015-040 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2015 | 2015-10-10 07:55 | 42287.3299 | No | YES | No | 0.14722 | 212 | 2015-10-10 11:27 | 42287.4771 | F | Equipment failure | Switch-line | COND | 11575 | BA | ME-2015-018 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2015 | 2015-10-18 07:00 | 42295.2917 | No | YES | No | 1900-01-04 11:24 | 7884 | 2015-10-23 18:24 | 42300.7667 | C | Equipment failure | Structure-line | COND | 11614 | CC-N | ML-2015-031a | 66007 | 55636 | 36053905 | 0.010215 | 6.6195 | 648.0319 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2015 | 2015-10-22 21:56 | 42299.9139 | No | YES | No | 0.74931 | 1079 | 2015-10-23 15:55 | 42300.6632 | F | Equipment failure | Conductor | COND | 11612 | CV-S | FR-2015-097b | 483 | 483 | 83178 | 8.8679e-05 | 0.015271 | 172.2112 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-10-23 07:01 | 42300.2924 | No | YES | No | 0.22639 | 326 | 2015-10-23 12:27 | 42300.5188 | F | Equipment failure | Connector/ hardware | COND | 11615 | CV-N | TE-2015-1527 | 525 | 525 | 95467 | 9.639e-05 | 0.017528 | 181.8419 | 5446629 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-10-26 07:08 | 42303.2972 | No | YES | No | 0.44444 | 640 | 2015-10-26 17:48 | 42303.7417 | F | Contamination | Animal waste | INSL | 11616 | CV-N | LB-2015-043 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-10-31 14:02 | 42308.5847 | No | YES | No | 0.18819 | 271 | 2015-10-31 18:33 | 42308.7729 | F | Equipment failure | Insulator-line | COND | NONE | NO-E | VD-2015-090 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2015 | 2015-11-02 16:26 | 42310.6847 | No | YES | No | 0.80069 | 1153 | 2015-11-03 11:39 | 42311.4854 | F | Equipment failure | Structure-line | COND | 11657 | NO-E | TM-2015-076 | 7585 | 7585 | 964264 | 0.0013926 | 0.17704 | 127.1278 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-11-18 22:18 | 42326.9292 | No | YES | No | 0.91319 | 1315 | 2015-11-19 20:13 | 42327.8424 | F | External contact | Vandalism | COND | NONE | CV-N | TE-2015-063 | 2 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2015 | 2015-11-22 06:45 | 42330.2812 | No | YES | No | 0.58889 | 848 | 2015-11-22 20:53 | 42330.8701 | F | Equipment failure | Conductor | COND | 11737 | CV-N | TE-2015-065 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-11-28 20:45 | 42336.8646 | No | YES | No | 0.26736 | 385 | 2015-11-29 03:10 | 42337.1319 | F | Equipment failure | Conductor | COND | 11719 | CV-N | TE-2015-067 | 525 | 525 | 48300 | 9.639e-05 | 0.0088679 | 92 | 5446629 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2015 | 2015-12-08 10:23 | 42346.4326 | No | YES | No | 0.78611 | 1132 | 2015-12-09 05:15 | 42347.2188 | F | Equipment failure | Conductor | COND | 11733 | CC-S | DW-2015-029 | 80 | 80 | 70184 | 1.4688e-05 | 0.012886 | 877.3 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2015 | 2015-12-10 06:01 | 42348.2507 | No | YES | No | 0.23056 | 332 | 2015-12-10 11:33 | 42348.4812 | F | Tree | Tree failure | COND | 11744 | NO-E | TM-2015-085 | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2015 | 2015-12-13 02:25 | 42351.1007 | YES | YES | No | 0.61319 | 883 | 2015-12-13 17:08 | 42351.7139 | F | External contact | Car pole | COND | 11746 | CV-N | TE-2015-068a | 4323 | 4323 | 581699 | 0.0007937 | 0.1068 | 134.5591 | 5446629 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2015 | 2015-12-13 03:54 | 42351.1625 | YES | YES | No | 0.44167 | 636 | 2015-12-13 14:30 | 42351.6042 | F | Equipment failure | Conductor | COND | 11743 | CV-S | FR-2015-108a | 0 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-12-13 04:48 | 42351.2 | YES | YES | No | 0.69722 | 1004 | 2015-12-13 21:32 | 42351.8972 | F | Tree | Tree failure | COND | 11748 | NO-E | RM-2015-075 | 976 | 976 | 124626 | 0.00017919 | 0.022881 | 127.6906 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-12-13 05:26 | 42351.2264 | YES | YES | No | 1899-12-31 14:29 | 2309 | 2015-12-14 19:55 | 42352.8299 | F | Tree | Tree failure | COND | 11757 | NO-W | HM-2015-039 | 1234 | 373 | 80941 | 6.8483e-05 | 0.014861 | 217 | 5446629 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2015 | 2015-12-13 17:22 | 42351.7236 | YES | YES | No | 0.49514 | 713 | 2015-12-14 05:15 | 42352.2188 | F | Tree | Tree failure | COND | 11745 | CC-S | ML-2015-036 | 4275 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2015 | 2015-12-15 08:27 | 42353.3521 | No | YES | No | 1899-12-31 00:05 | 1445 | 2015-12-16 08:32 | 42354.3556 | F | External contact | Car pole | COND | 11756 | BA | PS-2015-032 | 810 | 0 | 0 | 0 | 0 | 0 | 5446629 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2015 | 2015-12-22 01:07 | 42360.0465 | No | YES | No | 0.49028 | 706 | 2015-12-22 12:53 | 42360.5368 | F | External contact | Car pole | COND | 11766 | NO-E | TM-2015-088 | 4100 | 4100 | 315622 | 0.00075276 | 0.057948 | 76.981 | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2015 | 2015-12-24 23:09 | 42362.9646 | YES | YES | No | 1900-01-01 03:24 | 3084 | 2015-12-27 02:33 | 42365.1062 | F | Tree | Tree failure | COND | 11778 | NO-W | HM-2015-043 | 4422 | 1984 | TBD | TBD | TBD | TBD | 5446629 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2016 | 2016-01-09 08:32 | 42378.3556 | No | YES | No | 0.78125 | 1125 | 2016-01-10 03:17 | 42379.1368 | F | Tree | Tree failure | STRU | 11807 | NO-W | RM-2016-002 | 887 | 887 | 61187 | 0.00016285 | 0.011234 | 68.982 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2016 | 2016-01-18 05:47 | 42387.241 | No | YES | No | 1899-12-31 08:57 | 1977 | 2016-01-19 14:44 | 42388.6139 | F | Tree | Tree failure | COND | 11807 | NO-E | VD-2016-003 | 2 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 60 | 2016 | 2016-01-19 07:54 | 42388.3292 | No | YES | No | 1900-01-02 01:08 | 4388 | 2016-01-22 09:02 | 42391.3764 | C | External contact | Foreign object | COND | 11838 | CV-N | TE-2016-002 | 4513 | 4513 | 469358 | 0.00082859 | 0.086174 | 104.0013 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2016 | 2016-01-19 11:00 | 42388.4583 | No | YES | No | 0.34931 | 503 | 2016-01-19 19:23 | 42388.8076 | F | Equipment failure | Connector/ hardware | COND | 11839 | CV-N | TE-2015-004 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-01-22 08:31 | 42391.3549 | No | YES | No | 0.43472 | 626 | 2016-01-22 18:57 | 42391.7896 | F | External contact | Car pole | COND | 11849 | NO-W | FU-2016-004 | 16587 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-02-01 11:22 | 42401.4736 | No | YES | No | 0.17569 | 253 | 2016-02-01 15:35 | 42401.6493 | F | Equipment failure | Conductor | COND | 11873 | CV-S | FR-2016-1322 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-02-14 19:34 | 42414.8153 | No | YES | No | 0.49028 | 706 | 2016-02-15 07:20 | 42415.3056 | F | External contact | Vandalism | COND | 11908 | NO-E | RM-2016-010 | 778 | 778 | 227822 | 0.00014284 | 0.041828 | 292.8303 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-02-17 11:32 | 42417.4806 | YES | YES | No | 0.72431 | 1043 | 2016-02-18 04:55 | 42418.2049 | F | Tree | Tree failure | COND | 11911 | NO-W | FU-2016-007 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-02-17 17:56 | 42417.7472 | YES | YES | No | 0.83056 | 1196 | 2016-02-18 13:52 | 42418.5778 | F | Tree | Tree failure | COND | 11913 | NO-W | FU-2016-008 | 3677 | 3677 | 330930 | 0.0006751 | 0.060759 | 90 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 60 | 2016 | 2016-02-24 20:17 | 42424.8451 | No | YES | No | 0.34931 | 503 | 2016-02-25 04:40 | 42425.1944 | F | Equipment failure | Conductor | COND | 11941 | CV-N | TE-2016-011 | 2122 | 1843 | 226111 | 0.00033837 | 0.041514 | 122.6864 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-02-29 02:57 | 42429.1229 | No | YES | No | 0.33472 | 482 | 2016-02-29 10:59 | 42429.4576 | F | Equipment failure | Connector/ hardware | COND | 11952 | NO-E | VD-2016-010 | 4865 | 4865 | 586213 | 0.00089321 | 0.10763 | 120.496 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2016 | 2016-03-01 01:44 | 42430.0722 | No | YES | No | 0.57986 | 835 | 2016-03-01 15:39 | 42430.6521 | F | Equipment failure | Conductor | COND | 11962 | CV-N | TE-2016-0338 | 5980 | 5980 | 295458 | 0.0010979 | 0.054246 | 49.4077 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 60 | 2016 | 2016-03-03 19:52 | 42432.8278 | No | YES | No | 0.53819 | 775 | 2016-03-04 08:47 | 42433.366 | F | External contact | Car pole | STRU | 11964 | CV-N | TE-2016-013a | 2546 | 2546 | 407002 | 0.00046745 | 0.074725 | 159.8594 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-03-05 21:49 | 42434.909 | YES | YES | No | 0.26458 | 381 | 2016-03-06 04:10 | 42435.1736 | F | Tree | Tree failure | COND | 11974 | NO-E | VD-2016-012c | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2016 | 2016-03-06 03:04 | 42435.1278 | No | YES | No | 0.79167 | 1140 | 2016-03-06 22:04 | 42435.9194 | F | Equipment failure | Structure-line | COND | 11978 | NO-E | VD-2016-013 | 1095 | 1095 | 133590 | 0.00020104 | 0.024527 | 122 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-03-06 12:13 | 42435.509 | No | YES | No | 0.44861 | 646 | 2016-03-06 22:59 | 42435.9576 | F | Tree | Tree failure | COND | 11970 | NO-W | HM-2016-008 | 1095 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-03-07 05:25 | 42436.2257 | No | YES | No | 0.62014 | 893 | 2016-03-07 20:18 | 42436.8458 | F | Equipment failure | Conductor | COND | 12021 | NO-E | TM-2016-017 | 2458 | 2458 | 146479 | 0.00045129 | 0.026894 | 59.5928 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-03-12 09:37 | 42441.4007 | No | YES | No | 0.54444 | 784 | 2016-03-12 22:41 | 42441.9451 | F | Tree | Tree failure | COND | 12000 | NO-W | FU-2016-018 | 2566 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-03-29 21:23 | 42458.891 | No | YES | No | 0.39514 | 569 | 2016-03-30 06:52 | 42459.2861 | F | Tree | Tree failure | COND | 12046 | NO-W | FU-2016-022 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-03-31 10:04 | 42460.4194 | No | YES | No | 0.46597 | 671 | 2016-03-31 21:15 | 42460.8854 | F | Equipment failure | Conductor | COND | 12053 | NO-E | RM-2016-018 | 327 | 327 | 27468 | 6.0037e-05 | 0.0050431 | 84 | 5481869 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2016 | 2016-04-07 05:08 | 42467.2139 | No | YES | No | 0.67639 | 974 | 2016-04-07 21:22 | 42467.8903 | F | Tree | Tree failure | COND | 12072 | CC-N | ML-2016-008 | 11662 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2016 | 2016-04-10 21:33 | 42470.8979 | No | YES | No | 0.83819 | 1207 | 2016-04-11 17:40 | 42471.7361 | F | Equipment failure | Conductor | STRU | 12086 | CV-N | TE-2016-020 | 1 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-04-24 23:44 | 42484.9889 | No | YES | No | 0.65764 | 947 | 2016-04-25 15:31 | 42485.6465 | F | External contact | Car pole | COND | 12129 | CV-S | FR-2016-022 | 2606 | 2606 | 181808 | 0.00047846 | 0.03338 | 69.7652 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-04-25 12:19 | 42485.5132 | No | YES | No | 0.19931 | 287 | 2016-04-25 17:06 | 42485.7125 | F | Tree | Tree failure | COND | 12130 | NO-E | VD-2016-1109 | 1 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-05-05 19:17 | 42495.8035 | No | YES | No | 0.9125 | 1314 | 2016-05-06 17:11 | 42496.716 | F | Weather | Lightning | COND | 12162 | CV-N | FR-2016-027a | 269 | 269 | 62320 | 4.9388e-05 | 0.011442 | 231.6729 | 5481869 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2016 | 2016-05-06 17:36 | 42496.7333 | No | YES | No | 1899-12-31 03:09 | 1629 | 2016-05-07 20:45 | 42497.8646 | F | Weather | Lightning | STRU | 12163 | CV-S | MD-2016-0641 | 1532 | 1532 | 1019103 | 0.00028127 | 0.18711 | 665.2108 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-05-24 10:18 | 42514.4292 | No | YES | No | 0.39306 | 566 | 2016-05-24 19:44 | 42514.8222 | F | Tree | Tree-3rd party | COND | 12194 | NO-E | TM-2016-030 | 2794 | 1224 | 524454 | 0.00022473 | 0.09629 | 428.4755 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-06-07 16:03 | 42528.6687 | No | YES | No | 0.89514 | 1289 | 2016-06-08 13:32 | 42529.5639 | F | Equipment failure | Conductor | COND | 12236 | CV-N | LB-2016-015 | 2 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2016 | 2016-06-10 14:58 | 42531.6236 | No | YES | No | 0.30069 | 433 | 2016-06-10 22:11 | 42531.9243 | F | Equipment failure | Connector/ hardware | COND | 12246 | CV-N | LB-2016-016 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2016 | 2016-07-01 04:00 | 42552.1667 | No | YES | No | 0.40694 | 586 | 2016-07-01 13:46 | 42552.5736 | F | Equipment failure | Conductor | COND | 12286 | CV-S | MD-2016-031a | 1157 | 4760 | 477224 | 0.00087394 | 0.087618 | 100.2571 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-07-06 08:03 | 42557.3354 | No | YES | No | 0.53403 | 769 | 2016-07-06 20:52 | 42557.8694 | F | Tree | Tree-3rd party | COND | 12297 | NO-W | FU-2016-044 | 909 | 909 | 24102 | 0.00016689 | 0.0044251 | 26.5149 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-07-21 08:26 | 42572.3514 | No | YES | No | 0.2875 | 414 | 2016-07-21 15:20 | 42572.6389 | F | External contact | Aircraft | COND | 12335 | CV-S | FR-2016-052a | 2086 | 2086 | 115476 | 0.00038299 | 0.021201 | 55.3576 | 5481869 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2016 | 2016-07-23 19:08 | 42574.7972 | No | YES | No | 1900-01-16 21:29 | 25769 | 2016-08-10 16:37 | 42592.6924 | C | Disaster | Fire | STRU | 12390 | CC-S | ML-2016-021 | 1114 | 1114 | 274775 | 0.00020453 | 0.050449 | 246.6562 | 5481869 | NA | NA | AUTO | Single Mode
BAY AREA | NORTH | 115 | 115 | 2016 | 2016-07-24 16:28 | 42575.6861 | No | YES | No | 0.63958 | 921 | 2016-07-25 07:49 | 42576.3257 | F | Equipment failure | Conductor | COND | 12351 | NO-E | PS-2016-013 | 25199 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2016 | 2016-08-12 19:01 | 42594.7924 | No | YES | No | 1900-02-05 20:00 | 54480 | 2016-09-19 15:01 | 42632.6257 | C | Disaster | Fire | ENCR | 12416 | CC-S | ME-2016-008 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-08-27 06:34 | 42609.2736 | No | YES | No | 0.4125 | 594 | 2016-08-27 16:28 | 42609.6861 | F | Equipment failure | Conductor | COND | 12439 | CV-S | FR-2016-058 | 1039 | 1039 | 89157 | 0.00019076 | 0.016369 | 85.8104 | 5481869 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-09-15 09:48 | 42628.4083 | No | YES | No | 0.52847 | 761 | 2016-09-15 22:29 | 42628.9368 | F | External contact | Car pole | COND | 12496 | CV-S | INT-08533 | 284 | 284 | 34168 | 5.2142e-05 | 0.0062732 | 120.3099 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-10-01 04:07 | 42644.1715 | No | YES | No | 0.91458 | 1317 | 2016-10-02 02:04 | 42645.0861 | F | External contact | Vandalism | COND | 12538 | NO-W | INT-08597 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-10-05 07:34 | 42648.3153 | No | YES | No | 0.53125 | 765 | 2016-10-05 20:19 | 42648.8465 | F | External contact | Car pole | STRU | 12549 | NO-W | INT-08622a | 17131 | 13385 | 1473493 | 0.0024575 | 0.27053 | 110.0854 | 5481869 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2016 | 2016-10-11 23:16 | 42654.9694 | No | YES | No | 0.32639 | 470 | 2016-10-12 07:06 | 42655.2958 | F | External contact | Vandalism | COND | 12560 | NO-E | INT-08640a | 2634 | 2634 | 1274369 | 0.0004836 | 0.23397 | 483.8151 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-10-16 18:22 | 42659.7653 | No | YES | No | 1899-12-31 20:00 | 2640 | 2016-10-18 14:22 | 42661.5986 | F | Equipment failure | Structure-line | STRU | 12579 | CV-S | INT-08682a | 2984 | 1944 | 94744 | 0.00035692 | 0.017395 | 48.7366 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2016 | 2016-10-18 14:22 | 42661.5986 | No | YES | No | 0.33681 | 485 | 2016-10-18 22:27 | 42661.9354 | F | Equipment failure | Structure-line | STRU | 12580 | CV-S | INT-08682b | 2984 | 1944 | 77760 | 0.00035692 | 0.014277 | 40 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2016 | 2016-10-23 18:10 | 42666.7569 | No | YES | No | 0.95694 | 1378 | 2016-10-24 17:08 | 42666.7139 | F | Equipment failure | Conductor | COND | 12595 | CV-N | INT-08709 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2016 | 2016-10-29 12:43 | 42672.5299 | No | YES | No | 0.61597 | 887 | 2016-10-30 03:30 | 42673.1458 | F | External contact | Foreign object | COND | 12610 | BA | T16-015221c | 726 | 726 | 104544 | 0.00013329 | 0.019194 | 144 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2016 | 2016-11-20 08:11 | 42694.341 | No | YES | No | 0.60069 | 865 | 2016-11-20 22:36 | 42694.9417 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-08796 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2016 | 2016-12-07 23:44 | 42711.9889 | No | YES | No | 0.93542 | 1347 | 2016-12-08 22:11 | 42712.9243 | F | Tree | Tree failure | COND | NONE | NO-W | INT-08850 | 2572 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2016 | 2016-12-24 21:23 | 42728.891 | No | YES | No | 0.74375 | 1071 | 2016-12-25 15:14 | 42729.6347 | F | Equipment failure | Conductor | COND | NONE | CV-S | INT-08892 | 0 | 0 | 0 | 0 | 0 | 0 | 5481869 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-01-02 08:33 | 42737.3562 | No | YES | No | 0.43611 | 628 | 2017-01-02 19:01 | 42737.7924 | F | Tree | Tree failure | COND | NONE | NO-W | INT-08905 | 4495 | 2046 | 1291026 | 0.00037323 | 0.23551 | 631 | 5517212 | Mult | Mult | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-01-03 13:30 | 42738.5625 | YES | YES | No | 0.30139 | 434 | 2017-01-03 20:44 | 42738.8639 | F | Tree | Tree failure | COND | NONE | NO-E | T17-001640 | TBD | TBD | TBD | TBD | TBD | TBD | 5517212 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-01-04 00:19 | 42739.0132 | No | YES | No | 0.78958 | 1137 | 2017-01-04 19:16 | 42739.8028 | F | Tree | Tree failure | STRU | NONE | NO-E | INT-08924 | 2929 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 11/279 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-01-08 08:02 | 42743.3347 | YES | YES | No | 1899-12-31 09:01 | 1981 | 2017-01-09 17:03 | 42744.7104 | F | Tree | Tree failure | COND | NONE | NO-W | INT-08990b | 2557 | 2557 | 2557 | 0.00046645 | 0.00046645 | 1 | 5517212 | A-B-C | 014/002 | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2017 | 2017-01-08 11:23 | 42743.4743 | YES | YES | No | 0.80903 | 1165 | 2017-01-09 06:48 | 42744.2833 | F | Tree | Tree failure | COND | NONE | NO-W | INT-08985a | TBD | TBD | TBD | TBD | TBD | TBD | 5517212 | B-C | 023/001 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-01-08 21:29 | 42743.8951 | YES | YES | No | 0.61944 | 892 | 2017-01-09 12:21 | 42744.5146 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-08991 | 2491 | 2491 | 2491 | 0.00045441 | 0.00045441 | 1 | 5517212 | B-G | 008/150 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2017 | 2017-01-10 11:08 | 42745.4639 | YES | YES | No | 1900-01-03 07:59 | 6239 | 2017-01-14 19:07 | 42749.7965 | C | Tree | Tree failure | COND | NONE | NO-E | INT-09005 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 010/120 | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2017 | 2017-01-10 12:21 | 42745.5146 | YES | YES | No | 0.13819 | 199 | 2017-01-10 15:40 | 42745.6528 | F | External contact | Car pole | STRU | NONE | BA | INT-09016 | 14314 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 000/023 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-01-10 14:57 | 42745.6229 | YES | YES | No | 0.56111 | 808 | 2017-01-11 04:25 | 42746.184 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09011 | 2280 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 007/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2017 | 2017-01-10 19:28 | 42745.8111 | YES | YES | No | 1900-01-02 21:18 | 5598 | 2017-01-14 16:46 | 42749.6986 | C | Tree | Tree failure | STRU | NONE | NO-E | INT-08991 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 230 | 230 | 2017 | 2017-01-11 09:02 | 42746.3764 | YES | YES | No | 1900-01-05 10:53 | 9293 | 2017-01-17 19:55 | 42752.8299 | C | Tree | Tree failure | COND | NONE | NO-E | INT-09033a | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 000/009 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | 2017 | 2017-01-18 15:07 | 42753.6299 | YES | YES | No | 0.82014 | 1181 | 2017-01-19 10:48 | 42754.45 | F | Equipment failure | Conductor | COND | NONE | BA | INT-09056 | 9987 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 006/063 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2017 | 2017-01-18 16:41 | 42753.6951 | YES | YES | No | 0.33611 | 484 | 2017-01-19 00:45 | 42754.0312 | F | Tree | Tree failure | COND | NONE | CV-N | INT-09058 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 025/442 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2017 | 2017-01-18 19:07 | 42753.7965 | YES | YES | No | 0.47431 | 683 | 2017-01-19 06:30 | 42754.2708 | F | Tree | Tree failure | COND | NONE | CV-N | INT-09068 | 1337 | 1337 | 526161 | 0.00024389 | 0.095982 | 393.5385 | 5517212 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | 2017 | 2017-01-20 04:00 | 42755.1667 | YES | YES | No | 1899-12-31 10:55 | 2095 | 2017-01-21 14:55 | 42756.6215 | F | Equipment failure | Structure-line | COND | NONE | BA | INT-09089 | 15017 | 15017 | 1899041 | 0.0027394 | 0.34642 | 126.4594 | 5517212 | A-B-C | 003/009 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-01-21 05:00 | 42756.2083 | YES | YES | No | 1900-01-01 16:43 | 3883 | 2017-01-23 21:43 | 42758.9049 | F | Tree | Tree failure | COND | NONE | NO-E | INT-09110b | 6754 | 6754 | 910847 | 0.0012321 | 0.16616 | 134.8604 | 5517212 | A-C | 015/401 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2017 | 2017-01-22 04:11 | 42758.1743 | YES | YES | No | 1899-12-31 10:26 | 2066 | 2017-01-23 14:37 | 42758.609 | F | Tree | Tree failure | COND | NONE | CC-S | INT-09128 | 3212 | 3212 | 206632 | 0.00058593 | 0.037694 | 64.3313 | 5517212 | A-B-G | 004/057 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-02 02:40 | 42768.1111 | No | YES | No | 0.35556 | 512 | 2017-02-02 11:12 | 42768.4667 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09198 | 3970 | 229 | 89608 | 4.1774e-05 | 0.016346 | 391.3013 | 5517212 | A-C-G | 043/009 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-05 22:31 | 42771.9382 | No | YES | No | 0.61458 | 885 | 2017-02-06 13:16 | 42772.5528 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09210 | 1484 | 1484 | 33018 | 0.00027071 | 0.0060231 | 22.2493 | 5517212 | B-C | 015/007 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-07 03:11 | 42773.1326 | YES | YES | No | 1899-12-31 18:11 | 2531 | 2017-02-08 21:22 | 42774.8903 | F | Tree | Tree failure | STRU | NONE | NO-W | INT-09227 | 1819 | 352 | TBD | 6.4212e-05 | 0 | 0 | 5517212 | B-C | 022/007 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-07 08:43 | 42773.3632 | YES | YES | No | 0.5625 | 810 | 2017-02-07 22:13 | 42773.9257 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09235 | 10770 | 10770 | 98224 | 0.0019521 | 0.017803 | 9.1201 | 5517212 | A-G | 023/003 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2017 | 2017-02-08 18:29 | 42774.7701 | No | YES | No | 1900-01-01 19:39 | 4057 | 2017-02-11 14:08 | 42777.5889 | F | Tree | Tree failure | COND | NONE | CV-N | INT-09240 | 2978 | 2978 | 202740 | 0.00053977 | 0.036747 | 68.0792 | 5517212 | A-B-C | 007/061 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-09 16:04 | 42775.6694 | YES | YES | No | 1900-01-01 03:52 | 3112 | 2017-02-11 19:56 | 42777.8306 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09254 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 031/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2017 | 2017-02-10 17:57 | 42776.7479 | No | YES | No | 1900-02-20 02:12 | 75012 | 2017-04-03 20:09 | 42828.8396 | C | Equipment failure | Structure-line | COND | NONE | NO-E | T17-004000 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | NA | NA | EFO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2017 | 2017-02-10 18:09 | 42776.7562 | No | YES | No | 1900-02-20 02:18 | 75018 | 2017-04-03 20:27 | 42828.8521 | C | Equipment failure | Structure-line | COND | NONE | NO-E | T17-004001 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2017 | 2017-02-13 00:35 | 42779.0243 | No | YES | No | 0.69861 | 1006 | 2017-02-13 17:21 | 42779.7229 | F | Equipment failure | Insulator-line | COND | NONE | CV-N | INT-09268 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 013/255 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2017 | 2017-02-15 22:57 | 42781.9563 | No | YES | No | 0.81389 | 1172 | 2017-02-16 18:29 | 42782.7701 | F | Equipment failure | Conductor | COND | NONE | CC-S | INT-09281 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-C | 003/006 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2017 | 2017-02-17 05:35 | 42783.2326 | YES | YES | No | 1900-01-01 12:23 | 3623 | 2017-02-19 17:58 | 42785.7486 | F | Tree | Tree failure | COND | NONE | CC-S | INT-09286 | 2 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 018/229 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2017 | 2017-02-17 08:55 | 42783.3715 | YES | YES | No | 1900-06-26 01:49 | 256429 | 2017-08-14 10:44 | 42961.4472 | C | Equipment failure | Structure-line | STRU | NONE | CV-N | INT-09291 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-G | A31/248 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2017 | 2017-02-17 10:00 | 42783.4167 | YES | YES | No | 0.56181 | 809 | 2017-02-17 23:29 | 42783.9785 | F | Equipment failure | Conductor | STRU | NONE | CV-N | INT-09293 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 007/002 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-02-17 11:10 | 42783.4653 | YES | YES | No | 1899-12-31 01:45 | 1545 | 2017-02-18 12:55 | 42784.5382 | F | Equipment failure | Structure-line | COND | NONE | CV-S | INT-09302 | 1052 | 942 | 1594806 | 0.00017074 | 0.28906 | 1693 | 5517212 | A-G | 020/191 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-17 12:23 | 42783.516 | YES | YES | No | 0.71597 | 1031 | 2017-02-18 05:34 | 42784.2319 | F | Equipment failure | Structure-line | COND | NONE | NO-W | INT-09307 | 907 | 907 | 8163 | 0.00016439 | 0.0014796 | 9 | 5517212 | A-C | 051/006 | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-02-17 15:04 | 42783.6278 | YES | YES | No | 0.97639 | 1406 | 2017-02-18 14:30 | 42784.6042 | F | Equipment failure | Structure-line | COND | NONE | CV-S | INT-09315 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | NA | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2017 | 2017-02-17 15:32 | 42783.6472 | YES | YES | No | 0.25556 | 368 | 2017-02-17 21:40 | 42783.9028 | F | Tree | Tree failure | COND | NONE | CV-N | INT-09316 | 9875 | 9875 | 1678468 | 0.0017899 | 0.30422 | 169.9714 | 5517212 | B-G | 020/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-02-18 16:19 | 42784.6799 | YES | YES | No | 0.99653 | 1435 | 2017-02-19 16:14 | 42785.6764 | F | External contact | Aircraft | COND | NONE | NO-E | INT-09326 | 932 | 932 | 1377496 | 0.00016893 | 0.24967 | 1478 | 5517212 | A-B-C | 001/032 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-02-19 23:49 | 42785.9924 | No | YES | No | 0.95694 | 1378 | 2017-02-20 22:47 | 42786.9493 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09331 | 4666 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 002/008 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2017 | 2017-02-20 22:55 | 42786.9549 | YES | YES | No | 1900-01-01 18:25 | 3985 | 2017-02-23 17:20 | 42789.7222 | F | Tree | Tree failure | COND | NONE | NO-E | INT-09343b | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 020/240 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-02-21 00:45 | 42787.0312 | YES | YES | No | 0.77292 | 1113 | 2017-02-21 19:18 | 42787.8042 | F | Tree | Tree failure | COND | NONE | NO-E | INT-09347 | 1877 | 1877 | 20734 | 0.00034021 | 0.0037581 | 11.0464 | 5517212 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-02-23 05:28 | 42789.2278 | No | YES | No | 0.36875 | 531 | 2017-02-23 14:19 | 42789.5965 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-S | INT-09361 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 007/093 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2017 | 2017-03-03 13:44 | 42797.5722 | No | YES | No | 0.23819 | 343 | 2017-03-03 19:27 | 42797.8104 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-S | INT-09392 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 015/248 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-03-06 04:34 | 42800.1903 | No | YES | No | 0.48194 | 694 | 2017-03-06 16:08 | 42800.6722 | F | Tree | Tree failure | COND | NONE | NO-W | INT-09398 | 2449 | 2023 | 1503089 | 0.00036667 | 0.27244 | 743 | 5517212 | C-G | 023/000 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-03-11 05:29 | 42805.2285 | No | YES | No | 0.5 | 720 | 2017-03-11 17:29 | 42805.7285 | F | External contact | Car pole | COND | NONE | CV-S | INT-09419 | 2002 | 2002 | 142142 | 0.00036286 | 0.025763 | 71 | 5517212 | A-B | 003/006 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-04-07 19:38 | 42832.8181 | YES | YES | No | 1899-12-31 13:55 | 2275 | 2017-04-09 09:33 | 42834.3979 | F | External contact | Car pole | STRU | NONE | CV-S | INT-09509 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 004/074 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-04-08 20:55 | 42833.8715 | No | YES | No | 0.65139 | 938 | 2017-04-09 12:33 | 42834.5229 | F | Equipment failure | Connector/ hardware | COND | NONE | NO-W | INT-09513 | 1485 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 006/012 | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2017 | 2017-04-13 12:01 | 42838.5007 | No | YES | No | 0.53958 | 777 | 2017-04-14 00:58 | 42839.0403 | F | External contact | Car pole | COND | 112869121 | BA | INT-09541 | 3742 | 3742 | 326220 | 0.00067824 | 0.059128 | 87.178 | 5517212 | A-B-C-G | 001/034 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-04-23 17:48 | 42848.7417 | No | YES | No | 0.60903 | 877 | 2017-04-24 08:25 | 42849.3507 | F | Tree | Tree failure | COND | 112791883 | NO-E | INT-09589 | 2 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-C | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-05-06 21:43 | 42861.9049 | No | YES | No | 0.89306 | 1286 | 2017-05-07 19:09 | 42862.7979 | F | Equipment failure | Conductor | STRU | 112844621 | CV-S | INT-09635a | 155 | 155 | 26660 | 2.8094e-05 | 0.0048322 | 172 | 5517212 | A-B-C | 003/323 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 230 | 230 | 2017 | 2017-05-11 06:39 | 42866.2771 | No | YES | No | 0.63472 | 914 | 2017-05-11 21:53 | 42866.9118 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | INT-09641 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-C-G | 063/266 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-05-11 19:49 | 42866.8257 | No | YES | No | 0.82708 | 1189 | 2017-05-12 15:40 | 42867.6528 | F | External contact | Vandalism | COND | 112864159 | CV-N | INT-09644 | 2526 | 2526 | 416217 | 0.00045784 | 0.07544 | 164.7732 | 5517212 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-05-25 16:52 | 42880.7028 | No | YES | No | 1899-12-31 05:47 | 1787 | 2017-05-26 22:39 | 42881.9437 | F | Tree | Tree failure | COND | 112909666 | NO-W | INT-09682 | 4112 | 2046 | 3662184 | 0.00037084 | 0.66377 | 1789.9238 | 5517212 | A-B-G | 023/002 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-05-30 07:45 | 42885.3229 | No | YES | No | 0.59861 | 862 | 2017-05-30 22:07 | 42885.9215 | F | Equipment failure | Structure-line | COND | 112917097 | NO-W | INT-09690 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-C | 054/002 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-06-22 08:30 | 42908.3542 | No | YES | No | 1899-12-31 17:58 | 2518 | 2017-06-24 02:28 | 42910.1028 | F | Work Procedure Error | Inattention | COND | 113021236 | NO-W | INT-09764 | 6877 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 009/000 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2017 | 2017-07-12 15:43 | 42928.6549 | No | YES | No | 1899-12-31 07:42 | 1902 | 2017-07-13 23:25 | 42929.9757 | F | Disaster | Fire | STRU | NONE | CV-N | INT-09832d | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | NA | NA | EFO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-07-18 07:18 | 42934.3042 | No | YES | No | 0.082639 | 119 | 2017-07-18 09:17 | 42934.3868 | F | Disaster | Fire | COND | NONE | CV-N | INT-09862b | TBD | TBD | TBD | TBD | TBD | TBD | 5517212 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-07-18 07:58 | 42934.3319 | No | YES | No | 0.41875 | 603 | 2017-07-18 18:01 | 42934.7507 | F | Tree | Tree failure | COND | 113061227 | NO-W | INT-09863 | 2200 | 2200 | 806570 | 0.00040132 | 0.14713 | 366.6227 | 5517212 | A-B-C-G | 005/011 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-07-18 13:49 | 42934.5757 | No | YES | No | 1900-01-06 00:51 | 10131 | 2017-07-25 14:40 | 42941.6111 | C | Disaster | Fire | STRU | NONE | CV-N | INT-09872a | TBD | TBD | TBD | TBD | TBD | TBD | 5517212 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-07-18 18:50 | 42934.7847 | No | YES | No | 0.56319 | 811 | 2017-07-19 08:21 | 42935.3479 | F | External contact | Car pole | COND | 113072185 | NO-E | INT-09874 | 611 | 611 | 60808 | 0.00011146 | 0.011093 | 99.5221 | 5517212 | A-B-C | 013/277 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2017 | 2017-07-18 21:40 | 42934.9028 | No | YES | No | 0.50486 | 727 | 2017-07-19 09:47 | 42935.4076 | F | Equipment failure | Connector/ hardware | COND | NONE | BA | INT-09875 | 16559 | 0 | 0 | 0 | 0 | 0 | 5517212 | NA | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-07-25 00:08 | 42941.0056 | No | YES | No | 1899-12-31 00:35 | 1475 | 2017-07-26 00:43 | 42942.0299 | F | Tree | Tree failure | STRU | NONE | NO-W | INT-09902 | 3807 | 3807 | 194157 | 0.00069002 | 0.035191 | 51 | 5517212 | A-B | 002/006 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-08-16 20:24 | 42963.85 | No | YES | No | 0.67778 | 976 | 2017-08-17 12:40 | 42964.5278 | F | Equipment failure | Connector/ hardware | COND | 113172616 | CV-S | INT-09987 | 713 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 000/008 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-08-24 22:31 | 42971.9382 | No | YES | No | 0.79236 | 1141 | 2017-08-25 17:32 | 42972.7306 | F | Disaster | Fire | STRU | 113197723 | CV-S | INT-10012 | 2988 | 2988 | 185256 | 0.00054158 | 0.033578 | 62 | 5517212 | A-B-G | 014/004 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-08-30 17:32 | 42977.7306 | No | YES | No | 1900-01-09 21:19 | 15679 | 2017-09-10 14:51 | 42988.6188 | F | Disaster | Fire | ENCR | NONE | NO-W | INT-10035 | 4 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-C | 012/002 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2017 | 2017-08-30 18:31 | 42977.7715 | No | YES | No | 1900-01-05 12:41 | 9401 | 2017-09-06 07:12 | 42984.3 | F | Disaster | Fire | ENCR | NONE | NO-W | INT-10037b | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-C | 056/005 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-09-03 17:42 | 42981.7375 | YES | YES | No | 1899-12-31 22:21 | 2781 | 2017-09-05 16:03 | 42983.6687 | F | Equipment failure | Structure-line | COND | 113216820 | CV-S | INT-10049 | 210 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 000/010 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2017 | 2017-09-03 20:56 | 42981.8722 | YES | YES | No | 0.52083 | 750 | 2017-09-04 09:26 | 42982.3931 | F | Equipment failure | Structure-line | COND | 113216695 | CV-S | INT-10050 | 1689 | 1689 | 207330 | 0.00030613 | 0.037579 | 122.7531 | 5517212 | A-C-G | 009/003 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2017 | 2017-09-11 17:42 | 42989.7375 | YES | YES | No | 1899-12-31 13:14 | 2234 | 2017-09-13 06:56 | 42991.2889 | F | Weather | Lightning | COND | NONE | CV-S | INT-10107 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 019/004 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-09-11 17:49 | 42989.7424 | YES | YES | No | 1899-12-31 05:39 | 1779 | 2017-09-12 23:28 | 42990.9778 | F | Tree | Tree failure | COND | NONE | CV-S | INT-10108 | 2010 | 2010 | 154770 | 0.00036431 | 0.028052 | 77 | 5517212 | A-B-C | 017/006 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-09-11 17:59 | 42989.7493 | YES | YES | No | 0.79097 | 1139 | 2017-09-12 12:58 | 42990.5403 | F | Tree | Tree failure | STRU | NONE | CV-S | INT-10109 | 4721 | 4721 | 640124 | 0.00085569 | 0.11602 | 135.5908 | 5517212 | A-G | 004/006 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-09-11 18:42 | 42989.7792 | YES | YES | No | 0.61806 | 890 | 2017-09-12 09:32 | 42990.3972 | F | Equipment failure | Structure-line | COND | NONE | CV-N | INT-10118 | 389 | 389 | 175523 | 7.0507e-05 | 0.031814 | 451.2159 | 5517212 | A-B-C | 001/006 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2017 | 2017-09-18 07:31 | 42996.3132 | No | YES | No | 1899-12-31 12:17 | 2177 | 2017-09-19 19:48 | 42997.825 | F | Equipment failure | Structure-line | COND | 113271531 | BA | T17-014063 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 005/122 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2017 | 2017-09-23 09:28 | 43001.3944 | No | YES | No | 0.6875 | 990 | 2017-09-24 01:58 | 43002.0819 | F | Equipment failure | Connector/ hardware | COND | 113594836 | CC-S | INT-10175 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 000/004 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2017 | 2017-09-24 02:13 | 43002.0924 | No | YES | No | 0.40208 | 579 | 2017-09-24 11:52 | 43002.4944 | F | Equipment failure | Conductor | COND | 113622459 | BA | INT-10181 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 013/256 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-09-25 07:26 | 43003.3097 | No | YES | No | 0.45764 | 659 | 2017-09-25 18:25 | 43003.7674 | F | External contact | Foreign object | COND | 113612610 | CV-N | INT-10184 | 389 | 389 | 59731 | 7.0507e-05 | 0.010826 | 153.5501 | 5517212 | A-B-C-G | 003/005 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2017 | 2017-09-25 19:35 | 43003.816 | No | YES | No | 1899-12-31 05:29 | 1769 | 2017-09-27 01:04 | 43005.0444 | F | Equipment failure | Insulator-line | COND | 113630089 | CC-S | INT-10186 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C-G | 058/249 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 230 | 230 | 2017 | 2017-09-30 15:08 | 43008.6306 | No | YES | No | 1899-12-31 08:30 | 1950 | 2017-10-01 23:38 | 43009.9847 | F | External contact | Vandalism | COND | 113642191 | CV-N | INT-10207 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 028/140 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-10-03 17:48 | 43011.7417 | No | YES | No | 0.58403 | 841 | 2017-10-04 07:49 | 43012.3257 | F | Equipment failure | Structure-line | COND | 113662597 | CV-N | INT-10211 | 206 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-G | 001/024 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-10-08 10:33 | 43016.4396 | YES | YES | No | 0.36806 | 530 | 2017-10-08 19:23 | 43016.8076 | F | Tree | Tree failure | COND | NONE | NO-E | INT-10224 | 1801 | 1801 | 191721 | 0.00032643 | 0.03475 | 106.4525 | 5517212 | A-C-G | C28/515 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-10-08 11:12 | 43016.4667 | YES | YES | No | 0.29861 | 430 | 2017-10-08 18:22 | 43016.7653 | F | External contact | Vandalism | COND | NONE | CV-S | INT-10225 | 2957 | 2957 | 62814 | 0.00053596 | 0.011385 | 21.2425 | 5517212 | B-G | 011/132 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-10-08 13:11 | 43016.5493 | YES | YES | No | 0.62083 | 894 | 2017-10-09 04:05 | 43017.1701 | F | Disaster | Fire | STRU | NONE | NO-E | INT-10228 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 010/261 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2017 | 2017-10-08 22:54 | 43016.9542 | YES | YES | No | 0.26944 | 388 | 2017-10-09 05:22 | 43017.2236 | F | Equipment failure | Conductor | COND | 113703301 | CV-S | INT-10231 | 389 | 389 | 66311 | 7.0507e-05 | 0.012019 | 170.4653 | 5517212 | NA | NA | EFO | Single Mode
NORTH COAST | CENTRAL | 230 | 230 | 2017 | 2017-10-08 23:15 | 43016.9688 | YES | YES | No | 1900-01-08 21:06 | 14226 | 2017-10-18 20:21 | 43026.8479 | C | Weather | Wind | UG | NONE | NO-W | INT-10237 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 005/022 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-10-08 23:33 | 43016.9812 | YES | YES | No | 1900-01-01 15:24 | 3804 | 2017-10-11 14:57 | 43019.6229 | F | Tree | Tree failure | COND | NONE | NO-W | INT-10235 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-C | 000/004 | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2017 | 2017-10-09 02:01 | 43017.084 | YES | YES | No | 1900-01-03 14:13 | 6613 | 2017-10-13 16:14 | 43021.6764 | C | Disaster | Fire | COND | NONE | NO-W | INT-10248 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | B-C | 030/009 | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2017 | 2017-10-12 07:40 | 43020.3194 | No | YES | No | 1900-01-04 09:08 | 7748 | 2017-10-17 16:48 | 43025.7 | C | Disaster | Fire | STRU | NONE | NO-W | T17-014835 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 003/001 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-10-20 09:06 | 43028.3792 | YES | YES | No | 0.82847 | 1193 | 2017-10-21 04:59 | 43029.2076 | F | Contamination | Animal waste | COND | 113754176 | CV-S | INT-10298 | 2986 | 2986 | 603172 | 0.00054122 | 0.10933 | 202 | 5517212 | A-B-C | 009/006 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-10-31 18:56 | 43039.7889 | No | YES | No | 0.71806 | 1034 | 2017-11-01 12:10 | 43040.5069 | F | External contact | Car pole | COND | 113782769 | NO-E | INT-10324 | 1672 | 1672 | 289611 | 0.00030305 | 0.052492 | 173.2123 | 5517212 | A-B-C | 009/208 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2017 | 2017-11-04 14:53 | 43043.6201 | No | YES | No | 0.91528 | 1318 | 2017-11-05 12:51 | 43044.5354 | F | External contact | Car pole | STRU | 113788380 | CV-S | INT-10347 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-B-C | 008/006 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 500 | 500 | 2017 | 2017-11-05 22:33 | 43044.9396 | No | YES | No | 1900-01-01 03:23 | 3083 | 2017-11-08 01:56 | 43047.0806 | F | Equipment failure | Structure-line | COND | 113797063 | NO-E | INT-10352 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | C-G | 032/134 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-11-06 13:58 | 43045.5819 | No | YES | No | 0.36389 | 524 | 2017-11-06 22:42 | 43045.9458 | F | External contact | Foreign object | COND | 113795814 | NO-W | INT-10354 | 1492 | 1492 | 200170 | 0.00027043 | 0.036281 | 134.1622 | 5517212 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-11-08 06:49 | 43047.284 | No | YES | No | 0.25833 | 372 | 2017-11-08 13:01 | 43047.5424 | F | External contact | Car pole | COND | 113794873 | CV-S | INT-10356 | 76 | 76 | 15010 | 1.3775e-05 | 0.0027206 | 197.5 | 5517212 | A-G | 048/002 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2017 | 2017-11-15 18:24 | 43054.7667 | No | YES | No | 0.36944 | 532 | 2017-11-16 03:16 | 43055.1361 | F | Tree | Tree failure | STRU | 113870843 | NO-E | INT-10376 | 0 | 0 | 0 | 0 | 0 | 0 | 5517212 | A-G | 006/004 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2017 | 2017-12-03 21:24 | 43072.8917 | No | YES | No | 1899-12-31 18:42 | 2562 | 2017-12-05 16:06 | 43074.6708 | F | Equipment failure | Connector/ hardware | COND | NONE | CV-N | INT-10416 | 1 | 0 | 0 | 0 | 0 | 0 | 5517212 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2017 | 2017-12-04 09:55 | 43073.4132 | YES | YES | No | 0.44375 | 639 | 2017-12-04 20:34 | 43073.8569 | F | Tree | Tree failure | COND | NONE | NO-E | INT-10418 | 2814 | 2814 | 1114149 | 0.00051004 | 0.20194 | 395.9307 | 5517212 | B-C-G | 007/202 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-12-14 06:51 | 43083.2854 | No | YES | No | 0.28819 | 415 | 2017-12-14 13:46 | 43083.5736 | F | External contact | Vandalism | COND | 114105882 | CV-S | INT-10453 | 8565 | 8565 | 761668 | 0.0015524 | 0.13805 | 88.928 | 5517212 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2017 | 2017-12-20 19:22 | 43089.8069 | No | YES | No | 0.29306 | 422 | 2017-12-21 02:24 | 43090.1 | F | Equipment failure | Conductor | COND | 114120620 | CV-N | INT-10474 | 470 | 470 | 85091 | 8.5188e-05 | 0.015423 | 181.0447 | 5517212 | C-G | 006/006 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2017 | 2017-12-22 08:45 | 43091.3646 | No | YES | No | 0.64653 | 931 | 2017-12-23 00:16 | 43092.0111 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-10480 | 891 | 891 | 42146 | 0.00016149 | 0.007639 | 47.3019 | 5517212 | C-G | 047/360 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2018 | 2018-01-05 17:53 | 43105.7451 | No | YES | No | 1899-12-31 02:04 | 1564 | 2018-01-06 19:57 | 43106.8313 | F | Equipment failure | Structure-line | STRU | 114176020 | CV-N | INT-10501 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 010/009 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2018 | 2018-01-09 19:29 | 43109.8118 | No | YES | No | 0.80417 | 1158 | 2018-01-10 14:47 | 43110.616 | F | Equipment failure | Structure-line | COND | 114196571 | CV-S | INT-10521 | 3210 | 3210 | 194273 | 0.00057849 | 0.035011 | 60.5212 | 5548929 | B-C | 004/057 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-01-26 09:55 | 43126.4132 | No | YES | No | 0.45208 | 651 | 2018-01-26 20:46 | 43126.8653 | F | Equipment failure | Connector/ hardware | ARRS | 114253569 | CV-S | INT-10627 | 390 | 390 | 52618 | 7.0284e-05 | 0.0094826 | 134.9179 | 5548929 | B-G | 004/006 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-02-14 22:39 | 43145.9437 | No | YES | No | 0.38403 | 553 | 2018-02-15 07:52 | 43146.3278 | F | Tree | Tree failure | COND | 114313507 | CV-N | INT-10660 | 3046 | 2140 | 25680 | 0.00038566 | 0.0046279 | 12 | 5548929 | A-C-G | 012/014 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-02-19 04:21 | 43150.1813 | No | YES | No | 0.29375 | 423 | 2018-02-19 11:24 | 43150.475 | F | Equipment failure | Conductor | COND | 114321893 | CV-S | INT-10672a | 687 | 46 | 12708 | 8.2899e-06 | 0.0022902 | 276.2609 | 5548929 | B-G | 019/325 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-02-19 06:10 | 43150.2569 | No | YES | No | 0.31111 | 448 | 2018-02-19 13:38 | 43150.5681 | F | Equipment failure | Conductor | COND | 114322909 | NO-E | INT-10675 | 4093 | 4093 | 525661 | 0.00073762 | 0.094732 | 128.4293 | 5548929 | C-G | 006/116 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-02-19 22:10 | 43150.9236 | No | YES | No | 0.38194 | 550 | 2018-02-20 07:20 | 43151.3056 | F | External contact | Vandalism | COND | 114322909 | NO-E | INT-10686 | 831 | 831 | 79034 | 0.00014976 | 0.014243 | 95.1071 | 5548929 | A-G | 012/274 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2018 | 2018-02-20 16:36 | 43151.6917 | No | YES | No | 0.59167 | 852 | 2018-02-21 06:48 | 43152.2833 | F | External contact | Car pole | STRU | 114364663 | CC-S | INT-10694 | 4465 | 4465 | 647486 | 0.00080466 | 0.11669 | 145.0137 | 5548929 | A-C | 001/024 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2018 | 2018-03-01 15:12 | 43160.6333 | No | YES | No | 0.48681 | 701 | 2018-03-02 02:53 | 43161.1201 | F | Equipment failure | Structure-line | COND | 114350292 | CV-N | INT-10736 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-C-G | 019/012 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2018 | 2018-03-03 08:24 | 43162.35 | No | YES | No | 1900-01-02 16:23 | 5303 | 2018-03-07 00:47 | 43166.0326 | C | Disaster | Disaster-other | COND | 114364243 | NO-E | INT-10742 | 5 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 036/002 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-03-18 08:23 | 43177.3493 | No | YES | No | 1899-12-31 12:25 | 2185 | 2018-03-19 20:48 | 43178.8667 | F | External contact | Aircraft | COND | 114466399 | NO-E | INT-10817 | 570 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-03-30 06:12 | 43189.2583 | No | YES | No | 0.41181 | 593 | 2018-03-30 16:05 | 43189.6701 | F | Equipment failure | Conductor | COND | 114459150 | CV-S | INT-10871 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 006/001 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-04-07 06:11 | 43197.2576 | No | YES | No | 0.37222 | 536 | 2018-04-07 15:07 | 43197.6299 | F | External contact | Car pole | STRU | 114481088 | CV-S | INT-10898 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 005/095 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 70 | 2018 | 2018-04-07 18:50 | 43197.7847 | No | YES | No | 1899-12-31 01:35 | 1535 | 2018-04-08 20:25 | 43198.8507 | F | Contamination | Animal waste | STRU | 114480878 | CV-S | INT-10901 | 2986 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C | 011/004 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2018 | 2018-04-07 20:33 | 43197.8562 | No | YES | No | 0.45208 | 651 | 2018-04-08 07:24 | 43198.3083 | F | External contact | Car pole | STRU | 114480699 | CV-N | INT-10902 | 2035 | 2035 | 131112 | 0.00036674 | 0.023628 | 64.4285 | 5548929 | A-C-G | 007/111 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2018 | 2018-05-17 01:11 | 43237.0493 | YES | YES | No | 0.97708 | 1407 | 2018-05-18 00:38 | 43238.0264 | F | External contact | Car pole | STRU | 114620982 | CV-S | INT-11011 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 005/045 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2018 | 2018-05-19 09:39 | 43239.4021 | No | YES | No | 0.47986 | 691 | 2018-05-19 21:10 | 43239.8819 | F | External contact | Aircraft | COND | 114620727 | NO-E | INT-11018 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 042/320 | AUTO | Dependent Mode Initiating
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-05-28 05:40 | 43248.2361 | No | YES | No | 0.54722 | 788 | 2018-05-28 18:48 | 43248.7833 | F | External contact | Car pole | STRU | 114638795 | CV-S | INT-11053 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-G | 001/017 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2018 | 2018-05-29 03:53 | 43249.1618 | No | YES | No | 0.55903 | 805 | 2018-05-29 17:18 | 43249.7208 | F | Tree | Tree failure | COND | 114695423 | NO-W | INT-11057 | 2581 | 2581 | 20648 | 0.00046513 | 0.0037211 | 8 | 5548929 | A-C | 004/006 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-06-04 10:24 | 43255.4333 | No | YES | No | 0.74792 | 1077 | 2018-06-05 04:21 | 43256.1813 | F | External contact | Car pole | COND | 114638795 | NO-E | INT-11070 | 2 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 015/267 | AUTO | Single Mode
NORTH COAST | CENTRAL | 230 | 230 | 2018 | 2018-06-05 12:44 | 43256.5306 | No | YES | No | 1899-12-31 05:32 | 1772 | 2018-06-06 18:16 | 43257.7611 | F | Disaster | Fire | COND | 114667730 | NO-W | INT-11075 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-C | 032/149 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2018 | 2018-06-30 08:04 | 43281.3361 | No | YES | No | 0.77083 | 1110 | 2018-07-01 02:34 | 43282.1069 | F | External contact | Car pole | STRU | 114743658 | CV-S | INT-11159 | 3 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 000/001 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2018 | 2018-07-03 05:18 | 43284.2208 | No | YES | No | 0.44306 | 638 | 2018-07-03 15:56 | 43284.6639 | F | External contact | Car pole | STRU | 114752239 | CV-S | INT-11175 | 1497 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-C-G | 003/096 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2018 | 2018-07-11 02:11 | 43292.091 | No | YES | No | 1899-12-31 01:23 | 1523 | 2018-07-12 03:34 | 43293.1486 | F | External contact | Car pole | STRU | 114788937 | CV-N | INT-11195 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C-G | 007/008 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-07-20 14:34 | 43301.6069 | No | YES | No | 0.21875 | 315 | 2018-07-20 19:49 | 43301.8257 | F | Equipment failure | Conductor | COND | 114811190 | CV-S | INT-11230 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-G | 018/296 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-07-23 13:45 | 43304.5729 | No | YES | YES | 1900-01-20 05:27 | 30567 | 2018-08-13 19:12 | 43325.8 | C | Disaster | Fire | STRU | 114869054 | NO-E | INT-11239 | 333 | 333 |  | 6.0012e-05 | 0 | 0 | 5548929 | B-C | 010/124 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2018 | 2018-07-23 13:52 | 43304.5778 | No | YES | YES | 1900-01-23 01:25 | 34645 | 2018-08-16 15:17 | 43328.6368 | C | Disaster | Fire | STRU | NONE | NO-E | INT-11240 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C | 026/189 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-07-26 19:23 | 43307.8076 | No | YES | YES | 1900-01-04 23:17 | 8597 | 2018-08-01 18:40 | 43313.7778 | C | Disaster | Fire | STRU | 114868952 | NO-E | INT-11252 | 2102 | 2102 | 136630 | 0.00037881 | 0.024623 | 65 | 5548929 | A-B-C-G | 009/168 | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2018 | 2018-07-27 17:37 | 43308.734 | No | YES | No | 1900-01-01 01:41 | 2981 | 2018-07-29 19:18 | 43310.8042 | F | Disaster | Fire | COND | NONE | NO-W | T18-012527 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | EFO | Emergency Forced
NORTH COAST | CENTRAL | 69 | 60 | 2018 | 2018-07-29 14:33 | 43310.6062 | YES | YES | YES | 1900-01-02 04:41 | 4601 | 2018-08-01 19:14 | 43313.8014 | C | Disaster | Fire | STRU | NONE | NO-W | INT-11257e | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Dependent Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2018 | 2018-09-07 09:33 | 43350.3979 | No | YES | No | 0.41806 | 602 | 2018-09-07 19:35 | 43350.816 | F | External contact | Foreign object | COND | NONE | CV-N | INT-11349 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-C | 070/441 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 230 | 230 | 2018 | 2018-09-14 11:38 | 43357.4847 | No | YES | No | 0.69583 | 1002 | 2018-09-15 04:20 | 43358.1806 | F | Tree | Tree-3rd party | COND | 114976640 | CV-S | INT-11369 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-G | 005/44A | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | 2018 | 2018-09-16 08:26 | 43359.3514 | No | YES | YES | 0.51528 | 742 | 2018-09-16 20:48 | 43359.8667 | F | External contact | Vandalism | COND | 114976811 | CC-S | INT-11371 | 286 | 285 | 29925 | 5.1361e-05 | 0.0053929 | 105 | 5548929 | A-G | 004/023 | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2018 | 2018-09-27 12:43 | 43370.5299 | No | YES | YES | 0.87153 | 1255 | 2018-09-28 09:38 | 43371.4014 | F | External contact | Aircraft | COND | 115007491 | NO-W | INT-11394 | 8331 | 8331 | 1488992 | 0.0015014 | 0.26834 | 178.7291 | 5548929 | A-B-C | 000/001 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-09-28 09:55 | 43371.4132 | No | YES | No | 0.32778 | 472 | 2018-09-28 17:47 | 43371.741 | F | External contact | Car pole | COND | 115011600 | CV-N | INT-11395 | 3332 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 023/009 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 500 | 500 | 2018 | 2018-10-02 05:14 | 43375.2181 | No | YES | No | 0.69028 | 994 | 2018-10-02 21:48 | 43375.9083 | F | Equipment failure | Insulator-line | COND | 115018206 | NO-E | INT-11411 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 000/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2018 | 2018-10-02 05:27 | 43375.2271 | No | YES | No | 0.64514 | 929 | 2018-10-02 20:56 | 43375.8722 | F | Equipment failure | Structure-line | COND | 115017817 | NO-E | INT-11412 | 3043 | 3043 | 139928 | 0.00054839 | 0.025217 | 45.9836 | 5548929 | C-A-G | 023/417 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2018 | 2018-10-03 17:19 | 43376.7215 | No | YES | No | 1899-12-31 06:54 | 1854 | 2018-10-05 00:13 | 43378.009 | F | Equipment failure | Switch-station | INSL | 115024347 | CC-S | INT-11436 | 3202 | 3202 | 549032 | 0.00057705 | 0.098944 | 171.4653 | 5548929 | C-G | 007/133 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2018 | 2018-10-11 22:18 | 43384.9292 | No | YES | No | 0.65625 | 945 | 2018-10-12 14:03 | 43385.5854 | F | Equipment failure | Conductor | COND | 115058337 | CC-S | INT-11456 | 336 | 336 | 71904 | 6.0552e-05 | 0.012958 | 214 | 5548929 | B-C-G | 023/141 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2018 | 2018-11-10 10:39 | 43414.4437 | No | YES | YES | 0.64306 | 926 | 2018-11-11 02:05 | 43415.0868 | F | Tree | Tree-3rd party | COND | 115339804 | NO-W | INT-11534 | 1110 | 1110 | 71040 | 0.00020004 | 0.012802 | 64 | 5548929 | A-B-G | 035/009 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2018 | 2018-11-11 06:29 | 43415.2701 | No | YES | No | 1899-12-31 09:49 | 2029 | 2018-11-12 16:18 | 43416.6792 | F | Tree | Tree failure | COND | 115341102 | NO-W | INT-11535 | 1996 | 1996 | 749021 | 0.00035971 | 0.13498 | 375.261 | 5548929 | A-B-C-G | 024/002 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2018 | 2018-12-06 17:27 | 43440.7271 | No | YES | No | 0.30903 | 445 | 2018-12-07 00:52 | 43441.0361 | F | Tree | Tree failure | COND | 115468006 | CC-S | INT-11610 | 2367 | 2367 | 42913 | 0.00042657 | 0.0077336 | 18.1297 | 5548929 | A-G | 011/142 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2018 | 2018-12-07 07:45 | 43441.3229 | No | YES | No | 0.35694 | 514 | 2018-12-07 16:19 | 43441.6799 | F | Equipment failure | Conductor | COND | 115476935 | CV-S | INT-11611 | 3 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-G | 004/070 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2018 | 2018-12-25 09:55 | 43459.4132 | No | YES | No | 0.56319 | 811 | 2018-12-25 23:26 | 43459.9764 | F | Equipment failure | Conductor | COND | 115596545 | NO-W | INT-11661 | 4 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 023/002 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-01-06 20:27 | 43106.8521 | YES | YES | No | 0.33056 | 476 | 2019-01-07 04:23 | 43107.1826 | F | Tree | Tree failure | COND | 115647759 | CV-N | INT-11697 | 1190 | 288 | 51840 | 5.1902e-05 | 0.0093423 | 180 | 5548929 | A-B-C-G | 012/002 | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2019 | 2019-01-08 00:44 | 43108.0306 | No | YES | No | 1900-01-01 16:24 | 3864 | 2019-01-10 17:08 | 43110.7139 | F | Equipment failure | Connector/ hardware | COND | 115675959 | CC-N | INT-11706 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C-G | 001/014 | AUTO | Single Mode
NORTH COAST | CENTRAL | 69 | 60 | 2019 | 2019-01-12 14:19 | 43112.5965 | No | YES | No | 0.97847 | 1409 | 2019-01-13 13:48 | 43113.575 | F | Tree | Tree failure | COND | 115685648 | NO-W | INT-11723 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 006/003 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-01-16 15:19 | 43116.6382 | YES | YES | No | 1900-01-01 01:49 | 2989 | 2019-01-18 17:08 | 43118.7139 | F | Tree | Tree failure | COND | 115709555 | NO-W | INT-11730 | 3651 | 385 | 256835 | 6.9383e-05 | 0.046286 | 667.1039 | 5548929 | A-B-C | 051/005 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-01-16 22:08 | 43116.9222 | YES | YES | No | 1899-12-31 22:29 | 2789 | 2019-01-18 20:37 | 43118.859 | F | Equipment failure | Conductor | COND | 115700436 | NO-E | INT-11748 | 2821 | 1675 | TBD | TBD | TBD | TBD | 5548929 | C-A | 017/463 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-01-20 10:02 | 43120.4181 | No | YES | No | 0.69306 | 998 | 2019-01-21 02:40 | 43121.1111 | F | Equipment failure | Conductor | COND | 115709645 | NO-E | INT-11762 | 1 | 1 | 998 | 6.9383e-05 | 0.046286 | 667.1039 | 5548929 | A-B-C-G | A07/171 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-01-29 16:48 | 43129.7 | No | YES | No | 0.46806 | 674 | 2019-01-30 04:02 | 43130.1681 | F | Tree | Tree failure | COND | 115763622 | NO-W | INT-11788 | 1995 | 357 | 242886 | 6.4337e-05 | 0.043772 | 680.3529 | 5548929 | C-G | 022/008 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2019 | 2019-01-31 21:33 | 43131.8979 | No | YES | No | 0.46111 | 664 | 2019-02-01 08:37 | 43132.359 | F | External contact | Vandalism | COND | NONE | NO-E | T19-004229 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | EFO | Emergency Forced
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2019 | 2019-02-02 03:07 | 43133.1299 | YES | YES | No | 0.97708 | 1407 | 2019-02-03 02:34 | 43134.1069 | F | Tree | Tree failure | COND | 115783166 | CC-S | INT-11795 | 4305 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C-G | 005/133 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2019 | 2019-02-05 07:28 | 43136.3111 | YES | YES | No | 0.51458 | 741 | 2019-02-05 19:49 | 43136.8257 | F | Equipment failure | Insulator-line | COND | NONE | CC-N | INT-11824 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 056/244 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-10 01:16 | 43141.0528 | YES | YES | No | 1900-01-09 16:06 | 15366 | 2019-02-20 17:22 | 43516.7236 | F | Tree | Tree failure | STRU | 116469858 | NO-W | INT-11848 | 4667 | 4667 | 4667 | 0.00084106 | 0.00084106 | 1 | 5548929 | A-C | 002/007 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2019 | 2019-02-10 04:32 | 43141.1889 | YES | YES | No | 1900-01-01 14:47 | 3767 | 2019-02-12 19:19 | 43143.8049 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-11851 | 7733 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C | 004/027 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-10 05:55 | 43141.2465 | YES | YES | No | 1899-12-31 15:19 | 2359 | 2019-02-11 21:14 | 43142.8847 | F | Weather | Snow/ ice | NONE | NONE | NO-W | INT-11855 | 1110 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-G | 032/005 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-10 10:17 | 43506.4285 | YES | YES | No | 0.69861 | 1006 | 2019-02-11 03:03 | 43507.1271 | F | External contact | Vandalism | STRU | 116469685 | NO-W | INT-11862 | 1953 | 1953 | 1299144 | 0.00035196 | 0.23413 | 665.2043 | 5548929 | A-C | 010/011 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-12 22:23 | 43508.9326 | YES | YES | No | 1899-12-31 12:43 | 2203 | 2019-02-14 11:06 | 43510.4625 | F | Weather | Rain | NONE | 116493510 | NO-W | INT-11871 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 008/007 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-12 22:36 | 43508.9417 | YES | YES | No | 1899-12-31 13:29 | 2249 | 2019-02-14 12:05 | 43510.5035 | F | Tree | Tree failure | COND | 116493581 | NO-W | INT-11872 | 2578 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 014/010 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-13 00:56 | 43509.0389 | YES | YES | No | 1900-01-01 15:45 | 3825 | 2019-02-15 16:41 | 43511.6951 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-11942 | 787 | 787 | 787 | 0.00014183 | 0.00014183 | 1 | 5548929 | C-G | 000/020 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-13 00:57 | 43509.0396 | YES | YES | No | 1900-01-01 22:07 | 4207 | 2019-02-15 23:04 | 43511.9611 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-11880 | 954 | 954 | 954 | 0.00017193 | 0.00017193 | 1 | 5548929 | C-G | 004/084 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-13 02:17 | 43509.0951 | YES | YES | No | 1900-01-03 15:49 | 6709 | 2019-02-17 18:06 | 43513.7542 | C | Equipment failure | Structure-line | STRU | 116486890 | NO-E | INT-11885b | 13703 | 13703 | 2017986 | 0.0024695 | 0.36367 | 147.266 | 5548929 | A-G | 013/058 | AUTO | Dependent Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-13 03:17 | 43509.1368 | YES | YES | No | 1900-01-01 16:52 | 3892 | 2019-02-15 20:09 | 43511.8396 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-11887 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-13 04:49 | 43509.2007 | YES | YES | No | 1899-12-31 12:55 | 2215 | 2019-02-14 17:44 | 43510.7389 | F | Weather | Snow/ ice | COND | NONE | NO-E | INT-11895 | TBD | TBD | TBD | TBD | TBD | TBD | 5548929 | A-G | 009/167 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-13 06:17 | 43509.2618 | YES | YES | No | 0.53611 | 772 | 2019-02-13 19:09 | 43509.7979 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-11896 | 12736 | 12736 | 2603106 | 0.0022952 | 0.46912 | 204.3896 | 5548929 | A-B-C-G | 000/008 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2019 | 2019-02-13 11:05 | 43509.4618 | YES | YES | No | 0.27778 | 400 | 2019-02-13 17:45 | 43509.7396 | F | Tree | Tree failure | COND | 116487886 | CC-S | T19-005009a | TBD | TBD | TBD | TBD | TBD | TBD | 5548929 | NA | NA | EFO | Emergency Forced Outage
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-02-13 11:56 | 43509.4972 | YES | YES | No | 0.58125 | 837 | 2019-02-14 01:53 | 43510.0785 | F | External contact | Car pole | COND | 116485893 | CV-N | INT-11912 | 3382 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 021/012 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2019 | 2019-02-13 23:59 | 43509.9993 | YES | YES | No | 1899-12-31 17:59 | 2519 | 2019-02-15 17:58 | 43511.7486 | F | Tree | Tree failure | COND | 116487886 | CC-N | INT-11923a | 12736 | 12736 | 2603106 | 0.0022952 | 0.46912 | 204.3896 | 5548929 | A-B-C | 014/111 | AUTO | Dependent Mode-initiating
SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | 2019 | 2019-02-14 00:52 | 43510.0361 | YES | YES | No | 1899-12-31 17:36 | 2496 | 2019-02-15 18:28 | 43511.7694 | F | Equipment failure | Conductor | STRU | NONE | BA | INT-11924 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 004/006 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2019 | 2019-02-16 05:15 | 43512.2188 | YES | YES | No | 0.78194 | 1126 | 2019-02-17 00:01 | 43513.0007 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-11954 | 12736 | 12736 | 2603106 | 0.0022952 | 0.46912 | 204.3896 | 5548929 | C-A-G | 000/004 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2019 | 2019-02-19 05:13 | 43515.2174 | No | YES | No | 0.40694 | 586 | 2019-02-19 14:59 | 43515.6243 | F | Equipment failure | Conductor | COND | 116501566 | CV-N | INT-11963 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-G | 006/013 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2019 | 2019-02-23 04:34 | 43519.1903 | No | YES | No | 0.05 | 72 | 2019-02-23 05:46 | 43519.2403 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-11975a | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-G | 001/000 | AUTO | Dependent Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2019 | 2019-02-23 13:12 | 43519.55 | No | YES | No | 1899-12-31 02:37 | 1597 | 2019-02-24 15:49 | 43520.659 | F | Tree | Tree-3rd party | STRU | 116591227 | CC-S | INT-11976a | 13704 | 13704 | 2017986 | 0.0024697 | 0.36367 | 147.2553 | 5548929 | A-G | 013/058 | AUTO | Common Mode-initiating
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-25 13:33 | 43521.5646 | No | YES | No | 0.96458 | 1389 | 2019-02-26 12:42 | 43522.5292 | F | Tree | Tree failure | COND | 116609080 | NO-W | INT-11984 | 2585 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-A | 004/011 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-26 08:44 | 43522.3639 | YES | YES | No |  |  |  |  | F | Equipment failure | Conductor | STRU | NONE | NO-E | INT-11997 | 2480 | 2480 | 107123 | 0.00044693 | 0.019305 | 43.1948 | 5548929 | B-C-G | 000/023 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-26 09:54 | 43522.4125 | YES | YES | No | 1900-01-03 05:01 | 6061 | 2019-03-02 14:55 | 43526.6215 | C | Equipment failure | Conductor | STRU | NONE | NO-E | INT-12001 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C | 000/010 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-02-26 17:14 | 43522.7181 | YES | YES | No | 0.90764 | 1307 | 2019-02-27 15:01 | 43523.6257 | F | Tree | Tree failure | COND | 116613537 | NO-W | INT-12005 | 2470 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 016/001 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-02-26 23:47 | 43522.991 | YES | YES | No | 0.67569 | 973 | 2019-02-27 16:00 | 43523.6667 | F | Other | Distribution caused | COND | NONE | NO-E | INT-12009 | 1658 | 1658 | 107123 | 0.0002988 | 0.019305 | 64.6098 | 5548929 | A-C | 012/250 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-03-01 20:13 | 43525.8424 | No | YES | No | 0.84792 | 1221 | 2019-03-02 16:34 | 43526.6903 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-12019 | 1847 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | :000/022 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-03-05 13:05 | 43529.5451 | No | YES | No | 1899-12-31 00:49 | 1489 | 2019-03-06 13:54 | 43530.5792 | F | Equipment failure | Structure-line | STRU | 116639062 | CV-N | INT-12028 | 155 | 155 | 11935 | 2.7933e-05 | 0.0021509 | 77 | 5548929 | C-G | 007/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-03-07 06:08 | 43531.2556 | No | YES | No | 0.40694 | 586 | 2019-03-07 15:54 | 43531.6625 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-12042 | 2 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-C-G | 011/238 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2019 | 2019-03-16 11:45 | 43540.4896 | No | YES | No | 0.43125 | 621 | 2019-03-16 22:06 | 43540.9208 | F | Equipment failure | Conductor | COND | 116757964 | CV-N | INT-12062 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 049/314 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-03-17 12:10 | 43541.5069 | No | YES | No | 0.47986 | 691 | 2019-03-17 23:41 | 43541.9868 | F | External contact | Vandalism | COND | 116753427 | CV-N | INT-12063 | 3127 | 3127 | 163413 | 0.00056353 | 0.029449 | 52.2587 | 5548929 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-04-02 05:03 | 43557.2104 | No | YES | No | 1900-01-01 13:52 | 3712 | 2019-04-04 18:55 | 43559.7882 | F | Equipment failure | Conductor | COND | 117003823 | NO-E | INT-12127 | 0 | 0 | 0 |  |  |  | 5548929 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-04-09 04:11 | 43564.1743 | No | YES | No | 0.4625 | 666 | 2019-04-09 15:17 | 43564.6368 | F | Equipment failure | Conductor | COND | 117001980 | NO-E | INT-12147 | 6572 | 6572 | 140537 | 0.0011844 | 0.025327 | 21.3842 | 5548929 | B-G | 002/035 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2019 | 2019-04-09 16:26 | 43564.6847 | No | YES | No | 1899-12-31 04:20 | 1700 | 2019-04-10 20:46 | 43565.8653 | F | Equipment failure | Structure-line | STRU | 116999777 | CV-N | INT-12148 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C-G | :011/008 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-04-19 09:15 | 43574.3854 | No | YES | No | 0.30347 | 437 | 2019-04-19 16:32 | 43574.6889 | F | External contact | Car pole | STRU | 117066897 | CV-S | INT-12172 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | A10/132 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2019 | 2019-04-23 05:03 | 43578.2104 | No | YES | No | 0.93542 | 1347 | 2019-04-24 03:30 | 43579.1458 | F | Other | Customer/ IPP caused | STRU | 117087971 | CV-N | T19-008746 | 7821 | 7821 | 3302354 | 0.0014095 | 0.59513 | 422.2419 | 5548929 | NA | NA | EFO | Emergency Forced Outage
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-05-10 14:52 | 43595.6194 | No | YES | No | 0.29306 | 422 | 2019-05-10 21:54 | 43595.9125 | F | Work Procedure Error | Not following prescribed procedures | COND | 117213454 | NO-E | INT-12233 | 323 | 323 | 3876 | 5.8209e-05 | 0.00069851 | 12 | 5548929 | A-C | 023/360 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-05-14 07:17 | 43599.3035 | No | YES | No | 0.50139 | 722 | 2019-05-14 19:19 | 43599.8049 | F | External contact | Car pole | COND | 117237527 | NO-E | INT-12245 | 1673 | 1673 | 23422 | 0.0003015 | 0.004221 | 14 | 5548929 | C-G | 022/447 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-05-15 19:28 | 43600.8111 | No | YES | No | 0.61111 | 880 | 2019-05-16 10:08 | 43601.4222 | F | Tree | Tree failure | COND | 117247425 | NO-W | INT-12253 | 3977 | 228 | 162386 | 4.1089e-05 | 0.029264 | 712.2193 | 5548929 | A-B-C | 044/001 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-05-26 21:57 | 43611.9146 | No | YES | No | 0.83333 | 1200 | 2019-05-27 17:57 | 43612.7479 | F | Contamination | Animal waste | STRU | 117328836 | CV-S | INT-12295 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 014/010 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-07-01 13:40 | 43647.5694 | No | YES | No | 0.56597 | 815 | 2019-07-02 03:15 | 43648.1354 | F | External contact | Car pole | STRU | 117549265 | NO-W | INT-12406 | 2146 | 2146 | 1067150 | 0.00038674 | 0.19232 | 497.274 | 5548929 | A-B-G | 005/011 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-07-24 14:05 | 43670.5868 | No | YES | No | 0.54722 | 788 | 2019-07-25 03:13 | 43671.134 | F | External contact | Foreign object | COND | 117638644 | NO-W | INT-12458 | 2208 | 2208 | 324576 | 0.00039791 | 0.058493 | 147 | 5548929 | C-G | 035/009 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-07-25 14:54 | 43671.6208 | No | YES | No | 0.47986 | 691 | 2019-07-26 02:25 | 43672.1007 | F | Work Procedure Error | Not following prescribed procedures | COND | 117644578 | NO-E | INT-12462 | 1657 | 1657 | 1152280 | 0.00029862 | 0.20766 | 695.4013 | 5548929 | C-A | 009/202 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2019 | 2019-08-02 04:51 | 43679.2021 | No | YES | No | 0.72986 | 1051 | 2019-08-02 22:22 | 43679.9319 | F | Contamination | Animal waste | COND | 117713012 | CV-N | INT-12479 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C-G | 050/309 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2019 | 2019-08-05 18:38 | 43682.7764 | No | YES | No | 0.58472 | 842 | 2019-08-06 08:40 | 43683.3611 | F | External contact | Car pole | STRU | NONE | CC-S | INT-12483 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C-G | 004/063 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2019 | 2019-08-19 18:17 | 43696.7618 | No | YES | YES | 0.46597 | 671 | 2019-08-20 05:28 | 43697.2278 | F | External contact | Car pole | STRU | 117762487 | CV-S | INT-12520 | 14854 | 14854 | 757554 | 0.0026769 | 0.13652 | 51 | 5548929 | B-G | 001/009 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-08-23 12:56 | 43700.5389 | No | YES | No | 0.36736 | 529 | 2019-08-23 21:45 | 43700.9062 | F | Other | Customer/ IPP caused | COND | 117786020 | CV-S | INT-12526 | 3329 | 3329 | 48282 | 0.00059994 | 0.0087011 | 14.5035 | 5548929 | B-C-G | 008/010 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2019 | 2019-08-23 21:22 | 43700.8903 | No | YES | YES | 1899-12-31 00:53 | 1493 | 2019-08-24 22:15 | 43701.9271 | F | External contact | Car pole | STRU | 117808085 | CV-S | INT-12528 | 5 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 005/100 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2019 | 2019-08-28 09:47 | 43705.4076 | No | YES | No | 0.37639 | 542 | 2019-08-28 18:49 | 43705.784 | F | External contact | Car pole | STRU | NONE | CV-N | INT-12543 | 240 | 240 | 23900 | 4.3252e-05 | 0.0043071 | 99.5833 | 5548929 | C-G | 004/067 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2019 | 2019-09-01 03:38 | 43709.1514 | No | YES | No | 0.7125 | 1026 | 2019-09-01 20:44 | 43709.8639 | F | External contact | Car pole | STRU | 117838346 | NO-W | INT-12545 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 001/009 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-09-15 19:20 | 43723.8056 | No | YES | No | 1899-12-31 02:26 | 1586 | 2019-09-16 21:46 | 43724.9069 | F | External contact | Vandalism | COND | 117888602 | NO-W | INT-12587 | 4 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 023/176 | AUTO | Single Mode
CENTRAL VALLEY | NORTH | 69 | 60 | 2019 | 2019-10-20 11:16 | 43758.4694 | No | YES | No | 0.39653 | 571 | 2019-10-20 20:47 | 43758.866 | F | Equipment failure | Conductor | COND | NONE | NO-E | T19-019219b | 2754 | 2754 | 334238 | 0.00049631 | 0.060235 | 121.3646 | 5548929 | NA | NA | EFO | Emergency Forced Outage
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-10-26 21:55 | 43764.9132 | YES | YES | No | 1899-12-31 18:09 | 2529 | 2019-10-28 16:04 | 43766.6694 | F | Other | Safety clearance | PSPS | NONE | NO-W | T19-019405 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | EFO | Emergency Forced Outage
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-10-27 00:48 | 43765.0333 | YES | YES | No | 0.7375 | 1062 | 2019-10-27 18:30 | 43765.7708 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-12871 | 2 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 004/086 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-10-27 19:30 | 43765.8125 | YES | YES | No | 1900-01-02 00:06 | 4326 | 2019-10-30 19:36 | 43768.8167 | C | Equipment failure | Conductor | COND | NONE | NO-W | T19-019775 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | EFO | Emergency Forced Outage
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-10-28 13:00 | 43766.5417 | YES | YES | No | 1899-12-31 22:41 | 2801 | 2019-10-30 11:41 | 43768.4868 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-12957 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-C-G | 002/059 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-10-28 16:36 | 43766.6917 | YES | YES | No | 0.29514 | 425 | 2019-10-28 23:41 | 43766.9868 | F | Tree | Tree failure | COND | NONE | NO-W | T19-019825 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | EFO | Emergency Forced Outage
BAY AREA | CENTRAL | 115 | 115 | 2019 | 2019-11-03 07:51 | 43772.3271 | No | YES | No | 1899-12-31 11:52 | 2152 | 2019-11-04 19:43 | 43773.8215 | F | Equipment failure | Conductor | COND | NONE | BA | INT-13018 | 2 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 006/038 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-11-26 13:16 | 43795.5528 | YES | YES | No | 1899-12-31 02:28 | 1588 | 2019-11-27 15:44 | 43796.6556 | F | Tree | Tree failure | COND | NONE | NO-W | INT-13076 | 8097 | 8097 | 80970 | 0.0014592 | 0.014592 | 10 | 5548929 | A-B-C-G | 006/007 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-11-26 13:47 | 43795.5743 | YES | YES | No | 1899-12-31 21:00 | 2700 | 2019-11-28 10:47 | 43797.4493 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-13080 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C-G | 007/012 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-11-26 13:50 | 43795.5764 | YES | YES | No | 1900-01-01 02:35 | 3035 | 2019-11-28 16:25 | 43797.684 | F | Tree | Tree failure | COND | NONE | NO-W | INT-13081-1 | 11635 | 1867 | 4898353 | 0.00033646 | 0.88276 | 2623.6492 | 5548929 | A-B-C | :001/008 | AUTO | Dependent Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-11-26 20:38 | 43795.8597 | YES | YES | No | 1899-12-31 23:15 | 2835 | 2019-11-28 19:53 | 43797.8285 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-13089 | 2724 | 1681 | 2555541 | 0.00030294 | 0.46055 | 1520.2504 | 5548929 | B-C-G | 006/176 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-11-26 21:53 | 43795.9118 | YES | YES | No | 0.58958 | 849 | 2019-11-27 12:02 | 43796.5014 | F | Tree | Tree failure | COND | NONE | NO-E | INT-13096 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Common Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-11-27 06:24 | 43796.2667 | YES | YES | No | 0.36875 | 531 | 2019-11-27 15:15 | 43796.6354 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-13109 | 6666 | 662 | 76130 | 0.0001193 | 0.01372 | 115 | 5548929 | B-G | 003/045 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2019 | 2019-11-30 19:09 | 43799.7979 | No | YES | No | 1900-01-01 00:08 | 2888 | 2019-12-02 19:17 | 43801.8035 | F | Equipment failure | Conductor | COND | NONE | CC-S | INT-13133 | 968 | 968 | 308536 | 0.00017445 | 0.055603 | 318.7355 | 5548929 | B-A | 004/007 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2019 | 2019-12-01 00:37 | 43800.0257 | No | YES | No | 0.69722 | 1004 | 2019-12-01 17:21 | 43800.7229 | F | Tree | Tree failure | COND | 118213053 | NO-W | INT-13138 | 4459 | 4459 | 323862 | 0.00080358 | 0.058365 | 72.6311 | 5548929 | B-G | 014/148 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2019 | 2019-12-04 14:47 | 43803.616 | No | YES | No | 0.00069444 | 1 | 2019-12-04 14:48 | 43803.6167 | F | Weather | Lightning | COND | NONE | CC-S | INT-13146-2 | 340 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 000/008 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2019 | 2019-12-15 07:22 | 43814.3069 | No | YES | No | 0.31458 | 453 | 2019-12-15 14:55 | 43814.6215 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-13185 | 1433 | 1433 | 231664 | 0.00025825 | 0.041749 | 161.6636 | 5548929 | A-G | 019/399 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-01-01 00:01 | 43831.0007 | No | YES | No | 0.34861 | 502 | 2020-01-01 08:23 | 43831.3493 | F | External contact | Vandalism | COND | 118388952 | NO-W | INT-13212 | 4573 | 2086 | 985898 | 0.00037593 | 0.17767 | 472.6261 | 5548929 | A-G | 029/005 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2020 | 2020-01-06 06:02 | 43836.2514 | No | YES | No | 0.42847 | 617 | 2020-01-06 16:19 | 43836.6799 | F | Tree | Tree failure | COND | NONE | CC-S | INT-13218 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 002/012 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2020 | 2020-01-07 19:45 | 43837.8229 | No | YES | No | 0.8875 | 1278 | 2020-01-08 17:03 | 43838.7104 | F | Equipment failure | Insulator-line | COND | NONE | CC-S | INT-13221 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-C | 056/241 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2020 | 2020-01-09 08:18 | 43839.3458 | No | YES | No | 0.39375 | 567 | 2020-01-09 17:45 | 43839.7396 | F | External contact | Car pole | STRU | 118418115 | CV-S | INT-13224 | 4 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 000/003 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-01-16 02:59 | 43846.1243 | YES | YES | No | 1900-01-01 17:03 | 3903 | 2020-01-18 20:02 | 43848.8347 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-13237 | 4122 | 4122 | 5621957 | 0.00074285 | 1.0132 | 1363.8906 | 5548929 | B-G | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-01-16 02:59 | 43846.1243 | YES | YES | No | 1900-01-01 17:03 | 3903 | 2020-01-18 20:02 | 43848.8347 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-13237 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-01-16 02:59 | 43846.1243 | YES | YES | No | 1900-01-01 17:03 | 3903 | 2020-01-18 20:02 | 43848.8347 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-13237 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | NA | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-01-16 05:45 | 43846.2396 | YES | YES | No | 1900-01-02 22:18 | 5658 | 2020-01-20 04:03 | 43850.1687 | C | Tree | Tree failure | COND | NONE | NO-W | INT-13239 | 4 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 023/001 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2020 | 2020-01-16 05:52 | 43846.2444 | YES | YES | No | 1899-12-31 17:27 | 2487 | 2020-01-17 23:19 | 43847.9715 | F | Tree | Tree failure | COND | 118436423 | NO-W | INT-13240 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-G | 073/003 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2020 | 2020-01-16 09:05 | 43846.3785 | YES | YES | No | 0.29722 | 428 | 2020-01-16 16:13 | 43846.6757 | F | External contact | Car pole | COND | NONE | CV-N | T20-003055 | 3620 | 3620 | 522037 | 0.00065238 | 0.094079 | 144.2091 | 5548929 | NA | NA | EFO | Emergency Forced Outage
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2020 | 2020-01-16 16:48 | 43846.7 | YES | YES | No | 0.61458 | 885 | 2020-01-17 07:33 | 43847.3146 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-13256 | 2522 | 1606 | 522037 | 0.00028943 | 0.094079 | 325.0542 | 5548929 | C-G | 012/221 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2020 | 2020-01-28 03:58 | 43858.1653 | No | YES | No | 0.58125 | 837 | 2020-01-28 17:55 | 43858.7465 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-13279 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-G | 047/286 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2020 | 2020-02-09 08:55 | 43870.3715 | YES | YES | No | 0.68958 | 993 | 2020-02-10 01:28 | 43871.0611 | F | Equipment failure | Structure-line | COND | NONE | BA | INT-13302 | 4446 | 4446 | 926741 | 0.00080124 | 0.16701 | 208.4438 | 5548929 | A-B-C | 001/031 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2020 | 2020-02-09 08:55 | 43870.3715 | YES | YES | No | 0.70139 | 1010 | 2020-02-10 01:45 | 43871.0729 | F | Equipment failure | Conductor | COND | NONE | BA | INT-13308 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2020 | 2020-02-09 13:26 | 43870.5597 | YES | YES | No | 1899-12-31 21:25 | 2725 | 2020-02-11 10:51 | 43872.4521 | F | Equipment failure | Structure-line | COND | NONE | CC-S | INT-13312 | 265 | 265 | 13780 | 4.7757e-05 | 0.0024834 | 52 | 5548929 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2020 | 2020-02-29 12:58 | 43890.5403 | No | YES | No | 1899-12-31 00:50 | 1490 | 2020-03-01 13:48 | 43891.575 | F | Disaster | Fire | COND | 118606050 | CV-S | INT-13362 | 2167 | 1273 | 7638 | 0.00022941 | 0.0013765 | 6 | 5548929 | B-G | 005/116 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2020 | 2020-03-01 04:33 | 43891.1896 | No | YES | No | 0.54653 | 787 | 2020-03-01 17:40 | 43891.7361 | F | External contact | Car pole | STRU | 118593946 | CC-S | INT-13365 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-G | 008/012 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2020 | 2020-03-15 05:48 | 43905.2417 | YES | YES | No | 1900-01-01 12:21 | 3621 | 2020-03-17 18:09 | 43907.7562 | F | Tree | Tree failure | COND | NONE | NO-E | INT-13410 | 1375 | 1375 | 887625 | 0.0002478 | 0.15996 | 645.5455 | 5548929 | A-B | 009/238 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2020 | 2020-03-15 14:53 | 43905.6201 | YES | YES | No | 1900-01-03 06:20 | 6140 | 2020-03-19 21:13 | 43909.884 | C | Equipment failure | Conductor | INSL | NONE | NO-E | INT-13414 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 003/022 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2020 | 2020-03-20 14:17 | 43910.5951 | No | YES | No | 0.60486 | 871 | 2020-03-21 04:48 | 43911.2 | F | External contact | Car pole | STRU | 118732577 | NO-E | INT-13457-1 | 545 | 545 | 480145 | 9.8217e-05 | 0.086529 | 881 | 5548929 | A-B-C | 007/150 | AUTO | Dependent Mode-initiating
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-04-02 15:23 | 43923.641 | No | YES | No | 0.59722 | 860 | 2020-04-03 05:43 | 43924.2382 | F | Tree | Tree-3rd party | COND | NONE | NO-E | INT-13492-1 | 4912 | 4912 | 870429 | 0.00088522 | 0.15686 | 177.2046 | 5548929 | A-B-C | 065/004 | AUTO | Dependent Mode-initiating
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2020 | 2020-04-12 22:35 | 43933.941 | No | YES | No | 0.33264 | 479 | 2020-04-13 06:34 | 43934.2736 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-13539 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2020 | 2020-05-07 15:09 | 43958.6312 | No | YES | No | 0.42639 | 614 | 2020-05-08 01:23 | 43959.0576 | F | External contact | Aircraft | COND | 118998431 | CV-S | INT-13629 | 296 | 296 | 35245 | 5.3344e-05 | 0.0063517 | 119.0709 | 5548929 | B-C-G | 008/010 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2020 | 2020-05-28 19:39 | 43979.8187 | No | YES | No | 0.64375 | 927 | 2020-05-29 11:06 | 43980.4625 | F | Equipment failure | Connector/ hardware | COND | 119077458 | CC-S | INT-13698 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 010/052 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2020 | 2020-05-29 17:14 | 43980.7181 | No | YES | No | 0.78681 | 1133 | 2020-05-30 12:07 | 43981.5049 | F | Disaster | Fire | COND | 119081875 | CV-S | INT-13702-1 | 189 | 189 | 105714 | 3.4061e-05 | 0.019051 | 559.3333 | 5548929 | A-B-C-G | 006/081 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2020 | 2020-06-02 12:53 | 43984.5368 | No | YES | No | 1900-01-01 07:31 | 3331 | 2020-06-04 20:24 | 43986.85 | F | External contact | Aircraft | COND | NONE | NO-E | INT-13715 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 010/076 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2020 | 2020-06-27 00:55 | 44009.0382 | No | YES | No | 0.85486 | 1231 | 2020-06-27 21:26 | 44009.8931 | F | External contact | Car pole | STRU | 119232606 | CV-N | INT-13785 | 240 | 240 | 15120 | 4.3252e-05 | 0.0027249 | 63 | 5548929 | A-B-C | 004/102 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 230 | 230 | 2020 | 2020-07-01 22:55 | 44013.9549 | No | YES | No | 0.92639 | 1334 | 2020-07-02 21:09 | 44014.8812 | F | Equipment failure | Insulator-line | COND | 119307643 | CC-S | INT-13806 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 007/031 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | CENTRAL | 115 | 115 | 2020 | 2020-07-03 05:33 | 44015.2312 | No | YES | No | 0.42847 | 617 | 2020-07-03 15:50 | 44015.6597 | F | Disaster | Fire | COND | NONE | CV-N | INT-13808 | 1 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 049/300 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2020 | 2020-07-12 03:49 | 44024.159 | No | YES | No | 0.14444 | 208 | 2020-07-12 07:17 | 44024.3035 | F | Equipment failure | Connector/ hardware | COND | 119359880 | CV-S | INT-13829 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2020 | 2020-07-30 11:20 | 44042.4722 | No | YES | No | 0.42083 | 606 | 2020-07-30 21:26 | 44042.8931 | F | Equipment failure | Insulator-line | COND | 119534844 | CC-S | INT-13871 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 024/374C | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2020 | 2020-08-14 18:18 | 44057.7625 | No | YES | No | 0.36667 | 528 | 2020-08-15 03:06 | 44058.1292 | F | Equipment failure | Connector/ hardware | COND | 119645734 | BA | INT-13906 | 16869 | 0 | 0 | 0 | 0 | 0 | 5548929 | B-G | 000/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2020 | 2020-08-17 05:49 | 44060.2424 | YES | YES | YES | 0.62778 | 904 | 2020-08-17 20:53 | 44060.8701 | F | Weather | Lightning | COND | 119685791 | NO-E | INT-13984 | 1836 | 1836 | 942856 | 0.00033087 | 0.16992 | 513.5381 | 5548929 | C-G | 001/019 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-08-17 09:56 | 44060.4139 | YES | YES | YES | 0.54792 | 789 | 2020-08-17 23:05 | 44060.9618 | F | Weather | Lightning | COND | NONE | NO-W | INT-13997 | 2083 | 2083 | 590957 | 0.00037539 | 0.1065 | 283.7048 | 5548929 | A-B-C | 016/191 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2020 | 2020-08-19 03:41 | 44062.1535 | No | YES | YES | 1900-01-29 19:32 | 44372 | 2020-09-18 23:13 | 44092.9674 | C | Disaster | Fire | STRU | 119660916 | CC-N | INT-14030-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-C | 015/129 | AUTO | Dependent Mode-initiating
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2020 | 2020-09-13 16:18 | 44087.6792 | No | YES | No | 0.23542 | 339 | 2020-09-13 21:57 | 44087.9146 | F | External contact | Vandalism | COND | 119758306 | CV-N | INT-14103 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B-G | 000/014 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2020 | 2020-09-19 08:50 | 44093.3681 | No | YES | No | 0.46042 | 663 | 2020-09-19 19:53 | 44093.8285 | F | Equipment failure | Structure-line | COND | 119794434 | CC-S | INT-14125-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 011/209 | AUTO | Dependent Mode-initiating
CENTRAL VALLEY | SOUTH | 115 | 115 | 2020 | 2020-10-04 04:17 | 44108.1785 | No | YES | No | 0.36319 | 523 | 2020-10-04 13:00 | 44108.5417 | F | Equipment failure | Conductor | COND | 119852298 | CV-N | INT-14170-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | A-B | 015/005 | AUTO | Dependent Mode-initiating
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2020 | 2020-10-07 06:51 | 44111.2854 | No | YES | YES | 0.44375 | 639 | 2020-10-07 17:30 | 44111.7292 | F | Equipment failure | Conductor | COND | 119866433 | CC-S | INT-14180 | 2 | 0 | 0 | 0 | 0 | 0 | 5548929 | C-G | 023/289 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2020 | 2020-10-22 07:06 | 44126.2958 | YES | YES | YES | 1899-12-31 09:43 | 2023 | 2020-10-23 16:49 | 44127.7007 | F | External contact | Car pole | COND | NONE | NO-E | INT-14210 | 8437 | 8437 | 704139 | 0.0015205 | 0.1269 | 83.4585 | 5548929 | C-G | 001/040 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2020 | 2020-10-31 05:52 | 44135.2444 | No | YES | YES | 0.71806 | 1034 | 2020-10-31 23:06 | 44135.9625 | F | Equipment failure | Conductor | INSL | 119972887 | NO-W | INT-14237 | 5882 | 5882 | 641683 | 0.00106 | 0.11564 | 109.0927 | 5548929 | A-B-C | 013/142 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2020 | 2020-11-07 13:15 | 44142.5521 | No | YES | No | 0.65139 | 938 | 2020-11-08 04:53 | 44143.2035 | F | Contamination | Animal waste | STRU | 119996446 | CV-S | T20-017955 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | EFO | Emergency Forced Outage
BAY AREA | CENTRAL | 115 | 115 | 2020 | 2020-11-14 07:00 | 44149.2917 | No | YES | YES | 1899-12-31 11:46 | 2146 | 2020-11-15 18:46 | 44150.7819 | F | External contact | Car pole | STRU | NONE | BA | INT-14268 | 0 | 0 | 0 | 0 | 0 | 0 | 5548929 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2020 | 2020-11-17 13:14 | 44152.5514 | No | YES | YES | 0.55764 | 803 | 2020-11-18 02:37 | 44153.109 | F | Tree | Tree failure | COND | NONE | NO-E | INT-14278-2 | 4022 | 4022 | 953544 | 0.00072482 | 0.17184 | 237.082 | 5548929 | A-B-C-G | ;000/004 | AUTO | Dependent Mode
BAY AREA | CENTRAL | 115 | 115 | 2021 | 2021-01-13 06:46 | 44209.2819 | No | YES | No | 0.67639 | 974 | 2021-01-13 23:00 | 44209.9583 | F | External contact | Car pole | STRU | NONE | CC-N | INT-14376 | 1 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 003/061 | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2021 | 2021-01-13 18:17 | 44209.7618 | No | YES | No | 1900-01-01 22:13 | 4213 | 2021-01-16 16:30 | 44212.6875 | F | Equipment failure | Conductor | COND | 120432967 | CC-N | INT-14377 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-G | 004/034 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2021 | 2021-01-18 21:31 | 44214.8965 | YES | YES | No | 1900-01-06 20:46 | 11326 | 2021-01-26 18:17 | 44222.7618 | C | Equipment failure | Conductor | COND | 120452608 | NO-W | INT-14388 | 1 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-G | 000/002 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-01-19 00:19 | 44215.0132 | YES | YES | No | 0.87708 | 1263 | 2021-01-19 21:22 | 44215.8903 | F | Tree | Tree failure | COND | NONE | NO-E | INT-14393 | 2584 | 986 | 1751631 | 0.00017508 | 0.31103 | 1776.502 | 5631636 | A-B-G | 020/552 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | CENTRAL | 230 | 230 | 2021 | 2021-01-19 01:55 | 44215.0799 | YES | YES | No | 1900-01-02 14:51 | 5211 | 2021-01-22 16:46 | 44218.6986 | C | Tree | Tree failure | COND | 120448668 | CC-N | INT-14399 | 1 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B | 014/057 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | CENTRAL | 230 | 230 | 2021 | 2021-01-19 01:55 | 44215.0799 | YES | YES | No | 1900-01-02 14:25 | 5185 | 2021-01-22 16:20 | 44218.6806 | C | Tree | Tree failure | COND | 120448608 | CC-N | INT-14401 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B | 014/057 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-01-19 02:08 | 44215.0889 | YES | YES | No | 0.38333 | 552 | 2021-01-19 11:20 | 44215.4722 | F | Equipment failure | Conductor | COND | 120448711 | CV-S | INT-14400 | 4569 | 4569 | 887004 | 0.00081131 | 0.1575 | 194.1353 | 5631636 | B-G | 016/007 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-01-19 17:57 | 44215.7479 | YES | YES | No | 1900-01-01 00:02 | 2882 | 2021-01-21 17:59 | 44217.7493 | F | Equipment failure | Structure-line | STRU | 120448227 | CV-S | INT-14415 | 1181 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 001/018 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-01-21 15:15 | 44217.6354 | No | YES | No | 0.43958 | 633 | 2021-01-22 01:48 | 44218.075 | F | External contact | Car pole | STRU | 120454934 | CV-N | INT-14425 | 1 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C | 002/016 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2021 | 2021-01-25 02:08 | 44221.0889 | YES | YES | No | 0.68889 | 992 | 2021-01-25 18:40 | 44221.7778 | F | Equipment failure | Conductor | COND | 120475280 | CV-N | INT-14432 | 11480 | 9785 | 754804 | 0.0017375 | 0.13403 | 77.1389 | 5631636 | B-C | 004/026 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-01-25 02:52 | 44221.1194 | YES | YES | No | 0.35972 | 518 | 2021-01-25 11:30 | 44221.4792 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-14433 | 1790 | 1790 | 206744 | 0.00031785 | 0.036711 | 115.4994 | 5631636 | A-G | 019/396 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 12:22 | 44222.5153 | YES | YES | No | 1899-12-31 00:54 | 1494 | 2021-01-27 13:16 | 44223.5528 | F | Equipment failure | Conductor | LS | NONE | NO-W | INT-14443 | 9578 | 9578 | 1269711 | 0.0017007 | 0.22546 | 132.5654 | 5631636 | A-B-C-G | 006/006 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 18:42 | 44222.7792 | YES | YES | No | 1900-01-04 01:06 | 7266 | 2021-01-31 19:48 | 44227.825 | C | Tree | Tree failure | ENCR | NONE | NO-W | INT-14447 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B | 009/005 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 18:44 | 44222.7806 | YES | YES | No | 1899-12-31 23:22 | 2842 | 2021-01-28 18:06 | 44224.7542 | F | Tree | Tree failure | COND | NONE | NO-W | INT-14451 | 2004 | 356 | 1015045 | 6.3214e-05 | 0.18024 | 2851.25 | 5631636 | A-B-C | 020/004 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 18:56 | 44222.7889 | YES | YES | No | 1899-12-31 22:46 | 2806 | 2021-01-28 17:42 | 44224.7375 | F | Tree | Tree failure | COND | NONE | NO-W | INT-14452 | 4222 | 4222 | 8492333 | 0.00074969 | 1.508 | 2011.4479 | 5631636 | B-C | 018/003 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 19:32 | 44222.8139 | YES | YES | No | 1900-01-01 21:53 | 4193 | 2021-01-29 17:25 | 44225.7257 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-14454-1 | 239 | 239 | 1160814 | 4.2439e-05 | 0.20612 | 4856.9623 | 5631636 | C-A-G | 019/004 | AUTO | Dependent Mode-initiating
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 20:09 | 44222.8396 | YES | YES | No | 1900-01-04 01:59 | 7319 | 2021-01-31 22:08 | 44227.9222 | C | Tree | Tree failure | COND | NONE | NO-W | INT-14463 | 1 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-G | 050/005 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 22:17 | 44222.9285 | YES | YES | No | 1899-12-31 16:36 | 2436 | 2021-01-28 14:53 | 44224.6201 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-14483 | 4250 | 4250 | 10196280 | 0.00075467 | 1.8105 | 2399.1247 | 5631636 | C-G | 017/000 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2021 | 2021-01-26 22:18 | 44222.9292 | YES | YES | No | 0.77014 | 1109 | 2021-01-27 16:47 | 44223.6993 | F | Tree | Tree failure | COND | 120469156 | CC-S | INT-14484 | 1 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-G | 005/138 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-01-26 22:21 | 44222.9313 | YES | YES | No | 0.84931 | 1223 | 2021-01-27 18:44 | 44223.7806 | F | Equipment failure | Structure-line | COND | 120474164 | NO-E | INT-14490 | 896 | 896 | 2165639 | 0.0001591 | 0.38455 | 2417.0078 | 5631636 | A-G | 005/095 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-01-26 23:01 | 44222.959 | YES | YES | No | 0.75139 | 1082 | 2021-01-27 17:03 | 44223.7104 | F | Tree | Tree failure | COND | LCN-120470628 | NO-W | INT-14491 | 4607 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 028/003 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2021 | 2021-01-26 23:21 | 44222.9729 | YES | YES | No | 0.53056 | 764 | 2021-01-27 12:05 | 44223.5035 | F | Equipment failure | Conductor | INSL | NONE | CV-N | INT-14503 | 8818 | 8818 | 8678921 | 0.0015658 | 1.5411 | 984.2278 | 5631636 | B-G | 001/048 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-01-27 00:24 | 44223.0167 | YES | YES | No | 0.74306 | 1070 | 2021-01-27 18:14 | 44223.7597 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-14507 | 8214 | 8214 | 1363524 | 0.0014585 | 0.24212 | 166 | 5631636 | A-B-C | 003/068 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-01-27 05:42 | 44223.2375 | YES | YES | No | 1899-12-31 14:09 | 2289 | 2021-01-28 19:51 | 44224.8271 | F | Tree | Tree failure | COND | NONE | NO-E | INT-14551 | 565 | 565 | 1297240 | 0.00010033 | 0.23035 | 2296 | 5631636 | A-B | 000/012 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2021 | 2021-01-27 12:26 | 44223.5181 | YES | YES | No | 0.25625 | 369 | 2021-01-27 18:35 | 44223.7743 | F | Equipment failure | Conductor | COND | NONE | CV-S | INT-14540 | 5 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-G | 010/166 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-01-27 14:38 | 44223.6097 | YES | YES | No | 1899-12-31 04:55 | 1735 | 2021-01-28 19:33 | 44224.8146 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-14542 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | NA | NA | EFO | Emergency Forced Outage
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2021 | 2021-01-28 08:09 | 44224.3396 | YES | YES | No | 1900-01-01 09:21 | 3441 | 2021-01-30 17:30 | 44226.7292 | F | Tree | Tree failure | COND | NONE | CV-N | INT-14553 | 983 | 983 | 3396265 | 0.00017455 | 0.60307 | 3455 | 5631636 | C-G | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-02-01 04:34 | 44228.1903 | No | YES | No | 0.45694 | 658 | 2021-02-01 15:32 | 44228.6472 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-14573 | 322 | 322 | 109332 | 5.7177e-05 | 0.019414 | 339.5404 | 5631636 | B-G | 012/263 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-02-04 10:33 | 44231.4396 | No | YES | No | 1899-12-31 12:20 | 2180 | 2021-02-05 22:53 | 44232.9535 | F | Equipment failure | Conductor | COND | NONE | NO-E | T21-004574 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | NA | NA | EFO | Emergency Forced Outage
SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | 2021 | 2021-02-05 20:28 | 44232.8528 | No | YES | No | 0.95417 | 1374 | 2021-02-06 19:22 | 44233.8069 | F | External contact | Vandalism | COND | 120504769 | CC-S | INT-14584 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 002/013 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-02-07 05:54 | 44234.2458 | No | YES | No | 0.30347 | 437 | 2021-02-07 13:11 | 44234.5493 | F | Equipment failure | Conductor | COND | 120505824 | CV-S | INT-14585 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-G | :050/001 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-02-07 19:08 | 44234.7972 | No | YES | No | 0.81806 | 1178 | 2021-02-08 14:46 | 44235.6153 | F | External contact | Car pole | STRU | 120505794 | CV-S | INT-14589-1 | 6291 | 6291 | 1218719 | 0.0011171 | 0.21641 | 193.7242 | 5631636 | A-B-G | 006/084 | AUTO | Dependent Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-02-24 12:03 | 44251.5021 | No | YES | No | 0.29375 | 423 | 2021-02-24 19:06 | 44251.7958 | F | Equipment failure | Conductor | COND | 120575614 | NO-E | INT-14615 | 902 | 902 | 455510 | 0.00016017 | 0.080884 | 505 | 5631636 | NA | NA | EFO | Emergency Forced Outage
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-03-10 03:52 | 44265.1611 | No | YES | No | 0.59861 | 862 | 2021-03-10 18:14 | 44265.7597 | F | Equipment failure | Conductor | COND | 120609465 | CV-S | INT-14647 | 715 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 005/090 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2021 | 2021-03-11 02:33 | 44266.1062 | No | YES | No | 0.68542 | 987 | 2021-03-11 19:00 | 44266.7917 | F | Tree | Tree failure | COND | 120636414 | CC-S | INT-14666 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 002/048 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-03-14 16:46 | 44269.6986 | No | YES | No | 0.65764 | 947 | 2021-03-15 08:33 | 44270.3562 | F | Tree | Tree failure | COND | NONE | NO-E | INT-14669 | 14431 | 14431 | 1473083 | 0.0025625 | 0.26157 | 102.0777 | 5631636 | C-G | 014/322 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-03-15 11:20 | 44270.4722 | No | YES | No | 0.34514 | 497 | 2021-03-15 19:37 | 44270.8174 | F | Equipment failure | Conductor | COND | 120645394 | NO-E | INT-14677 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-G | 009/210 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-03-19 10:14 | 44274.4264 | No | YES | No | 1899-12-31 05:08 | 1748 | 2021-03-20 15:22 | 44275.6403 | F | External contact | Vandalism | COND | 120671288 | CV-S | INT-14693-1 | 1446 | 1446 | 216106 | 0.00025676 | 0.038374 | 149.4509 | 5631636 | A-G | 010/091 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-03-24 03:46 | 44279.1569 | No | YES | No | 0.31389 | 452 | 2021-03-24 11:18 | 44279.4708 | F | Equipment failure | Conductor | COND | 120685289 | CV-S | INT-14705 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-G | :048/002 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2021 | 2021-03-26 14:36 | 44281.6083 | No | YES | No | 0.55625 | 801 | 2021-03-27 03:57 | 44282.1646 | F | Equipment failure | Conductor | COND | 120702562 | CC-S | T21-007297 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | NA | NA | EFO | Emergency Forced Outage
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2021 | 2021-03-27 03:15 | 44282.1354 | No | YES | No | 0.63611 | 916 | 2021-03-27 18:31 | 44282.7715 | F | Equipment failure | Conductor | COND | NONE | CV-N | INT-14708 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-G | 012/076 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-03-29 14:40 | 44284.6111 | No | YES | No | 0.70278 | 1012 | 2021-03-30 07:32 | 44285.3139 | F | Tree | Tree failure | COND | NONE | NO-W | INT-14718 | 1492 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 017/010 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2021 | 2021-04-01 03:34 | 44287.1486 | No | YES | No | 0.80486 | 1159 | 2021-04-01 22:53 | 44287.9535 | F | External contact | Car pole | STRU | NONE | BA | INT-14730 | 230 | 230 | 30360 | 4.0841e-05 | 0.005391 | 132 | 5631636 | NA | NA | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-04-08 09:59 | 44294.416 | No | YES | No | 0.8125 | 1170 | 2021-04-09 05:29 | 44295.2285 | F | External contact | Car pole | STRU | 120766835 | NO-E | INT-14740 | 3010 | 3010 | 636086 | 0.00053448 | 0.11295 | 211.3243 | 5631636 | A-B-C-G | A002/064 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-05-07 03:42 | 44323.1542 | No | YES | No | 0.50972 | 734 | 2021-05-07 15:56 | 44323.6639 | F | External contact | Car pole | COND | 120990274 | CV-N | INT-14798 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C-G | 007/004 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-05-08 09:29 | 44324.3951 | No | YES | No | 0.31806 | 458 | 2021-05-08 17:07 | 44324.7132 | F | Equipment failure | Connector/ hardware | COND | 120990343 | NO-E | INT-14801 | 902 | 902 | 421234 | 0.00016017 | 0.074798 | 467 | 5631636 | A-G | 006/099 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-05-21 16:42 | 44337.6958 | No | YES | No | 0.67361 | 970 | 2021-05-22 08:52 | 44338.3694 | F | Equipment failure | Structure-line | STRU | 121386157 | NO-E | INT-14839 | 7694 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-G | 014/292 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-06-25 17:11 | 44372.716 | No | YES | No | 1899-12-31 22:57 | 2817 | 2021-06-27 16:08 | 44374.6722 | F | External contact | Foreign object | STRU | 121619699 | NO-E | INT-14934 | 276 | 276 | 80647 | 4.9009e-05 | 0.01432 | 292.1993 | 5631636 | C-A-G | 065/478 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-08-04 19:20 | 44412.8056 | YES | YES | No | 1900-02-18 23:17 | 73397 | 2021-09-24 18:37 | 44463.7757 | X | Disaster | Fire | ENCR | NONE | NO-W | T21-014294 | 4 | 0 | 0 | 0 | 0 | 0 | 5631636 | NA | NA | EFO | Emergency Forced Outage
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2021 | 2021-08-05 10:19 | 44413.4299 | No | YES | YES | 1899-12-31 06:14 | 1814 | 2021-08-06 16:33 | 44414.6896 | F | Equipment failure | Structure-line | STRU | 121852674 | CC-S | INT-15025 | 291 | 291 | 10731 | 5.1672e-05 | 0.0019055 | 36.8763 | 5631636 | A-B-C | A011/183 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2021 | 2021-08-26 05:08 | 44434.2139 | No | YES | No | 0.68889 | 992 | 2021-08-26 21:40 | 44434.9028 | F | External contact | Car pole | COND | 121960735 | CC-S | INT-15061 | 1541 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 004/118 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 115 | 115 | 2021 | 2021-08-26 13:40 | 44434.5694 | No | YES | YES | 1900-01-05 03:34 | 8854 | 2021-09-01 17:14 | 44440.7181 | C | Disaster | Fire | LS | NONE | CV-N | INT-15062-1 | 1802 | 1802 | 398930 | 0.00031998 | 0.070837 | 221.3818 | 5631636 | C-G | 003/051 | AUTO | Dependent Mode-initiating
BAY AREA | CENTRAL | 115 | 115 | 2021 | 2021-09-05 07:07 | 44444.2965 | No | YES | No | 1899-12-31 12:08 | 2168 | 2021-09-06 19:15 | 44445.8021 | F | Equipment failure | Conductor | COND | 122004349 | BA | INT-15091 | 2 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C-G | 003/022 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2021 | 2021-09-09 22:17 | 44448.9285 | No | YES | No | 0.55347 | 797 | 2021-09-10 11:34 | 44449.4819 | F | Weather | Lightning | NONE | 122031028 | CV-S | INT-15109 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 001/012 | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2021 | 2021-09-13 13:50 | 44452.5764 | No | YES | YES | 1899-12-31 07:11 | 1871 | 2021-09-14 21:01 | 44453.8757 | F | External contact | Aircraft | COND | 122045905 | BA | INT-15139 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-G | 002/019 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-07-24 21:50 | 44401.9097 | No | YES | No | 1900-02-22 22:03 | 79083 | 2021-09-17 19:53 | 44456.8285 | C | Disaster | Fire | STRU | NONE | NO-W | T21-008315 | 9343 | 3484 | 38324 | 0.00061865 | 0.0068051 | 11 | 5631636 | NA | NA | EFO | Emergency Forced Outage
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-09-21 19:38 | 44460.8181 | No | YES | YES | 0.81667 | 1176 | 2021-09-22 15:14 | 44461.6347 | F | Equipment failure | Conductor | COND | 122094404 | NO-W | INT-15151 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 006/006 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-10-13 00:53 | 44482.0368 | No | YES | No | 0.70833 | 1020 | 2021-10-13 17:53 | 44482.7451 | F | Equipment failure | Structure-line | STRU | 122206548 | NO-W | INT-15198-1 | 2085 | 2085 | 49551 | 0.00037023 | 0.0087987 | 23.7655 | 5631636 | A-B-C | 002/007 | AUTO | Dependent Mode-initiating
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-10-19 20:48 | 44488.8667 | No | YES | No | 0.91806 | 1322 | 2021-10-20 18:50 | 44489.7847 | F | Tree | Tree failure | COND | 122236853 | NO-W | INT-15214 | 1685 | 320 | 427608 | 5.6822e-05 | 0.07593 | 1336.275 | 5631636 | A-B-C | 025/001 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-10-24 03:52 | 44493.1611 | YES | YES | No | 0.62569 | 901 | 2021-10-24 18:53 | 44493.7868 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-15233 | 3834 | 3834 | 507605 | 0.0006808 | 0.090135 | 132.3957 | 5631636 | A-G | 000/004 | AUTO | Dependent Mode-initiating
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-10-24 05:04 | 44493.2111 | YES | YES | No | 1899-12-31 08:15 | 1935 | 2021-10-25 13:19 | 44494.5549 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-15239 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-C | 015/104 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2021 | 2021-10-24 15:42 | 44493.6542 | YES | YES | No | 1899-12-31 01:08 | 1508 | 2021-10-25 16:50 | 44494.7014 | F | Equipment failure | Conductor | COND | 122258838 | CV-N | T21-017904 | 1301 | 1301 | 433846 | 0.00023102 | 0.077037 | 333.4712 | 5631636 | NA | NA | EFO | Emergency Forced Outage
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-11-08 19:38 | 44508.8181 | No | YES | No | 0.91111 | 1312 | 2021-11-09 17:30 | 44509.7292 | F | Tree | Tree failure | COND | NONE | NO-W | INT-15311 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C | 009/001 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-11-09 08:14 | 44509.3431 | No | YES | No | 1899-12-31 12:07 | 2167 | 2021-11-10 20:21 | 44510.8479 | F | Tree | Tree failure | COND | NONE | NO-W | INT-15313 | 1121 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 036/001 | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2021 | 2021-11-10 15:52 | 44510.6611 | No | YES | No | 0.35139 | 506 | 2021-11-11 00:18 | 44511.0125 | F | External contact | Car pole | STRU | 122363642 | CC-S | INT-15317 | 2491 | 2491 | 56451 | 0.00044232 | 0.010024 | 22.662 | 5631636 | A-B-G | 011/220 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2021 | 2021-12-05 23:05 | 44535.9618 | No | YES | No | 0.55694 | 802 | 2021-12-06 12:27 | 44536.5188 | F | External contact | Car pole | STRU | NONE | CV-S | INT-15383 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B-C | 006/061 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-13 20:03 | 44543.8354 | YES | YES | No | 1899-12-31 01:21 | 1521 | 2021-12-14 21:24 | 44544.8917 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-15413 | 1659 | 1659 | 2523339 | 0.00029459 | 0.44807 | 1521 | 5631636 | B-G | 010/218 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2021 | 2021-12-14 12:51 | 44544.5354 | YES | YES | YES | 0.49583 | 714 | 2021-12-15 00:45 | 44545.0312 | F | Equipment failure | Conductor | COND | 122488747 | CV-S | INT-15445 | 3323 | 3323 | 586698 | 0.00059006 | 0.10418 | 176.5567 | 5631636 | B-C | 013/001 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-15 12:53 | 44545.5368 | YES | YES | No | 1899-12-31 03:41 | 1661 | 2021-12-16 16:34 | 44546.6903 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-15459 | 578 | 578 | 286698 | 0.00010263 | 0.050908 | 496.0173 | 5631636 | B-C | 006/227 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-15 13:28 | 44545.5611 | YES | YES | No | 1900-01-02 04:57 | 4617 | 2021-12-18 18:25 | 44548.7674 | C | Tree | Tree failure | COND | NONE | NO-W | INT-15460 | 892 | 892 | 9066 | 0.00015839 | 0.0016098 | 10.1637 | 5631636 | B-G | 058/426 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-15 19:39 | 44545.8187 | YES | YES | No | 1900-01-01 21:09 | 4149 | 2021-12-18 16:48 | 44548.7 | F | Tree | Tree failure | COND | NONE | NO-E | INT-15467 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-G | :002/000 | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2021 | 2021-12-25 00:38 | 44555.0264 | YES | YES | No | 1900-05-22 18:59 | 207059 | 2022-05-17 19:37 | 44698.8174 | C | Equipment failure | Conductor | COND | 122518788 | BA | INT-15482-1 | 15294 | 9 | 5066 | 1.5981e-06 | 0.00089956 | 562.8889 | 5631636 | A-G | 008/052 | AUTO | Dependent Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-25 10:28 | 44555.4361 | YES | YES | No | 1899-12-31 05:47 | 1787 | 2021-12-26 16:15 | 44556.6771 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-15487 | 1947 | 1947 | 555066 | 0.00034573 | 0.098562 | 285.0878 | 5631636 | C-G | 011/398 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-12-26 15:48 | 44556.6583 | YES | YES | No | 1900-01-06 21:17 | 11357 | 2022-01-03 13:05 | 44564.5451 | C | Equipment failure | Structure-line | COND | NONE | NO-W | INT-15508 | 4484 | 4484 | 455066 | 0.00079622 | 0.080805 | 101.4866 | 5631636 | A-B-C | 043/009 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-26 18:16 | 44556.7611 | YES | YES | No | 1900-01-08 20:40 | 14200 | 2022-01-05 14:56 | 44566.6222 | C | Tree | Tree failure | COND | NONE | NO-E | INT-15512 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B | 000/005 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-12-26 19:18 | 44556.8042 | YES | YES | No | 1900-01-14 16:39 | 22599 | 2022-01-11 11:57 | 44572.9979 | C | Equipment failure | Structure-line | STRU | NONE | NO-W | INT-15513 | 4486 | 2004 | 1355066 | 0.00035585 | 0.24062 | 676.1806 | 5631636 | B-G | 024/006 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-12-26 20:29 | 44556.8535 | YES | YES | No | 1900-01-01 23:20 | 4280 | 2021-12-29 19:49 | 44559.8257 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-15515 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 050/006 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-26 23:07 | 44556.9632 | YES | YES | No | 1899-12-31 00:28 | 1468 | 2021-12-27 23:35 | 44557.9826 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-15517 | 2518 | 1603 | 1333444 | 0.00028464 | 0.23678 | 831.8428 | 5631636 | B-G | 008/137 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-27 00:16 | 44557.0111 | YES | YES | No | 1900-01-15 18:07 | 24127 | 2022-01-12 18:23 | 44573.766 | C | Equipment failure | Conductor | COND | NONE | NO-E | INT-15522 | 1855 | 1855 | 1333444 | 0.00032939 | 0.23678 | 718.8377 | 5631636 | A-B-C | 000/012 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-27 00:55 | 44557.0382 | YES | YES | No | 1900-01-05 16:48 | 9648 | 2022-01-02 17:43 | 44563.7382 | C | Tree | Tree failure | COND | NONE | NO-E | INT-15525 | 8669 | 8669 | 4333444 | 0.0015393 | 0.76948 | 499.8782 | 5631636 | C-A | 005/071 | AUTO | Dependent Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-27 02:29 | 44557.1035 | YES | YES | No | 1900-01-05 14:39 | 9519 | 2022-01-02 17:08 | 44563.7139 | C | Tree | Tree failure | COND | NONE | NO-E | INT-15531 | 14000 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-G | 001/019 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-27 04:46 | 44557.1986 | YES | YES | No | 1900-01-07 14:46 | 12406 | 2022-01-04 19:32 | 44565.8139 | C | Equipment failure | Insulator-line | COND | NONE | NO-E | INT-15537 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C | 021/168 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-27 05:19 | 44557.2215 | YES | YES | No | 0.73056 | 1052 | 2021-12-27 22:51 | 44557.9521 | F | Tree | Tree failure | COND | NONE | NO-E | INT-15540-1 | 4968 | 4968 | 333444 | 0.00088216 | 0.059209 | 67.1184 | 5631636 | C-A | 001/024 | AUTO | Dependent Mode-initiating
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-27 06:19 | 44557.2632 | YES | YES | No | 1900-01-02 11:24 | 5004 | 2021-12-30 17:43 | 44560.7382 | C | Tree | Tree failure | COND | NONE | NO-E | INT-15543 | 11656 | 0 | 0 | 0 | 0 | 0 | 5631636 | A-B | 004/028 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-27 06:47 | 44557.2826 | YES | YES | No | 1899-12-31 20:39 | 2679 | 2021-12-29 03:26 | 44559.1431 | F | Tree | Tree failure | COND | NONE | NO-E | INT-15548 | 3715 | 3715 | 533444 | 0.00065967 | 0.094723 | 143.5919 | 5631636 | C-A-G | 012/309 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-27 07:29 | 44557.3118 | YES | YES | No | 1900-01-07 05:07 | 11827 | 2022-01-04 12:36 | 44565.525 | C | Tree | Tree failure | COND | NONE | NO-E | INT-15552 | 25287 | 25287 | 6233444 | 0.0044902 | 1.1069 | 246.5078 | 5631636 | C-A | 008/060 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2021 | 2021-12-27 08:38 | 44557.3597 | YES | YES | No | 0.64653 | 931 | 2021-12-28 00:09 | 44558.0062 | F | Tree | Tree failure | COND | NONE | CV-N | INT-15555 | 13159 | 13159 | 3233444 | 0.0023366 | 0.57416 | 245.7211 | 5631636 | B-C | 002/061 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2021 | 2021-12-27 09:48 | 44557.4083 | YES | YES | No | 0.39236 | 565 | 2021-12-27 19:13 | 44557.8007 | F | Equipment failure | Conductor | COND | NONE | NO-W | INT-15554 | 1725 | 1725 | 233444 | 0.00030631 | 0.041452 | 135.3299 | 5631636 | C-G | 006/002 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-27 21:14 | 44557.8847 | YES | YES | No | 1900-01-07 21:11 | 12791 | 2022-01-05 18:25 | 44566.7674 | C | Tree | Tree failure | COND | NONE | NO-E | T21-019155 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | NA | NA | EFO | Emergency Forced Outage
NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | 2021 | 2021-12-29 08:55 | 44559.3715 | YES | YES | No | 1900-01-03 13:05 | 6545 | 2022-01-02 22:00 | 44563.4167 | C | Tree | Tree failure | STRU | NONE | NO-E | INT-15573 | 21345 | 21345 | 6253464 | 0.0037902 | 1.1104 | 292.9709 | 5631636 | C-G | 000/003C | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2021 | 2021-12-30 10:31 | 44560.4382 | No | YES | No | 1899-12-31 04:05 | 1685 | 2021-12-31 14:36 | 44561.6083 | F | Equipment failure | Conductor | COND | NONE | NO-E | INT-15584 | 2837 | 1681 | 653464 | 0.00029849 | 0.11603 | 388.7353 | 5631636 | B-C | 019/521 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2022 | 2022-01-02 21:41 | 44563.9035 | No | YES | No | 1899-12-31 15:49 | 2389 | 2022-01-04 13:30 | 44565.5625 | F | Tree | Tree failure | COND | NONE | NORTH VALLEY AND SIERRA | INT-15591-1 | 8669 | 1462 | 71708 | 0.0004718 | 0.059249 | 125.58 | 5631636 | A-G | B016/372 | AUTO | Dependent Mode-initiating
CENTRAL VALLEY | SOUTH | 69 | 70 | 2022 | 2022-01-05 05:11 | 44566.216 | No | YES | No | 0.57222 | 824 | 2022-01-05 18:55 | 44566.7882 | F | External contact | Car pole | STRU | 122552394 | CENTRAL VALLEY | INT-15599 | 2792 | 1156 | 105150 | 0.00020527 | 0.018671 | 90.9602 | 5631636 | A-G | 027/12A | AUTO | Single Mode
SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | 2022 | 2022-01-21 19:54 | 44582.8292 | No | YES | No | 1900-01-08 19:53 | 14153 | 2022-01-31 15:47 | 44592.6576 | C | Disaster | Fire | STRU | NONE | SOUTH BAY AND CENTRAL COAST | INT-15624-2 | 1110 | 1110 | 2044884 | 0.0001971 | 0.36311 | 1842.2378 | 5631636 | A-G | 012/007 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2022 | 2022-01-22 01:45 | 44583.0729 | No | YES | No | 0.44375 | 639 | 2022-01-22 12:24 | 44583.5167 | F | Tree | Tree failure | COND | NONE | NORTH COAST | INT-15629 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-A | 002/004 | AUTO | Single Mode
NORTH COAST | NORTH | 69 | 60 | 2022 | 2022-01-22 05:48 | 44583.2417 | No | YES | No | 0.45764 | 659 | 2022-01-22 16:47 | 44583.6993 | F | Equipment failure | Conductor | COND | NONE | NORTH COAST | INT-15634 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C-G | 016/000 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2022 | 2022-01-22 12:14 | 44583.5097 | No | YES | No | 0.39097 | 563 | 2022-01-22 21:37 | 44583.9007 | F | Equipment failure | Conductor | COND | NONE | CENTRAL VALLEY | INT-15636 | 295 | 295 | 34810 | 5.2383e-05 | 0.0061812 | 118 | 5631636 | A-B-C | 009/086 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2022 | 2022-02-16 08:50 | 44608.3681 | No | YES | No | 0.39236 | 565 | 2022-02-16 18:15 | 44608.7604 | F | Equipment failure | Conductor | COND | NONE | CENTRAL VALLEY | INT-15679-1 | 129 | 129 | 3169 | 2.2906e-05 | 0.00056271 | 24.5659 | 5631636 | A-C | 001/026 | AUTO | Dependent Mode-initiating
CENTRAL VALLEY | SOUTH | 115 | 115 | 2022 | 2022-03-02 21:31 | 44622.8965 | No | YES | No | 0.43681 | 629 | 2022-03-03 08:00 | 44623.3333 | F | External contact | Car pole | COND | 123045935 | CENTRAL VALLEY | INT-15704 | 1757 | 1757 | 250802 | 0.00030958 | 0.044191 | 142.7445 | 5675418 | A-G | 025/009 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2022 | 2022-03-28 07:19 | 44648.3049 | No | YES | No | 0.33264 | 479 | 2022-03-28 15:18 | 44648.6375 | F | External contact | Vandalism | COND | 123204599 | CENTRAL VALLEY | INT-15748 | 1792 | 1792 | 401052 | 0.00031575 | 0.070665 | 223.8013 | 5675418 | B-G | 011/116 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2022 | 2022-04-11 11:00 | 44662.4583 | No | YES | No | 0.73194 | 1054 | 2022-04-12 04:34 | 44663.1903 | F | Equipment failure | Structure-line | STRU | NONE | NORTH VALLEY AND SIERRA | INT-15793 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | AUTO | Single Mode
BAY AREA | CENTRAL | 69 | 60 | 2022 | 2022-04-27 02:15 | 44678.0938 | No | YES | No | 0.34722 | 500 | 2022-04-27 10:35 | 44678.441 | F | Equipment failure | Connector/ hardware | COND | 123440783 | BAY AREA | INT-15855 | 234 | 231 | 111317 | 4.0702e-05 | 0.019614 | 481.8918 | 5675418 | C-G | 002/053 | AUTO | Single Mode
BAY AREA | CENTRAL | 115 | 115 | 2022 | 2022-04-27 21:05 | 44678.8785 | No | YES | No | 1899-12-31 14:29 | 2309 | 2022-04-29 11:34 | 44680.4819 | F | Equipment failure | Connector/ hardware | COND | NONE | CENTRAL VALLEY | INT-15859 | 2 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-A-G | AEC Site 300 2nd sub | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2022 | 2022-04-29 04:05 | 44680.1701 | No | YES | No | 0.35 | 504 | 2022-04-29 12:29 | 44680.5201 | F | External contact | Car pole | COND | NONE | NORTH VALLEY AND SIERRA | INT-15861 | 4573 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C-G | 000/005 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2022 | 2022-05-04 00:12 | 44685.0083 | No | YES | No | 0.78125 | 1125 | 2022-05-04 18:57 | 44685.7896 | F | External contact | Car pole | COND | NONE | CENTRAL VALLEY | INT-15873 | 278 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 031/584 | AUTO | Single Mode
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2022 | 2022-05-06 23:47 | 44687.991 | No | YES | No | 0.68333 | 984 | 2022-05-07 16:11 | 44688.6743 | F | External contact | Car pole | COND | NONE | NORTH VALLEY AND SIERRA | INT-15879 | 4124 | 4124 | 212214 | 0.00072664 | 0.037392 | 51.4583 | 5675418 | B-C-G | 014/280 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 115 | 115 | 2022 | 2022-05-25 14:05 | 44706.5868 | No | YES | No | 0.51736 | 745 | 2022-05-26 02:30 | 44707.1042 | F | External contact | Car pole | STRU | 123695976 | CENTRAL VALLEY | INT-15938 | 743 | 740 | 203500 | 0.00013039 | 0.035856 | 275 | 5675418 | A-B-C | 000/009 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2022 | 2022-05-25 17:48 | 44706.7417 | No | YES | No | 0.18889 | 272 | 2022-05-25 22:20 | 44706.9306 | F | Equipment failure | Connector/ hardware | COND | NONE | CENTRAL VALLEY | INT-15940 | 16366 | 16365 | 2693125 | 0.0028835 | 0.47452 | 164.5661 | 5675418 | A-G | 005/033 | AUTO | Single Mode
CENTRAL VALLEY | SOUTH | 69 | 70 | 2022 | 2022-05-29 05:00 | 44710.2083 | No | YES | No | 0.58681 | 845 | 2022-05-29 19:05 | 44710.7951 | F | Equipment failure | Conductor | COND | NONE | CENTRAL VALLEY | T22-010653 | 1790 | 1790 | 26414 | 0.0003154 | 0.0046541 | 14.7564 | 5675418 | NA | NA | EFO | Emergency Forced Outage
CENTRAL VALLEY | SOUTH | 69 | 70 | 2022 | 2022-06-01 16:19 | 44713.6799 | No | YES | No | 0.47708 | 687 | 2022-06-02 03:46 | 44714.1569 | F | External contact | Car pole | STRU | 123737145 | CENTRAL VALLEY | INT-15955 | 3369 | 2437 | 320481 | 0.0004294 | 0.056468 | 131.5064 | 5675418 | A-B | 011/003 | AUTO | Single Mode
NORTH COAST | NORTH | 115 | 115 | 2022 | 2022-06-16 05:24 | 44728.225 | No | YES | YES | 0.59306 | 854 | 2022-06-16 19:38 | 44728.8181 | F | Equipment failure | Conductor | COND | NONE | NORTH COAST | INT-16006 | 24520 | 1442 | 172697 | 0.00025408 | 0.030429 | 119.7621 | 5675418 | B-G | 003/017 | AUTO | Dependent Mode-initiating
CENTRAL VALLEY | SOUTH | 115 | 115 | 2022 | 2022-06-22 07:08 | 44734.2972 | No | YES | YES | 0.99444 | 1432 | 2022-06-23 07:00 | 44735.2917 | F | Equipment failure | Structure-line | STRU | 123900762 | CENTRAL VALLEY | INT-16024 | 7263 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C-G | 015/001 | AUTO | Single Mode
CENTRAL VALLEY | CENTRAL | 69 | 60 | 2022 | 2022-07-04 18:39 | 44746.7771 | No | YES | No | 1900-01-04 00:22 | 7222 | 2022-07-09 19:01 | 44751.7924 | C | Disaster | Disaster-fire | STRU | NONE | CENTRAL VALLEY | T22-012463 | 2838 | 2838 | 2282222 | 0.00050005 | 0.40212 | 804.1656 | 5675418 | NA | NA | EFO | Emergency Forced Outage
NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | 2022 | 2022-08-11 11:01 | 44784.459 | No | YES | No | 0.40486 | 583 | 2022-08-11 20:44 | 44784.8639 | F | Equipment Failure | Equip Fail-conductor | COND | NONE | NORTH VALLEY AND SIERRA | T22-014359 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | EFO | Emergency Forced Outage
June 2022 YTD result: (4/5525.9)*1000= | 0.7239
Formulas:
Durn (hr:min) = [Date In]-[Date Out]

## OH_Tx_wire_down_events_insideRF
SAP FL | LINE NO | Date Out | Time Out | Division | County | in RFW | date/ time | NWS Fire Zone | RFW ISSUED local | RFW EXPIRED local
ETL.6660 | 60058 | 2017-10-08 | 13:11 | North Valley | Tehama | 1 | 2017-10-08 13:11 | CAZ215 | 2017-10-08 11:00 | 2017-10-09 17:00
ETL.4780 | 20047 | 2017-10-08 | 23:15 | Sonoma | Sonoma | 1 | 2017-10-08 23:15 | CAZ507 | 2017-10-08 11:00 | 2017-10-10 05:00
ETL.6890 | 60083 | 2017-10-09 | 2:01 | Sonoma | Sonoma | 1 | 2017-10-09 02:01 | CAZ506 | 2017-10-08 11:00 | 2017-10-10 05:00
ETL.7180 | 60113 | 2020-08-17 | 9:56 | North Bay | Marin | 1 | 2020-08-17 09:56 | CAZ505 | 2020-08-15 23:00 | 2020-08-17 11:00

## Customer-MED Counts
System Customer Counts |  |  | 2.5b Declared Major Event Days | [17 empty] | DAILY AIDI THRESHOLDS FOR 2.5b (IEEE-1366) MAJOR EVENT DAY CLASSIFICATION | [35 empty] | IEEE-1366 TMED Days
Year | Customers |  | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | TRANSMISSION & DISTRIBUTION
1999 | 4913807 | 1 | 2005-01-07 | 2006-01-01 | 2007-02-26 | 2008-01-04 | 2009-02-13 | 2010-01-18 | 2011-02-16 | 2012-12-02 | 2013-04-08 | 2014-08-24 | 2015-02-06 | 2016-02-17 | 2017-01-03 | 2018-03-16 | 2019-01-06 | 2020-01-16 | 2021-01-18 |  | (Excluding ISO Outages) | [35 empty] | Planned Outage Classification Available
2000 | 4972045 | 2 | 2005-01-08 | 2006-01-02 | 2007-02-27 | 2008-01-05 | 2009-04-14 | 2010-01-19 | 2011-02-17 | 2012-12-17 | 2013-06-23 | 2014-12-03 | 2015-02-07 | 2016-03-05 | 2017-01-08 | 2018-05-17 | 2019-01-16 | 2020-01-17 | 2021-01-19 | [37 empty] | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
2001 | 4814662 | 3 | 2005-03-20 | 2006-02-27 | 2007-02-28 | 2008-01-06 | 2009-10-13 | 2010-01-20 | 2011-02-18 | 2012-12-21 | 2013-11-21 | 2014-12-11 | 2015-02-08 | 2016-10-14 | 2017-01-09 | 2018-07-28 | 2019-01-17 | 2020-02-09 | 2021-01-25 |  |  | No Planned Outage Classification | [34 empty] | 116 | 101 | 202 | 125 | 214 | 110 | 1107 | 822 | 101 | 107 | 101 | 226 | 104 | 213 | 118 | 216 | 1202 | 408 | 824 | 206 | 217 | 103
2002 | 4877939 | 4 | 2005-09-20 | 2006-03-10 |  | 2008-01-24 | 2009-11-28 | 2010-01-21 | 2011-02-24 | 2012-12-23 | 2013-11-22 | 2014-12-12 | 2015-04-06 |  | 2017-01-10 | 2018-10-14 | 2019-02-02 | 2020-03-15 | 2021-01-26 |  | Division/Region/System | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016-old | 2016* | 2017 | 2018 | 2019 | 2020 | 2021 | 118 | 122 | 203 | 209 | 614 | 125 | 1108 | 1214 | 217 | 108 | 102 | 227 | 105 | 414 | 119 | 217 | 1217 | 623 | 1203 | 207 | 305 | 108
2003 | 4953021 | 5 | 2005-11-20 | 2006-04-04 |  | 2008-01-26 | 2009-12-07 | 2010-01-22 | 2011-02-25 |  |  | 2014-12-30 | 2015-06-08 |  | 2017-01-11 | 2018-11-08 | 2019-02-04 | 2020-03-16 | 2021-01-27 |  | SYSTEM | 2.7743 | 2.4821 | 2.4284 | 2.4763 | 2.4376 | 2.3075 | 2.2803 | 2.2761 | 3.0148 | 3.3829 | 3.5432 | 3.9065 | 3.7879 | 3.095 | 3.0843 | 3.332 | 2.9879 | 3.0107 | 3.1496 | 3.212 | 2.8407 | 2.9564 | 2.9324 | 2.9286 | 2.8369 | 2.7606 | 2.388 | 2.186 | 1.8759 | 1.8793 | 1.4633 | 1.8473 | 1.9346 | 2.9409 | 3.5 | 702 | 224 | 205 | 403 | 1022 | 209 | 1214 | 1220 | 225 | 320 | 227 | 228 | 106 | 912 | 120 | 218 | 1221 | 1121 | 1211 | 208 | 1014 | 109
2004 | 5042759 | 6 | 2005-12-01 | 2006-07-21 |  | 2008-01-24: 2008-01-27; 2010-01-21: 2010-10-24; 2011-02-24: 2011-03-19; 2015-04-06: 2015-07-18 |  | 2017-01-18 | 2018-11-21 | 2019-02-05 | 2020-08-15 | 2021-01-28 | [37 empty] | 810 | 402 | 206 |  |  | 210 | 1215 | 1222 | 1001 | 920 | 310 |  | 124 | 1013 | 121 | 224 | 1223 | 1122 | 1212 | 406 |  | 110
2005 | 5128545 | 7 | 2005-12-18 | 2006-07-22 |  | 2008-01-24: 2008-10-04; 2010-01-21: 2010-11-20; 2011-02-24: 2011-03-20; 2015-04-06: 2015-07-19 |  | 2017-01-19 | 2018-11-29 | 2019-02-09 | 2020-08-16 | 2021-07-18 |  | CENTRAL COAST | 29.7956 | 27.9797 | 31.7936 | 35.7302 | 36.1992 | 32.2407 | 29.4237 | 24.9375 | 29.2416 | 28.3054 | 30.272 | 30.8415 | 30.4978 | 22.4117 | 20.9746 | 21.0546 | 18.7976 | 19.4847 | 19.1293 | 18.8613 | 15.5508 | 16.0395 | 14.4632 | 14.381 | 13.5858 | 12.3229 | 9.6242 | 8.2382 | 7.0246 | 7.0246 | 6.4149 | 7.8472 | 8.7204 | 11.3398 | 11.8757 | 1026 | 1023 | 207 |  |  | 211 | 1216 | 1228 | 1017 | 1120 | 404 |  | 126 | 1128 | 122 | 225 |  |  | 1230 | 608 |  | 111
2006 | 5209310 | 8 | 2005-12-31 | 2006-07-23 |  | 2010-01-21: 2010-11-21; 2011-02-24: 2011-03-21; 2015-04-06: 2015-10-18 |  | 2017-01-20 |  | 2019-02-10 | 2020-08-17 | 2021-07-22 |  | DE ANZA | 40.925 | 28.3096 | 27.5292 | 23.4539 | 18.1576 | 17.2622 | 20.5262 | 20.2749 | 25.0033 | 26.2424 | 31.4799 | 37.2912 | 48.9988 | 45.5321 | 44.3961 | 40.8331 | 27.2339 | 16.5537 | 13.3861 | 12.6085 | 10.4503 | 10.0709 | 9.3796 | 9.9782 | 8.7593 | 7.9515 | 7.309 | 6.8334 | 5.7334 | 5.7305 | 6.0731 | 7.8612 | 8.1627 | 9.7228 | 10.8804 | 1029 |  | 1107 |  |  | 212 | 1217 | 1229 | 1019 | 1201 | 721 |  | 127 | 1207 | 1024 | 319 |  |  |  | 718 |  | 118
2007 | 5276684 | 9 |  | 2006-07-24 |  | 2010-01-21: 2010-11-22; 2011-02-24: 2011-03-24; 2015-04-06: 2015-12-13 |  | 2017-01-21 |  | 2019-02-12 | 2020-09-07 | 2021-08-01 |  | DIABLO | 26.0952 | 28.6219 | 27.7943 | 25.5922 | 22.6206 | 18.8432 | 16.5356 | 15.3317 | 15.222 | 15.7469 | 15.5024 | 15.1618 | 14.3493 | 13.0006 | 11.781 | 12.8002 | 12.5482 | 12.2787 | 12.6794 | 14.6455 | 14.2133 | 14.0208 | 14.5534 | 13.8322 | 12.4227 | 11.3395 | 10.0917 | 8.1321 | 6.9462 | 6.986 | 6.2521 | 6.2885 | 5.7855 | 6.6325 | 7.7801 | 1210 |  | 1130 |  |  | 304 | 1218 |  | 1227 | 1218 | 722 |  | 613 |  | 1120 | 320 |  |  |  | 719 |  | 119
2008 | 5323472 | 10 |  | 2006-12-27 |  | 2011-02-24: 2011-03-25; 2015-04-06: 2015-12-24 |  | 2017-01-22 |  | 2019-02-13 | 2020-09-08 | 2021-08-02 |  | EAST BAY | 23.3106 | 20.4431 | 20.8912 | 18.7853 | 18.8296 | 17.659 | 15.903 | 15.5776 | 17.707 | 21.9142 | 21.0004 | 22.932 | 24.7377 | 24.6641 | 25.5369 | 29.7195 | 28.7102 | 26.4757 | 26.3669 | 24.9191 | 23.2597 | 23.6082 | 23.1841 | 20.7755 | 17.4851 | 15.1688 | 12.0773 | 9.9146 | 8.457 | 8.4492 | 7.758 | 7.9447 | 8.2848 | 9.3752 | 9.3386 | 1221 |  | 1205 |  |  | 924 | 1219 |  |  | 1231 | 723 |  | 1004 |  | 1121 | 321 |  |  |  | 1018 |  | 120
2009 | 5359808 | 11 |  |  |  | 2011-02-24: 2011-09-10 |  | 2017-01-23 |  | 2019-02-14 | 2020-09-27 | 2021-08-04 |  | FRESNO | 27.0895 | 24.249 | 21.5891 | 18.548 | 18.913 | 17.4559 | 15.6365 | 14.64 | 16.3631 | 14.8457 | 13.3282 | 12.4049 | 11.0546 | 9.5314 | 9.1162 | 9.4956 | 9.0396 | 8.7716 | 10.1656 | 11.4056 | 11.8835 | 11.467 | 11.3189 | 9.6538 | 7.7873 | 6.3472 | 5.3569 | 4.5289 | 3.8792 | 3.8758 | 3.485 | 3.3548 | 3.2429 | 3.4797 | 3.6883 | 1222 |  | 1208 |  |  | 1030 | 1220 |  |  |  | 724 |  | 1215 |  | 1122 | 324 |  |  |  | 1213 |  | 121
2010 | 5359808 | 12 |  |  |  | 2011-02-24: 2011-10-05 |  | 2017-02-07 |  | 2019-02-15 | 2020-10-14 | 2021-08-12 |  | HUMBOLDT | 33.7004 | 29.8918 | 25.4558 | 22.8777 | 20.7785 | 22.611 | 23.6058 | 27.6451 | 40.4891 | 47.134 | 43.5987 | 45.4644 | 44.7245 | 38.5151 | 37.2148 | 40.2017 | 39.5772 | 39.7323 | 40.3081 | 40.8073 | 36.2494 | 35.8037 | 30.7331 | 30.9818 | 29.5608 | 27.9378 | 22.6985 | 21.4557 | 18.3121 | 18.2852 | 14.2175 | 16.2945 | 17.2275 | 24.7155 | 24.6448 | 1229 |  |  |  |  | 1112 | 1228 |  |  |  | 1227 |  |  |  | 1219 | 325 |  |  |  | 1224 |  | 122
2011 | 5386499 | 13 |  |  |  | 2011-02-24: 2011-11-30 |  | 2017-02-09 |  | 2019-02-16 | 2020-10-22 | 2021-08-17 |  | KERN | 37.3499 | 31.0687 | 27.7588 | 23.8522 | 20.8568 | 16.0656 | 13.9008 | 11.9781 | 10.6701 | 9.583 | 9.6157 | 10.035 | 10.5443 | 11.6207 | 12.5791 | 13.4196 | 13.1788 | 13.1627 | 13.2121 | 14.3747 | 12.7963 | 13.3475 | 13.7296 | 12.8673 | 11.9189 | 11.6095 | 9.4773 | 8.3095 | 7.2845 | 7.2748 | 6.1779 | 5.9947 | 5.7608 | 6.3715 | 6.7257 | [5 empty] | 1124 | 1231 | [8 empty] | 910 | [5 empty] | 123
2012 | 5411331 | 14 |  |  |  | 2011-02-24: 2011-12-01 |  | 2017-02-17 |  | 2019-02-17 | 2020-10-25 | 2021-09-10 |  | LOS PADRES | 30.6859 | 26.226 | 20.7161 | 18.729 | 18.586 | 15.5827 | 15.6297 | 17.4062 | 18.7027 | 17.7693 | 17.9178 | 17.2934 | 14.6124 | 13.5424 | 12.6061 | 12.7062 | 10.4703 | 10.3967 | 9.6459 | 11.4619 | 10.8598 | 12.1052 | 11.6524 | 11.8349 | 9.3654 | 8.4355 | 7.0262 | 6.9924 | 6.2195 | 6.2118 | 6.3767 | 7.1408 | 7.6021 | 7.9917 | 8.1675 | [5 empty] | 1128 | [9 empty] | 1005 | [5 empty] | 207
2013 | 5353272 | 15 | [12 empty] | 2017-02-18 |  | 2019-02-26 |  | 2021-10-11 |  | MISSION | 23.1343 | 20.9547 | 19.6983 | 17.7523 | 15.7507 | 12.2657 | 9.6897 | 8.733 | 7.7796 | 8.7852 | 9.4448 | 10.812 | 9.9537 | 9.7438 | 9.9103 | 9.8646 | 9.3505 | 10.1431 | 10.1156 | 10.2168 | 10.034 | 10.2577 | 9.9837 | 10.2608 | 8.6865 | 8.6529 | 7.7378 | 7.366 | 6.6158 | 6.5797 | 6.444 | 6.0608 | 5.8005 | 6.2517 | 7.283 | [5 empty] | 1202 | [9 empty] | 1130 | [5 empty] | 209
2014 | 5380759 | 16 | [12 empty] | 2017-02-20 |  | 2019-02-27 |  | 2021-10-17 |  | NORTH BAY | 31.6301 | 25.7916 | 25.4697 | 23.1362 | 21.1708 | 19.2044 | 17.3425 | 16.1215 | 23.4636 | 22.529 | 20.1028 | 18.3081 | 14.9954 | 10.9729 | 11.0272 | 12.0501 | 12.3188 | 13.9407 | 13.9055 | 13.804 | 12.1336 | 11.7619 | 11.1607 | 11.3615 | 10.9157 | 10.645 | 9.9959 | 9.1642 | 8.4503 | 8.4497 | 8.1107 | 9.9453 | 10.2159 | 14.1936 | 15.9559 | [15 empty] | 1201 | [5 empty] | 217
2015 | 5412924 | 17 | [12 empty] | 2017-02-21 |  | 2019-06-08 |  | 2021-10-24 |  | NORTH VALLEY | 19.1667 | 19.7126 | 20.1947 | 21.179 | 20.4107 | 19.5846 | 19.3205 | 21.2066 | 25.2292 | 27.6956 | 27.5436 | 23.6486 | 18.6833 | 14.6635 | 15.4294 | 16.8541 | 16.8417 | 18.1699 | 19.7115 | 18.9752 | 16.0519 | 17.9047 | 16.7617 | 16.5008 | 16.8739 | 17.9234 | 14.2241 | 13.6168 | 12.7628 | 12.754 | 9.9434 | 9.8311 | 11.1344 | 18.4241 | 22.9392 | [21 empty] | 218
2016 | 5446629 | 18 | [12 empty] | 2017-02-22 |  | 2019-06-10 |  | 2021-10-25 |  | PENINSULA | 22.4478 | 17.6664 | 15.7952 | 16.7714 | 17.3507 | 17.8248 | 17.4533 | 17.4672 | 17.9516 | 19.9743 | 20.3814 | 20.8427 | 20.2497 | 18.5705 | 16.6961 | 19.4547 | 18.9418 | 17.1606 | 15.046 | 14.5511 | 10.6339 | 10.0563 | 9.2809 | 10.28 | 9.2388 | 9.6816 | 8.2598 | 8.6077 | 7.3152 | 7.314 | 7.3078 | 7.1592 | 7.6057 | 8.8191 | 9.4583 | [21 empty] | 220
2017 | 5481869 | 19 | [12 empty] | 2017-04-06 |  | 2019-08-15 |  | 2021-12-13 |  | SACRAMENTO | 16.7581 | 16.3545 | 16.2287 | 15.6275 | 14.8004 | 14.0836 | 13.2529 | 12.3231 | 15.0273 | 16.4212 | 16.9554 | 16.6526 | 15.4296 | 13.6105 | 13.4484 | 15.5519 | 15.9276 | 17.122 | 18.7802 | 18.1072 | 13.8065 | 14.4149 | 13.9189 | 12.8423 | 11.656 | 11.975 | 9.2875 | 8.1192 | 5.4682 | 5.4816 | 4.8826 | 5.5988 | 5.9502 | 7.1076 | 8.083 | [21 empty] | 221
2018 | 5517212 | 20 | [12 empty] | 2017-04-07 |  | 2019-09-23 |  | 2021-12-14 |  | SAN FRANCISCO | 16.2193 | 15.4024 | 16.0711 | 15.722 | 14.5959 | 12.4654 | 11.7575 | 10.1488 | 11.273 | 12.8848 | 13.7878 | 16.1973 | 17.4278 | 15.4231 | 16.7499 | 17.824 | 16.9952 | 16.2504 | 17.1558 | 14.7393 | 14.2511 | 13.4005 | 13.1956 | 11.5166 | 10.6933 | 9.3429 | 8.1507 | 7.6008 | 7.2242 | 7.2177 | 6.857 | 7.5901 | 7.349 | 7.6854 | 7.3068
2019 | 5548929 | 21 | [12 empty] | 2017-04-21 |  | 2019-09-25 |  | 2021-12-15 |  | SAN JOSE | 42.973 | 38.9643 | 37.0907 | 32.8845 | 30.1717 | 24.8646 | 21.0028 | 18.055 | 20.2159 | 20.7542 | 19.3341 | 22.4937 | 19.843 | 17.6989 | 17.2477 | 17.8766 | 15.8869 | 16.3723 | 14.9172 | 15.1155 | 12.9156 | 11.5085 | 9.9197 | 8.9501 | 7.2688 | 6.8181 | 6.0325 | 5.9086 | 5.9435 | 5.9408 | 5.3819 | 5.9075 | 5.9008 | 6.0478 | 7.1971
2020 | 5631636 | 22 | [12 empty] | 2017-06-18 |  | 2019-10-05 |  | 2021-12-25 |  | SIERRA | 29.4669 | 26.8393 | 25.0458 | 22.34 | 20.1387 | 18.2359 | 17.3698 | 16.6089 | 19.2982 | 19.8585 | 19.5428 | 16.4533 | 14.4027 | 13.0541 | 14.1382 | 15.2898 | 15.2701 | 17.5285 | 16.5144 | 15.7896 | 14.8341 | 16.5472 | 15.1117 | 15.1955 | 15.3004 | 14.5615 | 11.0575 | 9.9456 | 12.5476 | 12.5508 | 9.2519 | 11.2684 | 12.2626 | 17.7554 | 20.6159
2021 | 5675418 | 23 | [12 empty] | 2017-09-03 |  | 2019-10-09 |  | 2021-12-26 |  | SONOMA | 42.1774 | 33.9014 | 32.0081 | 24.4269 | 20.1787 | 20.4563 | 18.6597 | 18.3467 | 24.5527 | 26.395 | 24.4077 | 23.9535 | 22.2764 | 17.4928 | 17.1688 | 19.8013 | 18.6259 | 18.1346 | 17.687 | 16.4624 | 13.7805 | 13.4078 | 12.9683 | 12.665 | 11.4197 | 11.1574 | 10.128 | 9.4959 | 8.4624 | 8.4719 | 7.4782 | 9.1451 | 8.9661 | 11.9398 | 13.4378
2022 | 5675418 | 24 | [12 empty] | 2017-09-11 |  | 2019-10-10 |  | 2021-12-27 |  | STOCKTON | 36.9342 | 39.7434 | 36.4171 | 32.6105 | 30.624 | 26.6769 | 21.3636 | 20.5621 | 22.9686 | 23.9022 | 21.0436 | 20.5508 | 17.6441 | 14.8517 | 13.8208 | 14.7643 | 14.2862 | 16.0757 | 17.5596 | 17.6347 | 16.4462 | 15.043 | 14.2487 | 12.8654 | 12.6977 | 11.2908 | 10.6064 | 8.7967 | 7.2359 | 7.3293 | 5.2068 | 5.8196 | 5.6987 | 8.1025 | 9.0077
|  | 25 | [12 empty] | 2017-10-08 |  | 2019-10-23 |  | 2021-12-29 |  | YOSEMITE | 30.7666 | 27.7223 | 22.1675 | 21.1607 | 20.637 | 18.3841 | 17.3202 | 18.7433 | 21.0363 | 21.6605 | 21.0392 | 21.2401 | 18.6991 | 15.6926 | 14.6972 | 13.209 | 12.0424 | 12.2975 | 12.8817 | 13.5794 | 13.402 | 13.6068 | 13.0035 | 13.5258 | 13.2458 | 12.328 | 10.5203 | 9.3714 | 7.5925 | 7.5576 | 5.9316 | 7.0342 | 7.0512 | 9.4814 | 10.712
|  | 26 | [12 empty] | 2017-10-09 |  | 2019-10-26 |  |  |  | BAY AREA REGION | 9.2101 | 8.3559 | 8.9728 | 8.4976 | 7.7545 | 6.2648 | 5.6038 | 4.965 | 5.8001 | 5.8641 | 5.8423 | 5.7624 | 5.0385 | 4.3966 | 4.4399 | 5.1013 | 5.2506 | 5.31 | 5.3614 | 5.3855 | 4.9009 | 4.6516 | 4.7877 | 4.3362 | 3.9018 | 3.6322 | 3.3095 | 2.8817 | 2.5656 | 2.5642 | 2.2928 | 2.5256 | 2.3822 | 2.9479 | 3.3593 | 10 | 5 | 9 | 2 | 3 | 13 | 11 | 6 | 7 | 8 | 10 | 3 | 7 | 5 | 10 | 14 | 4 | 4 | 5 | 10 | 3 | 17
|  | 27 | [12 empty] | 2017-10-14 |  | 2019-10-27 |  |  |  | CENTRAL COAST REGION | 7.1181 | 6.3939 | 6.2607 | 5.7696 | 4.9755 | 4.1606 | 4.0074 | 3.8328 | 4.6145 | 4.9735 | 5.5273 | 6.4239 | 6.211 | 5.365 | 5.1019 | 5.1234 | 4.236 | 4.0099 | 3.8438 | 4.0272 | 3.4923 | 3.562 | 3.2506 | 3.2409 | 2.8815 | 2.7896 | 2.4396 | 2.2766 | 2.0149 | 2.0126 | 1.8151 | 2.1535 | 2.132 | 2.6176 | 2.8597
|  | 28 | [12 empty] | 2017-10-20 |  | 2019-10-29 |  |  |  | CENTRAL VALLEY REGION | 7.7342 | 7.1164 | 6.6806 | 6.3296 | 6.2788 | 5.4803 | 4.8756 | 4.822 | 5.7896 | 6.1038 | 5.9288 | 6.2799 | 5.9096 | 5.073 | 4.8438 | 4.9805 | 4.543 | 4.7523 | 5.2691 | 5.6096 | 5.4542 | 5.4439 | 5.3043 | 5.0917 | 4.8122 | 4.3153 | 3.7998 | 3.3012 | 2.6518 | 2.6693 | 1.9663 | 2.2187 | 2.1901 | 3.0284 | 3.4893 |  | With the inclusion of Planned Outages in our reliability calculations, the four blacked-out dates no longer exceed the ME Day Threshold.
|  | 29 | [12 empty] | 2017-12-04 |  | 2019-11-20 |  |  |  | NORTHERN REGION | 7.4911 | 6.4967 | 6.2075 | 5.8694 | 5.5885 | 5.935 | 6.066 | 6.4 | 8.473 | 9.3954 | 8.8813 | 8.681 | 7.9614 | 6.4139 | 6.5869 | 7.5261 | 7.3599 | 7.6109 | 7.787 | 7.6237 | 6.5615 | 7.0835 | 7.0726 | 7.315 | 7.222 | 7.3201 | 6.1328 | 5.5751 | 4.7594 | 4.758 | 3.6722 | 4.3669 | 4.6227 | 7.2832 | 8.8069 |  | They remain on this list, as well as on the "raw" tab, in their blacked-out state for reference only.
|  | 30 | [12 empty] | 2017-12-16 |  | 2019-11-26 | [40 empty] | They are not included in the totals on row 28.
|  | 31 | [14 empty] | 2019-11-27
32
|  | 33 | [6 empty] | 14 | 4 | 4 | 5 | 10 | 3 | 30 | 7 | 31 | 14 | 25
|  |  | Prior to 2011, a MED was declared when daily CESO |  |  | 2011-02-24: Daily SAIDI 2.5b Threshold (governing standard: IEEE 1366) | [25 empty] | * 1/25/17 – Reset the 2016 TMed value from 1.876 to 1.879 due to a discovered 2014 data error related to the DART OUTAGE conversion.
|  |  | was >= 10% of System Customer Count. CPUC used this | [5 empty] | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
|  |  | criterion, but adopted SAIDI threshold 2.5 beta in 2015 | [5 empty] | 2.97 | 2.843 | 2.759 | 2.388 | 2.186 | 1.879 | 1.469 | 1.847 | 1.935 | 2.941 | 3.5 | 5.035